## Table 1
CCONTPRACBTORS Waikeria Prison Development - Inspection & Test Plan (ITP) Process/ Sub - Process: Combined Services natural Gas & LPG Gas Tight Pressure Test WP Number: NZ1005-CS-WPK-051 ITP No.: AES-NZ1005-STE-ITP-PMT-0012 Rev: 2 Date: 02/06/2022 THIS iNSPECTION & TEST PLAN COMPRISES THE lf'OLl!..OWENG DOCUMENTS AND IS APPROVED FOR USE: PART1 Inspection and Test Plan PART2 Gaslight Air Pressure Test Report PART3 Lot Verification Checklist PART4 Reference Documentation: Reviewed by: Commissioning Engineer Rasem Naji refer to WF-004348 30/06/2023 Prepared by: Lance Craigie (Company Name) AE Smith 2/06/2023 {date) Reviewed by: CPB Engineer Rajesh Sredharan (signature) / /" r J <1.,,f-Y? {date) 05/o7/23. (date) /\dnrf 17 2,.. (date)
r c..;1111ers c..;1aasen - Reviewed by: Consultant Heather Huckle - AECOM . . Jack Yang - AECOM (If applicable. N/A for Architects) Nick Jolly -AECOM (signature) F-004348 30/06/2023 (date) Approved by: CPB SPE or higher Chris Revell (signature) Tl'-7-1z.t::_ (date) A MEMBER OF THE OMICGROUP :ICIMIC
Reference Documentation: |  |  |  |  |  Project Specifications: NZT5007-STE-HSSP-0001 NZT5007-STE-CESP-0001  Drawings:
AES-NZ1005-STE-SHD-HYD-4003 - Natural Gas Piping Layout Area 3 AES-NZ1005-STE-SHD-HYD-4004 - Natural Gas Piping Layout Area 4 AES-NZ1005-STE-SHD-HYD-4006 - Natural Gas Piping Layout Area 6 AES-NZ1005-STE-SHD-HYD-4007 - Natural Gas Piping Layout Area 7 AES-NZ1005-STE-SHD-HYD-4009 - Natural Gas Piping Layout Area 9 AES-NZ1005-STE-SHD-HYD-4010 - Natural Gas Piping Layout Area 10 AES-NZ1005-STE-SHD-HYD-4011 - Natural Gas Piping Layout Area 11
AES-NZ1005-STE-SHD-HYD-4014 - AES-NZ1005-STE-SHD-HYD-4015 - | [13 empty] | LPG & NAT Gas Piping Layout AREA 14 LPG & NAT Gas Piping Layout AREA 15
AES-NZ1005-STE-SHD-HYD-4016 - Natural Gas Piping Layout Area 16 AES-NZ1005-STE-SHD-HYD-4017 - Natural Gas Piping Layout Area 17 AES-NZ1005-STE-SHD-HYD-4018 - Natural Gas Piping Layout Area 18 AES-NZ1005-STE-SHD-HYD-4019 - Natural Gas Piping Layout Area 19 AES-NZ1005-STE-SHD-HYD-4020 - Natural Gas Piping Layout Area 20 AES-NZ1005-STE-SHD-HYD-4021 - Natural Gas Piping Layout Area 21 AES-NZ1005-STE-SHD-HYD-4022 - Natural Gas Piping Layout Area 22 AES-NZ1005-STE-SHD-HYD-4023 - Natural Gas Piping Layout Area 23
INSPECTION and TEST PLAN COMBINED SERVICES Natural GAS & LPG GASTIGHT AIR PRESSURE TEST 1 | [20 empty] | ITP # AES-NZlOOS-STE-ITP-PMT-0012 Rev.2
|  | Contract | [6 empty] | lnground Services -Gas Reticulation Installation
|  | Document Title | [6 empty] | ITP Combined Services Natural Gas & LPG Gastight Air Pressure Test
|  | Document No. | [6 empty] | AES-NZl00S-STE-ITP-PMT-0012
|  | Process | [6 empty] | Combined Services - Natural Gas & LPG Gastight Air Pressure Test for Section 1- NG - Area 23 to UT1- @ 210kPa Section Z -NG- UTl to FM1 @ 70kPa Section 3-NG- UTl to FM3 , IND , SPO & KIT - @ 70kPa Section 4 LPG- FMl TO LAU @> 70kPa
|  | Action | [6 empty] | Position |  |  |  |  | Name |  |  |  | Signa e |  | Date,
|  | Prepared by | [6 empty] | AE Smith QA Coordinator |  |  |  |  | L Craigie |  |  |  | A =2,j |  | 1/b/&3
|  | Reviewed by | [6 empty] | AE Smith Project Manager |  |  |  |  | M Simpson |  |  |  | ;#1 V |  | 1/6/tJ
|  | Approved by | [6 empty] | AE Smith Plumbing supervisor |  |  |  |  | STamatea |  |  |  | j.ff "ti' I |  | j_/ k/25 ,
|  | Reviewed by | [6 empty] | CPB Quality Team | [8 empty] | I
|  | Approved by | [6 empty] | CPB Services Manger
|  | Accepted by | [6 empty] | CPB Engineer
AE Smith - HVAC, Refrigeration & Electrical Waikeria Prison Development Project Project No. NZC10013
1. SOCPE OF WORKS: This scope of works comprises the provision of the following materials , documentation, services and works for the Combined Services -Natural Gas Gastight Air Pressure Test as per AE Smith Pressure Testing Plan for Sections 1,2,3 and 4 1. Conduct Combined Services Natural Gas Gastight Air Pressure Test ( AECOM Specification - NZT5007-STE-HSSP-0001 ) 2. Quality records: * Test results, reports and measurements, * conformance and non-conformance reports * Gas cerificate of compliance
2. REFERENCED DOCUMENTATION:
Specifications:
[11 empty] | NZT5007-STE-HSSP-0001 | [5 empty] | Hydraulic Services Specification
[11 empty] | AS/NZS 5601.1:2022 | [5 empty] | Pressure Test
Drawings:
[11 empty] | AES-NZ1005-STE-SHD-HYD-4003 - In sequence to – AES-NZ1005-STE-SHD- HYD-4023 | [5 empty] | Natural Gas Piping layout Area 3 - 23
3. DEFINITION OF TERMS:
Conformance Record | [6 empty] | Record submitted by AE Smith to CPB of the evidence pertaining to each lot which demonstrates that the specified requirements for that lot have been met
Hold Point | [6 empty] | An identified point in a process past which AE Smith shall not proceed without a direction from CPB
Lot | [6 empty] | A portion of material or a section of the Works which has been constructed and/or supplied under essentially uniform conditions and contains material of essentially uniform quality, or A single finished item of work which includes several materials and/or work types (e.g. a pit in place)
Witness Point | [6 empty] | An identified point in a construction process at which an activity is observed
4. INSPECTION AND TEST PLAN: Responsible: SE-AE Smith / Downer Site Engineer, SUP-AE Smith / Downer Supervisor, SRV-Surveyor Method: DR-Document review, FM-Field measure, FT-Field test, M-Monitoring, S-Survey, V-Visual Record: FTR-Field test report, LTR-Laboratory test report, TDS-Technical data sheet, QCC-Quality control checklist
# |  |  |  | Inspection and Test Control Point | [5 empty] | Resp. |  | Referenced Documentation |  |  |  | Conformance Criteria |  |  |  | Method |  | Frequency | Ctrl Point |  | Records
[23 empty] | WP | HP
1.0 PRE-COMMENCEMENT CHECKS FOR NATURAL GAS GASTIGHT AIR PRESSURE TEST
1.1 |  |  |  | Natural Gas Reticulation (AECOM Specifications – NZT5007-STE-HSSP-0001) | [5 empty] | SUP |  | AES-NZ1005-STE-ITP-PMT- 003 |  |  |  | Ensure Combined Services HDPE Natural Gas Pipework Installation Inspection and Testing Plan has been signed off prior to commencing Gastight Air Pressure Test. |  |  |  | Document Review |  | Before each Test | AE Smith | CPB | Signed off ITP
1.2 |  |  |  | General | [5 empty] | SE |  | NZT5007-STE-MSSP-0001 |  |  |  | For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.  Specifications & QA Documents Approved  Drawings are confirmed  Equipment fit for purpose |  |  |  | DR |  | Each |  | CPB | Aconex
[12 empty] | REV 4 | [9 empty] | material |  |  | approval
Incoming
Inspection
Checklists
Drawing
Register
2.0 NATURAL GAS GASTIGHT AIR PRESSURE TEST – AS/NZ5601 Appendix E.4 Pipework Test Procedure
# |  |  |  | Inspection and Test Control Point | [5 empty] | Resp. |  | Referenced Documentation |  |  |  | Conformance Criteria |  |  |  | Method |  | Frequency | Ctrl Point |  | Records
[23 empty] | WP | HP
2.1 |  |  |  | Natural Gas Gastight Air | [5 empty] | SUP |  | AE Smith – Waikeria |  |  |  | 1. SYSTEM IS DISCONNECTED AT THE METER |  |  |  | DR |  | Before each | AE | CPB/ | Gastight
|  |  |  | Pressure Test | [7 empty] | Prison Development |  |  |  | OR THE CYLINDER. | [5 empty] | test | Smith | AECOM | Air
[12 empty] | Pressure Testing |  |  |  | 2. ALL OPEN-END CAPS ARE CAPPED OR | [7 empty] | /IR | Pressure
[12 empty] | Procedure V1 |  |  |  | PLUGGED? | [8 empty] | Test
[12 empty] | Appendix D |  |  |  | 3. ALL GAS APPLIANCES ARE ISOLATED? | [8 empty] | Report /
[12 empty] | Schedule 11 WCT62 |  |  |  | 4. SUITABLE TESTING INSTRUMENT | [8 empty] | CONQA
CONNECTED. SERIAL No…………………….
5. RAISE PRESSURE TO 1.5 TIMES THE
OPERATING PRESSURE  Section 1 – NG – Area 23 to UT1
@ 210kPa =315kPa  Section 2 -NG- UT1 to FM1 @
70kPa= 105 kPa  Section 3-NG- UT1 to FM3 , IND &
SPO - @ 70kPa = 105 kPa  Section 4 LPG- FM1 TO LAU @
70kPa= 105kPa
6. ISOLATE PRESSURE SOURCE AND ALLOW 2
MINUTES FOR THE TEMPERATURE OF THE
TESTING MEDUIM TO STABILISE.
7. RECORD TEST START TIME AND GAUGE
READING AND PHOTOGRAPH FOR:  Section 1  Section 2  Section 3  Section 4
# |  |  |  | Inspection and Test Control Point | [5 empty] | Resp. |  | Referenced Documentation |  |  |  | Conformance Criteria |  |  |  | Method |  | Frequency | Ctrl Point |  | Records
[23 empty] | WP | HP
8. TEST DURATIONS AND TEST PRESSUREs  Section 1 – NG – Area 23 to UT1 - 50.52 HOURS at 315 kPa  Section 2 -NG -UT1 to FM1: 1.13 HOURS at 105 kPa  Section 3-NG- UT1 to FM3: 15.27 HOURS at 105 kPa  Section 4 LPG FM1 to LAU: 10 hours at 105 kPa 9. RECORD TEST END TIME AND GAUGE READING AND PHOTOGRAPH FOR  Section 1  Section 2  Section 3  Section 4 10. CALCULATE ADJUSTED TEST END PRESSURE.AND ANY PRESSURE LOSS  Section 1  Section 2  Section 3  Section 4 IF NO PRESSURE LOSS DURING THE PERIOD THE PIPEWORK CAN BE CONSIDERED GASTIGHT. 11. RECORD PASS/FAIL  Section 1  Section 2  Section 3  Section 4
# |  |  |  | Inspection and Test Control Point | [5 empty] | Resp. |  | Referenced Documentation |  |  |  | Conformance Criteria |  |  |  | Method |  | Frequency | Ctrl Point |  | Records
[23 empty] | WP | HP
12. WCT 62 (a)(i)(H) IR to witness gas start test pressure. 13. WCT 62 (a)(i)(H) IR to witness gas end test pressure.
3.0 COMPLETION RECORDS
3.1 |  |  |  | Test results | [5 empty] | SE |  | AE Smith – Waikeria Prison Development Pressure Testing Procedure V1 Schedule 11 WCT 62 |  |  |  | WCT 62 (a)(iii) All pipework pressure test reports shall be provided to the Independent reviewer. |  |  |  | DR |  | Witness | AE Smith | CPB/ AECOM /IR | FTR Gastight Air Pressure Test Report
3.2 |  |  |  | Gas Certificate of compliance | [5 empty] | SE |  | Schedule 11 WCT 62 |  |  |  | WCT 62 (c) GAS COC shall be provided to the Independent reviewer |  |  |  | DR |  | Receive and review | AE Smith | CPB/ AECOM /IR | GAS COC
AE Smith & Son Pty Ltd (SEQ) 117 Carbine Road, Mount Wellington Auckland Telephone 08002376484 GASTIGHT AIR PRESSURE TEST REPORT NATURAL GAS RETICULATION PROJECT NAME / No…………………………………………………………………………………………………………………….. SYSTEM NAME / No. ……………………………………………………………………………………………………………………. LOCATION / DRAWING No……………………………………………………………………………………………………………… TESTING STANDARD: …………………………………………………………………………………………………………………… SECTION OF PIPEWORK TESED: …………………………………………………………………………………………………… TEST INSTRUMENT / SERIAL No………… 1. SYSTEM IS DISCONNECTED AT THE METER OR THE CYLINDER? 2. ALL OPEN-END CAPS ARE CAPPED OR PLUGGED? 3. ALL GAS APPLIANCES ARE ISOLATED? 4. SUITABLE TEST INSTRUMENT CONNECTED. SERIAL No………………………………….. 5. RAISE PRESSURE TO 1.5 TIMES THE OPERATING PRESSURE kPa 6. ISOLATE PRESSURE SOURCE AND ALLOW 2 MINUTES FOR THE TEMPERATURE OF THE TESTING MEDIUM TO STABILISE.
7. RECORD THE PRESSURE AT THE END OF TEST DURATION............ HRs kPa
8. IF NO PRESSURE LOSS DURING THE 10 MINUTES PERIOD THE PIPEWORK CAN BE CONSIDERED GASTIGHT. 9.. PASS / FAIL
REMARKS :-
TESTED BY : | [13 empty] | DATE :
WITNESSED BY : | [13 empty] | DATE :
CONSULTANT REVIEW | [13 empty] | DATE :
Inspection and Test Plan Lot Verification Checklist PART 3 OF INSPECTION & TEST PLAN
Lot Number:
Lot Description:
Note: Item / # records to be filled out by CPB Engineer - minimum is to match ITP, extra documents can be added
No. |  |  | Item | [9 empty] | Number of Records Required |  | LOT Subfolder No: |  |  | Remarks (initial / date)
ITP / Quality Control Checklists
1
1.1
Survey Results
2
2.1
Test Results
3
Conformance of Work Statement (if required ie if some docs not signed): The works for this construction lot conforms in respects to the ITP.
| Name: | [6 empty] | Signed: | [5 empty] | Subcontractor: |  |  |  |  | Date:
Conformance of Work Statement: The works for this construction lot conforms in respects to the ITP.
| Name: | [6 empty] | Signed: | [5 empty] | Foreman/Supervisor |  |  |  |  | Date:
Conformance / Verification of Construction Lot Statement: This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete and attached. Any non-conformances have been dispositioned in accordance with the contract requirements.
| Name: | [6 empty] | Signed: | [5 empty] | Project Engineer/Senior Project Engineer |  |  |  |  | Date:
Quality Review:
| Name: | [6 empty] | Signed: | [5 empty] | Quality Manager / Rep. |  |  |  |  | Date:
Title: WPD Inspection and Test Plan - Template ID: MSID-298162371-1209 Version: 3.0 Date Published: 20/08/2020 Waikeria Prison Development / WPDP - Uncontrolled Document when Printed Project Specific Document Page 4 of 4
Reviewed by: CPB QA Rep Jimmy Montgomery
(sig ture) /
/
Reviewed by: CPB Completions Rep Arun TR
(signature) d