## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | AES-NZ1005-STE-ITP-PMT-0012 - Natural Gas & LPG Gastight Air Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0012 - Natural Gas & LPG Gastight Air Pressure Test
section | PRE-COMMENCEMENT CHECKS FOR NATURAL GAS GASTIGHT AIR PRESSURE TEST
checkpoint | Natural Gas Reticulation (AECOM Specifications – NZT5007-STE-HSSP-0001) - CPB Hold Point
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-003
label | Conformance Criteria - Ensure Combined Services HDPE Natural Gas Pipework Installation Inspection and Testing Plan has been signed off prior to commencing Gastight Air Pressure Test.
label | Method - Document Review
label | Frequency - Before each Test
label | Hold Point - CPB
label | Records - Signed off ITP
checkpoint | General - CPB Hold Point
label | Resp. - SE
label | Referenced Documentation - NZT5007-STE-MSSP-0001 REV 4
label | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | • Specifications & QA Documents Approved
label | • Drawings are confirmed
label | • Equipment fit for purpose
label | Method - DR
label | Frequency - Each material
label | Hold Point - CPB
label | Records - Aconex approval
label | • Incoming Inspection Checklists
label | • Drawing Register
section | NATURAL GAS GASTIGHT AIR PRESSURE TEST – AS/NZ5601 Appendix E.4 Pipework Test Procedure
checkpoint | Natural Gas Gastight Air Pressure Test - CPB/AECOM/IR Hold Point
label | Resp. - SUP
label | Referenced Documentation - AE Smith – Waikeria Prison Development Pressure Testing Procedure V1 Appendix D Schedule 11 WCT62
label | Conformance Criteria - 1. SYSTEM IS DISCONNECTED AT THE METER OR THE CYLINDER.
label | 2. ALL OPEN-END CAPS ARE CAPPED OR PLUGGED?
label | 3. ALL GAS APPLIANCES ARE ISOLATED?
label | 4. SUITABLE TESTING INSTRUMENT CONNECTED. SERIAL No…………………….
label | 5. RAISE PRESSURE TO 1.5 TIMES THE OPERATING PRESSURE
label | • Section 1 – NG – Area 23 to UT1 @ 210kPa =315kPa
label | • Section 2 -NG- UT1 to FM1 @ 70kPa= 105 kPa
label | • Section 3 - NG- UT1 to FM3 , IND & SPO - @ 70kPa = 105 kPa
label | • Section 4 LPG - FM1 TO LAU @ 70kPa= 105kPa
label | 6. ISOLATE PRESSURE SOURCE AND ALLOW 2 MINUTES FOR THE TEMPERATURE OF THE TESTING MEDUIM TO STABILISE.
label | 7. RECORD TEST START TIME AND GAUGE READING AND PHOTOGRAPH FOR:
label | • Section 1
label | • Section 2
label | • Section 3
label | • Section 4
label | 8. TEST DURATIONS AND TEST PRESSUREs
label | • Section 1 – NG – Area 23 to UT1 - 50.52 HOURS at 315 kPa
label | • Section 2 - NG - UT1 to FM1: 1.13 HOURS at 105 kPa
label | • Section 3 - NG - UT1 to FM3: 15.27 HOURS at 105 kPa
label | • Section 4 LPG FM1 to LAU: 10 hours at 105 kPa
label | 9. RECORD TEST END TIME AND GAUGE READING AND PHOTOGRAPH FOR
label | • Section 1
label | • Section 2
label | • Section 3
label | • Section 4
label | 10. CALCULATE ADJUSTED TEST END PRESSURE. AND ANY PRESSURE LOSS
label | • Section 1
label | • Section 2
label | • Section 3
label | • Section 4
label | IF NO PRESSURE LOSS DURING THE PERIOD THE PIPEWORK CAN BE CONSIDERED GASTIGHT.
label | 11. RECORD PASS/FAIL
label | • Section 1
label | • Section 2
label | • Section 3
label | • Section 4
label | 12. WCT 62 (a)(i)(H) IR to witness gas start test pressure.
label | 13. WCT 62 (a)(i)(H) IR to witness gas end test pressure.
label | Method - DR
label | Frequency - Before each test
label | Hold Point - CPB/AECOM/IR
label | Records - Gastight Air Pressure Test Report / CONQA
section | COMPLETION RECORDS
checkpoint | Test results - CPB/AECOM/IR Hold Point
label | Resp. - SE
label | Referenced Documentation - AE Smith – Waikeria Prison Development Pressure Testing Procedure V1 Schedule 11 WCT 62
label | Conformance Criteria - WCT 62 (a)(iii)
label | • All pipework pressure test reports shall be provided to the Independent reviewer.
label | Method - DR
label | Frequency - Witness
label | Hold Point - CPB/AECOM/IR
label | Records - FTR Gastight Air Pressure Test Report
checkpoint | Gas Certificate of compliance - CPB/AECOM/IR Hold Point
label | Resp. - SE
label | Referenced Documentation - Schedule 11 WCT 62
label | Conformance Criteria - WCT 62 (c)
label | • GAS COC shall be provided to the Independent reviewer
label | Method - DR
label | Frequency - Receive and review
label | Hold Point - CPB/AECOM/IR
label | Records - GAS COC