## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | b1c5f361-f350-4c63-9d5f-4f96f0b12377 |  | checklist | Mechanical Services HHW and CHW Water Reticulation |  |  |  |  | Yes | Mechanical Services HHW and CHW Water Reticulation | 023e0854-e20a-4387-82d4-225ed19ee9cb
checkpoint-status | 0eb0c189-cfca-46fc-9062-70b3da886345 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | efd692d6-ccc5-43d0-964f-0f2419d1b6cd |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | cb6dd5e1-1200-4c96-b947-b23bf585966f |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | b5d46a49-d538-5de6-a774-a73cfff20522 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 6c8cc609-c698-5b22-842d-5315944924be |  | note | QA documents to be provided prior to installing pipework in trenches. CPB to provide to AE Smith.
checkpoint-status | 4ba182e1-5aa0-443b-89ac-845538d41350 |  | checkpoint | Heat Shrink Weld
checkpoint-status | 3eede750-b4b6-4f75-9cd6-f33df7d87c8b |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | dab76dbe-7a5f-477b-8ece-1fdbee1f1ede |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | 5e19a26a-d43f-4152-89d2-dbf84e41a8f8 |  | checkpoint | Welding of pipework
label | a4f3c2e9-39dd-548c-b87b-a0d81acabdc8 |  | note | Joining of steel pipework to be welded as per approved Welding Procedure Specifications (WSP)
checkpoint-status | b1ae2251-8d45-4578-9926-9cc7af5aa52a |  | checkpoint | Installation of valves
label | d9fe49d2-ebdd-5cf3-89b2-b53e3365c4a4 |  | note | Install valves as per construction drawings
label | cd6b6878-42d0-59aa-9b0e-d2fc3fbef4ed |  | note | Lockable toby boxes installed for in-ground valves.
label | d1d3935d-0d89-5e39-bb21-d7ff1f71d112 |  | note | Correct gaskets installed
label | aa53fdf2-a002-5e55-bddd-7eb19c3e2f00 |  | note | Flange bolts tightened in correct tightening sequence.
checkpoint-status | 793b14d5-f27e-44e9-8832-36a1f9ea4daa |  | checkpoint | Install Thrust and Anchor Blocks
label | ee22a8e1-7309-588d-ae6c-e0d2ac5492b2 |  | note | Minimum dimensions as per IFC drawings.
label | 95952af1-7504-53d4-80e8-b6a26b363d69 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 4f45d8d8-78e2-4bbd-829e-2273e576cf7f |  | checkpoint | Installation of Expansion Loops
label | 6378bd87-7c37-5ed1-adcd-df36c2b29fa5 |  | note | Expansion Loops installed as per IFC drawings.
label | 8ac995f6-f227-54b5-8be3-5ee69444c875 |  | note | Correct dimensions for inner smaller loop as per IFC drawing.
checkpoint-status | 6dd595ea-cb96-418f-9268-6b4bca7446b9 |  | checkpoint | Inspection of Insulation
label | 889b0245-25c3-5ec4-b3f8-50c59ce50d34 |  | note | Inspect insulation for damage
label | 5276e7a3-dfa4-5d65-bd98-60655d530300 |  | note | Confirm Insulation is 50mm as per IFC drawings.
checkpoint-status | 2633f9dd-21ae-4974-96e7-2b70c4fee580 |  | checkpoint | Installation of Pipework Marking Tape.
label | ca6b36e4-eeee-506e-837f-db421d999fcc |  | note | Flow and Return direction arrows installed on all pipework.
label | b272e99d-8835-547f-8986-3ba4311522e7 |  | note | Install detector tape 200mm below existing ground level
checkpoint-status | 3710323f-720f-4e08-846c-6f9e9166af0c |  | checkpoint | Protection of In-ground bolted flange connections.
label | 7da74793-1eac-5530-92e8-e212aad6f3b7 |  | note | All in-ground bolted flange connections are to be cladded and foam filled.
checkpoint-status | 2b69c9e5-e8a1-4a7a-9a5c-6b24390aa5cb |  | checkpoint | Completed Construction Pressure Testing with Air at 750 kPa for 4 hours.
checkpoint-status | 35b0e7cd-2d27-4db7-b3f9-1bd38cd46359 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 65b32a23-98df-57bd-8ad4-87c42c06f1e5 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | f712bc55-b0ca-536d-8024-acbac726e53c |  | note | Ensure each test length is capped and ball valve installed.
label | e2f95062-76c4-55e9-924f-e0887ce07eb4 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | ab09e376-63df-5ad5-985c-2b9bc6bac230 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | ff975576-df85-40ed-9679-c6674e6cfc71 |  | checkpoint | Introduction of Air to 300 kPa
label | 69e2d346-311e-53d5-941e-66cf8ad3c50c |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | b1cce6cf-0f62-5ce9-bca5-22906a3fbac8 |  | note | Monitor for any drop-in pressure.
label | 77ae0720-f4ca-5ede-a6d7-1cc79c384ba4 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 31829bf3-2cc5-4ebf-96f5-5eb98ac7acb7 |  | checkpoint | Increasing Test Pressure
label | 591e5b2a-3e53-5e21-b628-68438645f9f5 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved. Test will begin when pressure reaches 750kPa
checkpoint-status | b65a3692-5dcc-4bb9-97f7-26af13498881 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | fbe6dd86-b064-41ad-b294-f678f4c797d2 |  | checkpoint | HDPE Jacketing
label | 667ccbe9-2502-555b-b3f7-47aa9f07bb53 |  | note | In situ HDPE jacketing at pipe joints to be completed only after pressure testing is completed and the welds have been checked.
checkpoint-status | 8ced1632-665b-491b-9693-231343a08050 |  | checkpoint | As-Builts Completed.
holdpoint | dbd8001c-20f9-4e09-81c0-8a8c6ddec4dc |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 84f1edd6-92d1-4095-b761-3c20f7184d5e |  | checklist | Combined Services HDPE Natural Gas Installation |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation | 0945f706-e66f-4b50-8d17-9a9730a1c2a3
checkpoint-status | 0a3175aa-fe41-4b3d-90b1-f8f0094544c9 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | a8cc2176-8380-4925-bd8a-218cd6b96d04 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | c2633378-7b57-4d29-842e-850f3303719b |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 1362d58b-790a-5bf7-ae6c-46c24049fcec |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | e6094e81-94ca-4d9d-950c-39e28deaa4bc |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 8494e1a3-1f51-4714-ba4f-d8880c45c0f3 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | d060a17a-9506-475f-9663-83bcb0f89d02 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | b842a126-9259-4258-b424-da306dfbbf3d |  | checkpoint | Installation of Valves
label | e6b327b2-1ab3-50da-8e5a-1f74e07840a1 |  | note | Valves Installed as per approved drawings
label | ac7906b2-b8cc-5c24-b10d-c7629c2465ea |  | note | All works have been completed by a registered gas fitter ?
checkpoint-status | 7a8d2d0b-1a5b-40ae-be98-4c3fbfa7742d |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 3b47c0f9-7509-41f8-aad2-7c04494e4d10 |  | checkpoint | As-Builts Completed.
holdpoint | 770763b2-60b2-4a52-bd9c-629cb339c4fb |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 2071fdce-71e6-48f5-a16e-3e869c90e011 |  | checklist | Electrical and Communications Conduit Installation |  |  |  |  | Yes | Electrical and Communications Conduit Installation | 0ac1c466-5cab-4995-b8c8-2e310a39fd64
checkpoint-status | 89ca0071-978f-46b2-a4e2-2e7e94dc2d8c |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 2bd8548e-95dd-488d-93b9-ad086383f072 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b40091b8-fcd4-44c9-a134-579c66a61246 |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | b7700a38-cba9-450c-9482-923f55821e7a |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | bd2227c6-325f-427c-a471-1bfb352116d2 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | a9e6b61f-846b-4aa4-a4fe-f8efb63ed756 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | 7a0ee8dc-b02f-4d17-aa02-3eb795f97afb |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | 301b1e76-1927-4a3c-a012-7277bee08cec |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 80bb38ef-e6fc-440e-830d-ffa071494bb6 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 3e601c5a-5007-4205-8db0-449f1d223a2b |  | checkpoint | As-built drawings completed.
holdpoint | 1d6b6049-ac4b-4177-bc81-571764e33f00 |  | signoff | Request Signoff/ Raise Remedial
checklist-sectioned |  |  | checklist | Combined Services HHW & CHW Hydrostatic Pressure Test |  |  |  |  | Yes | Combined Services HHW & CHW Hydrostatic Pressure Test | 18d47431-cf3d-4194-9add-027c55182e43
checkpoint-group |  |  | section | 1.0 MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | 1.1 - RDM & Consent Approval
label | 42fe2070-266f-5f50-865e-fbd19faf1692 |  | note | Resp. - CPB
label | 092f82de-32b3-584c-806f-bc48a43d4eb7 |  | note | Referenced Documentation - RDM Tracker Consent Tracker
label | b0ca815e-e004-5f4d-9d23-354b1b42cb99 |  | note | Conformance Criteria - RDM approval tracker Consent approval tracker
label | d1854896-b7f4-570e-97f2-074691fd77da |  | note | Method - Document Review
label | 6b886f95-eeb8-58d1-93ae-15a657ea8b93 |  | note | Frequency - By Building/Site Wide
label | ecbd6c65-57a6-52fd-b93d-ce0910dd8b06 |  | note | HP - CPB
label | c098a8a2-e116-524c-be23-209478149840 |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB HP
checkpoint-status |  |  | checkpoint | 1.2 - General
label | 7a7ef121-f348-524c-b853-216665afa0f5 |  | note | Resp. - SE
label | b37803d9-c963-5069-9d18-34de0ab90029 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 92cb23d8-ce8e-58cd-961e-99f8dd251533 |  | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 98c790c1-3749-5499-a210-df5792015957 |  | note | Specifications & QA Documents Approved
label | 9f50b146-f3c7-55f6-8d36-064a81c5cc1e |  | note | Drawings are confirmed
label | 40b1fe30-843e-5d95-8408-2c18c29aef5b |  | note | Equipment fit for purpose
label | 1b1753f9-59e2-538e-991d-302dbde6cb48 |  | note | Method - DR
label | b48e7b66-8fad-5bf0-8f47-d3620df4f376 |  | note | Frequency - Each material
label | 6e4d0359-8658-53bd-a823-72ecaf4e1860 |  | note | HP - CPB
label | 9e4c0b6a-45f6-5c63-9868-885c04e28fef |  | note | Records - Aconex approval
label | 20044c46-16a6-5653-bb38-86e9eac96cfd |  | note | Incoming Inspection Checklists
label | e87c4fd3-ace1-54df-9eec-f5b0babb4190 |  | note | Drawing Register
holdpoint |  |  | signoff | CPB HP
checkpoint-group |  |  | section | 2.0 CONNECT PUMP TO HHW & CHW RING MAINS
checkpoint-status |  |  | checkpoint | 2.1 - Accept delivery of pump to site
label | 4de5871e-ded7-51a4-9748-8e6b12213552 |  | note | Resp. - SUP
label | 80249ea8-6f3b-53b8-ba0c-a55fcab1d109 |  | note | Referenced Documentation -
label | 82b56ede-3d53-5de1-8927-f69a8e72bf6d |  | note | Conformance Criteria - 1. Check pump is rated for pressure test
label | 6ee1c529-d969-5029-b2fa-9d9b09a84e60 |  | note | 2. Check all supplied attachments are correct and in good order
label | 50d54d1a-8b71-56d2-9c91-5be196a85e8c |  | note | 3. Check fluid levels & fill as necessary
label | 6b63e176-1078-52d6-af07-a40b89b9b6a0 |  | note | Method - V
label | 272952e5-7958-5998-8daf-477e8bb69a70 |  | note | Frequency - Once
label | ebc69fdb-984f-5548-a862-a595112daaad |  | note | WP - AE Smith
label | 7ff5d60d-a420-5a85-b1b4-49bb0da7116e |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 2.2 - Connect pump to CHW & CHW ring mains
label | 24ba0e5e-19dc-5867-a4a9-a23da762bba5 |  | note | Resp. - SUP
label | d4cebd9a-5742-5b79-830f-66717ded9f4c |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | ebde1811-2ce6-5add-a9c2-5e89f4680d39 |  | note | Conformance Criteria - Confirm connections are safe and correct
label | 840a6750-e755-52ab-86a4-a3fec4128d3c |  | note | Method - V
label | 3e2327da-0449-5493-9d69-7c69a83c6b5c |  | note | Frequency - Once
label | 1961c039-12e4-5715-a2f4-8a92f44b2fd2 |  | note | WP - AE Smith
label | 1ea3ae8a-c259-5013-a691-13e902230c13 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 2.3 - Connect calibrated gauges for pressure test
label | f147c631-8bf0-5de1-ab1b-f7cddc78af8f |  | note | Resp. - SUP
label | f205106a-63ef-5bb3-8728-619f30489e95 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | ead006d1-bad2-5ba2-9098-e82b5a83bf78 |  | note | AS 4041:2006
label | 4b541c16-9a80-5a62-a4d8-449483cae8ae |  | note | Conformance Criteria - Confirm position is correct, gauge is in good order for test & calibrated
label | 23e669d1-e924-5b4f-b6df-3cfcfde74ec7 |  | note | Method - V + DR
label | 2117e956-1cb6-5021-9543-e964c226f0c8 |  | note | Frequency - Each test
label | bf72b69e-9216-5327-8add-a622feda9163 |  | note | WP - AE Smith
label | 6dfaa82e-e643-5942-bdf8-fabd6e29dc08 |  | note | Records - Check Sheet + Document
checkpoint-group |  |  | section | 3.0 HYDROSTATIC TEST (STAGE ONE)
checkpoint-status |  |  | checkpoint | 3.1 - Fill CHW & HHW ring mains with domestic water
label | 07a4d022-bb0e-5c97-90f9-028fa97ac1b9 |  | note | Resp. - SUP
label | 116550fe-4292-599e-bc58-635476acbf16 |  | note | Referenced Documentation -
label | 2ea70106-fb54-54d4-9ed1-ba3c69bee8c2 |  | note | Conformance Criteria - Completely fill closed loop system with water releasing all air
label | 181958bd-87ee-5cc2-aac8-4deea989c3f9 |  | note | Method - V
label | a2549bb1-0c8d-58e7-99b9-c622a40d81b6 |  | note | Frequency - Every time system is opened
label | c2ec47e3-681a-5769-9e81-372ab94c5de0 |  | note | WP - AE Smith
label | bbe7eb25-c0cf-55ce-af94-ff8df4b4e7c6 |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 3.2 - Gradually increase system pressure to 10 bar
label | fee084cb-3165-53c5-a879-f9522a66890f |  | note | Resp. - SUP
label | 2ecf5040-b48c-5b68-bad2-62c5d091310b |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | b88336e9-8e2b-5963-8c57-753c7ef9f337 |  | note | AS 4041:2006
label | 9242d255-412d-5487-b09c-8b9b8e4c57eb |  | note | Conformance Criteria - Slowly raise system pressure to 10 bar
label | fd5f5b5f-0f5c-5e27-bab7-5b037a960320 |  | note | Checking for any signs of leaks or pressure drops
label | cb9d6b6f-f62e-55c5-a090-ecf5235cafbc |  | note | Method - V+M
label | 7564fde7-56c2-5804-8287-dfd32bec2295 |  | note | Frequency - Constantly Monitored
label | c54195f6-d25c-5f1d-98d3-782ef4ea6d17 |  | note | WP - AE Smith
label | e976be8f-46d5-540e-9ea0-0510fcbf369a |  | note | Records - Check sheet
checkpoint-status |  |  | checkpoint | 3.3 - Hold 10 bar pressure for 2 hours (START WITNESSED)
label | d89d3884-7b2c-535a-9b28-3630cafefde4 |  | note | Resp. - SUP
label | 6e01555b-9edf-570e-9059-a57f6be8cff1 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 7aa90a24-deda-5850-8c8b-2e034727d323 |  | note | AS 4041:2006
label | be08df72-a90f-5b00-a9b9-dfa4ba8b496e |  | note | Conformance Criteria - Record START time & photograph gauge
label | f2744cfc-5f22-5182-ae3c-57fc1fb4f48d |  | note | All relevant parties to witness starting pressure of 10 bar
label | b48b7c00-36d5-5da1-9546-04cd418e92d1 |  | note | Method - V+M
label | 7c00cb95-a592-58bc-9339-d40d9eae6c22 |  | note | Frequency - Once
label | 50a72cce-7807-5bd9-a1df-c2419e44d982 |  | note | WP - AE Smith
label | a853bec3-0410-5fe9-9d87-29731080e99b |  | note | HP - AE Smith / CPB / IR
label | 8e62c1ee-8b03-50a7-9172-0f922c0bdf66 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 3.4 - Hold 10 bar pressure for 2 hours (END WITNESSED)
label | 1836d09b-e6ab-5040-8915-35c2fac0b94a |  | note | Resp. - SUP
label | 7f0d95a5-cf11-5c27-8071-856bec27ff52 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 840d167e-d294-5bd4-bf20-e4d721d15106 |  | note | AS 4041:2006
label | a1fcb3bf-7262-5b59-80ff-3465d04c2702 |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | ae9e9913-6ff1-5fa3-ab5e-4c722cb2322d |  | note | All relevant parties to witness starting pressure of 10 bar
label | 240f40ca-41f3-5234-9cec-803dfb47e72e |  | note | Method - V+M
label | a7618aa1-06f5-5ae3-a856-c658e8a74259 |  | note | Frequency - Once
label | 11eeb17d-11d4-58b8-a743-17d4fcca512c |  | note | WP - AE Smith
label | 19ab030d-0f28-546b-89eb-fa2874e6de62 |  | note | HP - AE Smith / CPB / IR
label | dd2e7d56-2680-549a-9ee6-ef7f9af1ae62 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 3.5 - Pressure released or reduced for next test
label | 5318cc4e-0903-5dd9-a63a-452a5e47516c |  | note | Resp. - SUP
label | 363e9644-7f16-5681-ace8-a5119b48705c |  | note | Referenced Documentation -
label | 37755f47-5588-55f5-85cb-c9fceacf68ed |  | note | Conformance Criteria - Supervisor to ensure energy (pressure) is only stored while under test
label | 41bccc65-a48d-5f02-be93-e16001f3a14d |  | note | Method - V+M
label | 96dd9a49-dd80-575c-b4ee-ed1d91167f0c |  | note | Frequency - Once
label | b81e14e1-79f6-52c0-b448-18e469882403 |  | note | WP - AE Smith
label | 2a6ba4b8-d18a-53dd-b242-3f800f420f8b |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 4.0 HYDROSTATIC TEST (STAGE TWO)
checkpoint-status |  |  | checkpoint | 4.1 - Ensure pressure is 7 bar for second stage of test
label | 5703e44f-45f4-5b0b-8e28-b168c3d83ce1 |  | note | Resp. - SUP
label | 241b59d1-05a3-55a5-89fd-80cd7ecb0cb0 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 39307396-8000-5b82-874c-cbe9e28e7091 |  | note | AS 4041:2006
label | 626b2fce-a4d1-5234-bfb4-6a49f3192ff9 |  | note | Conformance Criteria - Ensure system pressure has been reduced from previous test to 7 bar or Gradually raise to 7 bar
label | 3208b85c-2d41-576c-b4ba-9a34ce0d7551 |  | note | Method - V+M
label | ae5bb2a2-d8a7-5c1a-8b15-77b998902806 |  | note | Frequency - Constantly Monitor
label | 2223f762-4ca1-555d-b828-404039931a3e |  | note | WP - AE Smith
label | de7f4b30-e074-516a-9180-12825b073fad |  | note | Records - Check Sheet
checkpoint-status |  |  | checkpoint | 4.2 - Hold 7 bar pressure for 24 hours (START WITNESSED)
label | 210084a7-eb07-5e82-b2a7-6c0900212fae |  | note | Resp. - SUP
label | f25a8d77-6b46-57c4-a19b-623f6a4d7a8e |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 50d077d0-b62d-57e9-aa4e-fc9363c2730b |  | note | AS 4041:2006
label | d7c836dd-00bc-5064-8612-70f67b58abfd |  | note | Conformance Criteria - Record START time & photograph gauge
label | 58f772e5-c6ae-5479-b434-86448999d3db |  | note | All relevant parties to witness starting pressure of 7 bar
label | dc1052bd-ba0e-5d9b-9f90-66ecfa91f033 |  | note | Method - V+M
label | 54449de3-5da5-548c-8dd8-bf131d7cd84e |  | note | Frequency - Once
label | eed5e589-6cfd-5cef-8b60-d343cd8d929c |  | note | WP - AE Smith
label | ec3989c2-27e6-5e1f-b279-4a4e06d1e991 |  | note | HP - AE Smith / CPB / IR
label | 02ecc4bf-3d0d-5296-b7e3-cc2fe793fc11 |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 4.3 - Hold 7 bar pressure for 24 hours (FINISH WITNESSED)
label | 2005f09f-07c2-565f-a666-be07df2b4f59 |  | note | Resp. - SUP
label | 9fe71053-5e1a-5ef0-a9ad-b58161235e76 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | c2649a77-f1cd-510c-a40e-c153e64e2242 |  | note | AS 4041:2006
label | 17816dd8-1161-572f-93f5-33dd40b22356 |  | note | Conformance Criteria - Record FINISH time & photograph gauge
label | 8bcf2a73-6fb5-58c9-a285-25350ee29877 |  | note | All relevant parties to witness starting pressure of 7 bar
label | 8bd1f1e9-b31a-5673-9419-f71c7d758207 |  | note | Method - V+M
label | 3ab4ea5e-d776-5ca5-8d01-77129f6c2dca |  | note | Frequency - Once
label | ef2b3437-9153-511e-9a52-4faf74e14625 |  | note | WP - AE Smith
label | a43e29d6-83bc-5158-aa5b-8d99d78e2617 |  | note | HP - AE Smith / CPB / IR
label | d20260ae-71f7-59b9-9d09-1cb8f3e9a54d |  | note | Records - Check Sheet + Photos
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checkpoint-status |  |  | checkpoint | 4.4 - Discharge pressure leave system in a safe state
label | 1d8eafc7-e235-524e-9904-86b3bf37655a |  | note | Resp. - SUP
label | 3a33b368-c0f4-5d75-999a-39adba06caa1 |  | note | Conformance Criteria - Discharge system pressure, ensure area is left in a safe state meeting site requirement
label | 2478ed94-dc68-550c-8955-f69a9256a683 |  | note | Method - V+M
label | 04459c59-5b1a-53b6-84aa-e6c461bb2153 |  | note | Frequency - Once
label | a8cf9f86-7729-5ca6-8544-74fce392df22 |  | note | WP - AE Smith
label | 96507776-ec15-565c-879b-581d07d0b9ef |  | note | Records - Check Sheet
checkpoint-group |  |  | section | 5.0 COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | 12.1 - Testing Results
label | 1a6a668c-892f-5933-96e7-ec5edfda3ab7 |  | note | Resp. - SE SUP
label | 9508fbe5-c82f-5381-87f4-057d78aeed91 |  | note | Referenced Documentation - NZT5007-STE-MSSP-0001
label | 5e26ff11-574c-5eb9-81b1-b2cb098abc74 |  | note | AS 4041:2006
label | 95def8ef-9d40-52ee-a0ba-dd81cbaffc30 |  | note | Conformance Criteria - All pipework pressure test reports shall be provided
label | 5fcc341f-5b5e-59a2-9206-213881240f6b |  | note | Method - DR
label | 5182c4cd-cc03-5171-897d-38b5c37d034e |  | note | Frequency - Each lot
label | b22abbe8-c235-5e7d-8031-4f363e20668e |  | note | WP - AE Smith
label | 99452292-6fa2-5070-b370-cf1f1dcdab7b |  | note | HP - AE Smith / CPB / IR
label | 25b9c24e-3fea-59a9-875b-b66ce5d40539 |  | note | Records - Check Sheet
holdpoint |  |  | signoff | AE Smith / CPB / IR HP
checklist-flat | 910b4d2f-20e6-4202-b30f-e5a98f1673b7 |  | checklist | Butt Welding |  |  |  |  | Yes | Butt Welding | 1af85a7b-4718-4fbb-9bfd-d718da1b261e
checkpoint-status | c8dee859-39ca-4784-9e6e-7d9941180258 |  | checkpoint | Weld Details Completed
text | ed0b2069-38ae-51a6-b0c2-c74383a77503 |  | textbox | Weld Number
select | 654e0c4e-ae75-5efb-9283-fce9597f1eee |  | dropdown | Weld Completed By: | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw
select | d7bd3611-6574-5e7b-985b-31213b80e0b3 |  | dropdown | Welding Machine # | Machine 1, Machine 2, Machine 3
text | 1ef3ca77-bad6-5887-9679-d203af4d134f |  | textbox | Certificate #
checkpoint-status | 9348f672-5bb8-48af-8f81-f1ebc2d0197e |  | checkpoint | Pre-weld checks - Visual Inspection of Pipe
label | c297085c-730f-5bd0-a703-add028ac308b |  | note | Ensure branding markings correct
text | 72f28d58-c2ea-537b-88a4-d9afc569fad0 |  | textbox | Record pipe batch number as labelled on the pipe.
text | 72602a86-7457-55e5-9585-0023a698231b |  | textbox | Record pipe wall thickness and inspect.
label | aa5c60b5-1bda-547e-b1ba-b0ddb3e8d4df |  | note | External surfaces are free from scratches deeper than 10% of wall thickness.
label | 307a431e-3d7e-5560-bb54-19623f62c94f |  | note | Inspect internal surface of pipe for scratches.
label | 741c3ce7-5ff4-5c6d-a4a4-44176bfa9235 |  | note | Inspect pipe for cracks.
label | 31efab25-044f-586a-afc0-b20d72a11a63 |  | note | Inspect internal ridges or ripples exceeding 0.5mm in height.
label | 69994fdc-2df3-5a06-889c-37bd5e3df477 |  | note | Clean and wipe pipe with Isopropanol.
label | 78fbbf96-1404-5ecd-bb1b-106fd6853b90 |  | note | Inspect pipe ends are dry from any water content.
checkpoint-status | 73772ba4-d361-4e96-8692-3d8c064313f8 |  | checkpoint | Pre-Weld Checks - Weld Machine Checks
checkpoint-status | 305a8ae4-dd9b-47d5-a05a-c98a7c967f08 |  | checkpoint | Heater plate temperature checks taken and recorded
label | 1392f678-f011-5811-8d91-60940c6de348 |  | note | Ensure pipe ends are capped, welding area isolated to regulate cooling and prevent airborne contaminants.
checkpoint-status | 1ea12469-42df-4f80-8fdc-0a2f3f53ec8c |  | checkpoint | Post Weld - Visual Checks
label | 76f5e0b6-ffdb-5394-8452-e2113022e127 |  | note | Alignment of pipes is less than 10% of pipe wall thickness?
label | d23a7c58-7cf9-5b49-93d3-f2f4774a6d5d |  | note | Fusion beads symmetrical on both sides of weld
label | 8a940c97-118c-5404-a362-346945f8027d |  | note | Ensure Beads are fully rolled over
label | e44185ee-cac1-5d5e-881e-703a3e83133c |  | note | Inspect for cracks in beads and welds are free of pitting and bubbling.
label | f6237a4a-5669-50c3-8fc2-c13123f6f9ee |  | note | Inspect for inclusions or other obvious faults present.
label | ab1817be-06cf-55e1-9e24-276ba3926f96 |  | note | Internal weld beads removed from pipe?
checkpoint-status | 0c3354d5-b811-4786-a402-b6cc6a3c35f5 |  | checkpoint | Weld Records and Inspections
label | bd6b904f-1749-5199-a285-561c0b2364f8 |  | note | Data logger records printed, checked and attached?
label | a35d4317-dd9a-5182-809b-b0cc5628a06c |  | note | Weld completed, inspected by AE Smith Supervisor and CPB ?
holdpoint | adfc0216-485c-4223-9d0d-7e70004f848a |  | signoff | Post weld checks by CPB and AE Smith - Request Signoff/ Raise Remedial
checklist-flat | 01cd6066-c691-4cdd-8044-9f2af37c371a |  | checklist | Combined Services HDPE Natural Gas Installation V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V3 | 1b98d9dd-a1b6-4918-babe-6353e9eafc1d
checkpoint-status | 3b674fde-12f9-491c-bfd7-91c9b8522928 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 3a0c7ffb-c6b4-467a-bb9c-83f87827d5ed |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 5e8825ca-1a25-49dd-822a-916b4fa8946f |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | b168a14e-0bb3-56c9-b664-19797cd888d6 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 3461e5a9-318f-5fc0-a417-3ddc82050093 |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 3e8d9bdc-8dca-46d0-b250-5fe8cbcdb9fb |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 4cd0ca5b-a3d5-439b-a994-79870a1f228b |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | 18b50b7b-9014-4b34-8653-e02d05e536e8 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | e6454834-14bf-4535-89a3-bbb3f129a8b5 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | b97dce31-cff0-4ac1-a37b-ee154c2a2f5b |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | d5822e75-2ec3-445b-b647-dfd98ce47bc9 |  | checkpoint | Installation of Valves
label | 7f838b93-c03d-5931-9cfd-9e6a794969f6 |  | note | Valves Installed as per approved drawings
label | 8d6b2291-2ba9-59e7-96fc-ccb1d813cf07 |  | note | All works have been completed by a registered gas fitter ?
holdpoint | 80b3063f-738b-4e90-bd52-863bce899e31 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | a8899700-077e-4043-8753-8156697457d4 |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | c69bf45f-77b4-4366-a9e2-b609062d4c8a |  | checkpoint | As-constructed survey
label | f0e8f58c-1bad-58d0-a0d2-6d37906c2324 |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checkpoint-status | 7f5fbfa1-6e42-446b-95d7-6cfe1d9ae15c |  | checkpoint | As-Builts Completed.
holdpoint | e14ac220-b795-48b2-8654-2a844ab02d8b |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Flushing Preparation Checklist |  |  |  |  | Yes | Flushing - Flushing Preparation Checklist | 269eb189-04c4-48eb-868a-46cff70dbdd1
checkpoint-status |  |  | checkpoint | Differential pressure manometer
text | 58fcd858-1a3a-5861-936f-5df4a5c385fc |  | textbox | Model Number
text | 6b5ab151-b5c7-576e-b380-cccf68acb19a |  | textbox | Serial Number
checkpoint-status |  |  | checkpoint | HydROtwist Portable Digital PH Test Meter
checkpoint-status |  |  | checkpoint | HM Digital Hand Held TDS Temperature Water Test Meter TDS-3
checkpoint-status |  |  | checkpoint | Hm Digital Hand Held Conductivity & Temperature Meter EC-3
checkpoint-status |  |  | checkpoint | 0-14 pH test strips
checkpoint-status |  |  | checkpoint | High level 200 ppm chlorine test strips
checkpoint-status |  |  | checkpoint | Low level 4 ppm chlorine test strips
select | b2f6ccae-d9d0-5d9a-a4b1-50c6155dc429 |  | dropdown | Flushing pump | Temporary pump,system pump
checkpoint-status |  |  | checkpoint | Pump is available to run under VSD control.
checkpoint-status |  |  | checkpoint | Pump is wired and ready to be turned on.
checkpoint-status |  |  | checkpoint | Strainer basket(s) is installed with commissioning mesh. / skimmers socks installed.
checkpoint-status |  |  | checkpoint | Skimmers sock is installed on the strainers.
checkpoint-status |  |  | checkpoint | Schematic and layout drawings are available and studied.
checkpoint-status |  |  | checkpoint | Isolation valves are installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valve is installed at each terminal.
checkpoint-status |  |  | checkpoint | Balancing valves are used to measure waterflows
select | e585fd55-08c9-5a3f-a34c-e728465b3319 |  | dropdown | Any additional method to measure /confirm flushing waterflows. (flushing velocities) | Pump curve,Ultrasonic flow meter,Main Branch valve
checkpoint-status |  |  | checkpoint | Chemicals available on site as detailed in the
checkpoint-status |  |  | checkpoint | Piping system has been pressure tested and passed.
checkpoint-status |  |  | checkpoint | System has been installed as per drawing and schematic. If not mark-up the drawing and upload here.
checkpoint-status |  |  | checkpoint | All high points have air vents installed
checkpoint-status |  |  | checkpoint | All low points have drain cocks installed.
checkpoint-status |  |  | checkpoint | Mains water / make-up water supply pipe is connected at the suction side of the pump downstream of the drain port.
checkpoint-status |  |  | checkpoint | Mains water pipe connection size is 40 mm or bigger.
checkpoint-status |  |  | checkpoint | Mains water pressure is minimum 1.3 Bar at flow.
checkpoint-status |  |  | checkpoint | A backflow prevention valve (check valve) is installed at the mains water supply valve and it is certified.
checkpoint-status |  |  | checkpoint | A local drain is available in the vicinity of the flushing pump.
checkpoint-status |  |  | checkpoint | The drain pipe minimum 40 mm size is connected upstream of the strainer.
checkpoint-status |  |  | checkpoint | A high volume of contaminated water is to be discharged to the sewer drain. A discharge consent is not required and the discharge limits are recorded below in the note sections.
checkpoint-status |  |  | checkpoint | A special council discharge (trade waste water) consent is required and obtained. A copy of permit is attached. The discharge limits are recorded below in the note section.
checkpoint-status |  |  | checkpoint | Sensitive equipment as listed below are isolated (by-passes), and not included in the dynamic and chemical flushing processes.
checkpoint-status |  |  | checkpoint | Coils
checkpoint-status |  |  | checkpoint | Control valves
checkpoint-status |  |  | checkpoint | Heat exchangers
checkpoint-status |  |  | checkpoint | Condensers
checkpoint-status |  |  | checkpoint | Evaporators
checkpoint-status |  |  | checkpoint | Cartridges from any auto-flow control valves
checkpoint-status |  |  | checkpoint | 15 L dosing pot is installed and connected
label | 3b355f3b-1d65-5dfd-aed6-b230650a2315 |  | note | BSRIA BG 29/2012 recommends make up water quality as below. Label the sample bottle as "Make-up water sample" and date it.
checkpoint-status |  |  | checkpoint | Sulphate
label | a9192ac0-d3e7-5bf1-bf0f-7e2e9075b1dd |  | note | Recommended: <250 mg/L
text | e5b77ef7-0f0f-576e-bce4-d4707e143067 |  | textbox | Site measurement
text | 27bda725-6adb-5210-8da1-495dcab92053 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
label | 9a77971a-405a-5658-97b1-f346df1bb3de |  | note | Recommended: <250 mg/L
text | 607ac1b0-9cf4-5e79-84e3-c2f93cab34b5 |  | textbox | Site measurement
text | 1f401755-433b-5b7d-a406-2cc5ed38e1c9 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
label | 4c19fe8c-e595-57f9-8875-b965dafbacc8 |  | note | Recommended: 6.0 < x < 8.5
text | 4b1eee1c-ca1f-5612-a05c-f94ead523d1b |  | textbox | Site measurement
text | b810ef2a-53b5-53ef-87f4-8670f2ffc87c |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | cfda8399-9ece-5baa-8146-1fe4d5b39a7d |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 82ebb6e8-9bf9-5d47-8850-df31875cace3 |  | textbox | Site measurement
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
label | 90ab1a86-2dc4-5708-903e-597f971aae99 |  | note | Recommended: <10000 per ml
text | a2aaabfe-25af-5161-9ae0-5e8304853b19 |  | textbox | Site measurement
text | a6997c99-9a3a-5ffb-8ed6-c60d3289f52b |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
label | 0defbb3c-7d61-58d0-ac94-c3b25dfe19e0 |  | note | Recommended: <10 per ml
text | dfa70a05-4626-54f9-942c-f851ed8069fb |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | System filled with make-up water
checkpoint-status |  |  | checkpoint | Date
checkpoint-status |  |  | checkpoint | Make-up water connection location
checkpoint-status |  |  | checkpoint | Mains water pressure (kPa)
checkpoint-status |  |  | checkpoint | Water drained from furthest terminal until clear water is visible.
text | 0fafdfde-8348-5743-8007-852e92543352 |  | textbox | Drain waterflow (l/s)
text | 4a65ff20-c87e-5056-9418-e8cd7a7ca85f |  | textbox | Drain location
text | d420d8db-deda-55ae-acf5-f694fcb73cce |  | textbox | Drain duration (minutes)
text | 4a11c89c-193a-5ee8-b40e-ece79364f046 |  | textbox | Calculated drain water volume (L)
checkpoint-status |  |  | checkpoint | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Water drained from all other location same as above
checkpoint-status |  |  | checkpoint | Air vent from all high points.
checklist-flat | 6652d6e4-22a6-44dd-89b7-d9fad6a9cbf7 |  | checklist | Electrical and Communications Conduit Trench Riser Installation checklist |  |  |  |  | Yes | Electrical and Communications Conduit Trench Riser Installation checklist | 361f1b9f-66ee-4838-867f-e932b5a66fb7
checkpoint-status | bb6a80f2-e56b-42fe-91b4-c3c48af7640f |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | d344d940-9c45-4416-8d0d-709cd2e09d24 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b1c2655c-59f2-4b9d-aa70-f02d8956f8df |  | checkpoint | Confirm trench depth, width and pipe alignment, QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | af235ead-2c4f-498a-9467-7806fd4c8469 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | 3b54bd5e-1b9d-40cc-8133-7a9cdae089d9 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | bf2ffa7e-f109-47b4-bf39-a9e6a4102ccf |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | dbdcf3a6-e1a8-48b3-80f7-022be8bc2258 |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | e2b8b3af-7c7d-439c-81cc-ffa9d765f60c |  | checkpoint | A draw rope shall be installed in each conduit run and shall extend a minimum of 500mm above the top of pit collar.
checkpoint-status | 18acff54-f214-40d7-8f3f-6605891d1785 |  | checkpoint | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 8c57b926-1fe7-4512-9631-1b5495a5183a |  | checkpoint | As-built drawings completed.
holdpoint | 3522a344-b88d-4993-9a37-38f6669926a3 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 89983eeb-40b8-4d9a-846b-86db75106d69 |  | checklist | Document: |  |  |  |  | Yes | Project Documentation | 39a14167-4ddb-4a2f-9155-27e491efa078
checkpoint-no-status | 78d25478-5723-4f8e-b4d8-3b7b8d9a0cd0 |  | checkpoint | Document Attached
checklist-flat | a797e116-4314-4950-b21e-318499f53ed9 |  | checklist | Electrical In-ground Conduits and cable pits |  |  |  |  | Yes | Electrical In-ground Conduits and cable pits | 42117a23-0f2f-4926-8b51-438e41adfb90
checkpoint-status | 65ffbea4-b117-4865-a38c-73958b9eaca8 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | e8cc9c95-81d4-44f3-ad26-b68b31ded36c |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 93d4a819-6671-4dca-975f-fbc8930120e4 |  | checkpoint | Location
label | 8ab6ab6b-a2c5-595c-8241-81075f52e7c9 |  | note | Shall be as shown on the drawings,
label | 8b202d77-efc5-5357-b3c4-12f7877b8001 |  | note | Shall be as instructed by CPB Rep. as to best suit the conditions on the Site at the time of construction.
checkpoint-status | e1a4cc61-ec49-4bfb-b716-d4415025ebb6 |  | checkpoint | Confirm trench depth, width and pipe alignment
label | d45101f8-51a2-51e2-8b20-ca085e320d51 |  | note | Trench depth, width and conduit alignment shall be as shown on drawing
label | f4dfac2f-93e3-5ff0-8634-f450245e84d5 |  | note | Excavation Checklist to be completed prior to installing services.
holdpoint | 77d6968e-83a2-4884-8283-7324a2de6a9d |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | eaee2ef1-32fb-4899-94db-280bcd07eff0 |  | checkpoint | Bottom of the trench shall be compacted to form a firm uniform surface free from loose material.
checkpoint-status | ff28e55f-fd75-4c7d-9693-4adda04b31e5 |  | checkpoint | Number of conduit dimensions shall be shown on drawings.
checkpoint-status | 463599e0-f64a-411d-80ba-25b29746c924 |  | checkpoint | Location of conduits shall be shown on the drawings.
checkpoint-status | 0ff3d4ec-c922-4383-b727-941667a0a9c7 |  | checkpoint | After Installation all conduits shall be free from foreign matter and from rough edges which could damage the cable during Installation.
checkpoint-status | d8d3c5e2-b7c3-453d-bc31-8bbeee73a664 |  | checkpoint | Where practicable conduits shall enter and exit the pit at the same height and orientation.
checkpoint-status | 24a9ddd1-3b9a-49f7-b0cb-fb9ad99465a4 |  | checkpoint | Bedding of Conduit and Pit
label | 0b9e2f92-0bb8-50e4-aa20-98370962d322 |  | note | Conduits and pits shall be bedded on approved bedding material.
label | 67d93714-18fb-5ad8-bdcf-fbad1e303f4b |  | note | Bedding material shall be 150mm above top of conduit
label | b00f964f-842d-5047-a638-262d6379fde2 |  | note | Orange marker tape installed with the words DANGER Electrical Cable buried below, laid in the trench 150mm below ground level.
checkpoint-status | 3dd3db69-1383-484d-b172-e2798f0a782c |  | checkpoint | Conduit Pits
label | b577a8d2-4b70-5dca-93be-f95a8abe2224 |  | note | Conduit entering and exiting a pit shall conform to the locations and dimensions shown on construction drawings and specifications.
label | 4c130786-6738-50a8-b0a2-656ee60e4680 |  | note | Conduits shall protrude into pits at least 50 mm and not more than 100 mm.
label | a50a204a-aaad-58c5-870a-e5f36fad0ae0 |  | note | Where practicable, conduits shall enter and exit a pit at the same height and orientation.
label | d46e2cd7-5961-5d9b-bb64-4197c5f64e68 |  | note | Sealing around conduits where they enter the pit is to be undertaken on the inside and outside of the pit.
label | 27da49d6-a277-561d-89ac-651d35ba930c |  | note | All pit lids to be labelled �ELECTRIC CABLES� and directional arrows set flush in the ground.
label | f6c08634-e720-5f78-8dbc-09669757a677 |  | note | All pits to be recessed with removable lids (Class B Steel Lids) to accommodate a padlock.
holdpoint | 129c242e-79f1-44b8-a96b-55deef4bfcf5 |  | signoff | request Signoff/ Raise Remedial
checkpoint-status | f7f5122b-16a6-41bb-bdeb-698151e94993 |  | checkpoint | Bell mouths to be installed where possible and correctly colour coded.
checkpoint-status | d227f617-150d-4944-948f-e4d82e438fb4 |  | checkpoint | Draw Rope Installation
label | 11524846-2f17-5ecb-a9f0-767c053fc943 |  | note | Draw rope shall be installed in each conduit run and shall extend a minimum of 500 mm above the top of pit collar.
label | 6d66396e-a727-51be-a97c-b3c00aa08cfc |  | note | Rope ends shall be firmly secured to prevent the ends being lost in a conduit.
checkpoint-status | 42318634-01c6-499c-8192-020a646b8df3 |  | checkpoint | As-built drawings completed.
holdpoint | 202a265b-4a86-4a9c-9680-b7c745734b01 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 2baeceb8-38d8-4273-93a3-5e95292911a0 |  | checklist | Pressure Test Report QCC-01.01 |  |  |  |  | Yes | Pressure Test Report QCC-01.01 | 47e74aba-1a0a-48ca-bcd5-30013cba44bf
checkpoint-status | ea703a41-ec2f-42c2-b741-d07e7c401b23 |  | checkpoint | Details of pressure test
text | 125a1f58-fb93-4fca-b207-81062af299ba |  | textbox | System Name/No.
text | 42b4109d-b3ba-450d-a96a-9217ffe123f7 |  | textbox | Location / Drawing No.
text | ddddbb20-aebf-4150-af44-058724908df6 |  | textbox | Test Instrument & Serial Number.
text | 1ffb4b68-825a-4ff9-a9c6-87fa9700d497 |  | textbox | Normal Working Pressure
text | 22d523d8-c31a-4752-ba5d-2a1ebce470fe |  | textbox | Start test ambient temperature
text | c20847d5-6182-4dec-9899-d1888d45e3d4 |  | textbox | Start test date
text | 31e3a80b-edab-4454-bb5f-ac357745cc76 |  | textbox | Start test time
text | 917ef879-4510-4dcc-a2c1-691a80ea5c5f |  | textbox | Start test pressure
text | dd5b4735-e182-4d04-841c-f425c1267348 |  | textbox | Finish test ambient temperature
text | 2c810d16-e75f-4644-99cc-359aa4d8a695 |  | textbox | Finish test date
text | b675deb2-9fad-453e-be71-589c96095ef0 |  | textbox | Finish test time
text | 4e71ffa8-f76f-4832-8216-a4f15f2ff734 |  | textbox | Finish test pressure
text | cbeee8b8-03d5-46b6-a5ea-8522baa6875f |  | textbox | Corrected pressure at test completion
label | 7990a0c7-14a7-4f43-b773-fb56a6ae93c1 |  | note | Attach photos of the gauges as required
label | 6059a464-043f-4bd0-8b04-c2f8cbad5042 |  | note | FORMULA :
label | 71330246-4fe0-4294-921b-beb085d495cb |  | note | Pc = P x (Ts + 273) / (T + 273) kpa
label | 1a04a208-c0e5-4d52-ad08-4300aed9e545 |  | note | Pc = P x ( +273 ) / ( + 273) kPa
label | 9f8ea800-f4bb-49af-a8b5-389758071961 |  | note | Pc = kPa
label | 57105522-72b0-4769-8f26-25359e8f238e |  | note | WHERE:-
label | 26a80af3-2173-40a6-9868-00ed118f3db0 |  | note | P = PRESSURE REQUIRING CORRECTION i.e. PRESSURE ACTUALLY READ AT TEST END
label | ed49c168-0d5b-4b0f-a64e-e31771f502a8 |  | note | Pc = CORRECTED PRESSURE
label | 241239a4-61f2-4368-98de-7a04516ebd82 |  | note | Ts = AMBIENT TEMPERATURE oC AT START OF TEST
label | 8e6e5ef8-edf4-47ec-9cd1-094d5e762d8d |  | note | T = AMBIENT TEMPERATURE oC AT SAME TIME OF READING P.
checklist-flat | dc5debdb-78dd-41df-9d0d-7175d51df667 |  | checklist | Trench Pipe Riser Installation Checklist |  |  |  |  | Yes | Trench Pipe Riser Installation Checklist | 49ab133b-deac-4693-89d0-576f5af3330c
checkpoint-status | 202c1457-00e8-45cc-a9b0-96400a8f8c13 |  | checkpoint | RDM & Consent Approval received by the client and approved?
checkpoint-status | 7daeeea3-35bf-4161-8815-2566626375ba |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | a5e9b983-bfa3-4fc2-adb2-24dbab8c0672 |  | checkpoint | Confirm trench depth, width and pipe alignment.
checkpoint-status | 2e7a780f-196b-4d1b-a6e0-a1c448c36e7c |  | checkpoint | All pipe flanges are capped, and ball valve installed on pipe ends exiting the trench.
checkpoint-status | 775b3bbe-579b-4041-aa6e-77949cffe878 |  | checkpoint | Each pipe shall be pressure tested prior to installation , Refer to separate pressure test report QCC-01.01
checkpoint-status | 3af545b2-1344-450d-a87c-ce6dd3dfc5f3 |  | checkpoint | 100Kpa of air to remain in pipework to verify no leakage, Refer to separate pressure test report QCC-01.01
checkpoint-status | 8d53cfa0-a2bd-41e4-98cb-e5090f5126fe |  | checkpoint | Number of pipework dimensions shall be shown on drawings.
checkpoint-status | 0f01edef-aad1-4f6a-ba4b-c885a1a8fb93 |  | checkpoint | Location of pipework shall be shown on the drawings.
checkpoint-status | 151b52dd-ba2d-4afb-a04a-cc4aac9b792d |  | checkpoint | Pipework exiting the trench shall conform to the location and dimensions shown on construction drawings and specification.
checkpoint-status | 79d455d7-8c87-49f3-a4b6-389e05da6bf9 |  | checkpoint | Before backfilling inspect all installed pipework and insulation for damage
checkpoint-status | 22c2ead9-6a8c-4fe6-98ef-c247518d52cd |  | checkpoint | Pipework pressure to be verified of no pressure drop prior to connecting to mains pipework
checkpoint-status | d2b04c28-bef1-4754-a1e2-e973211527db |  | checkpoint | As-Builts Completed.
holdpoint | 73c83ccf-d94e-4b6a-aa1e-0e83384c3ca8 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B5A - Area valve service units – closure and zoning test |  |  |  |  | Yes | B5A - Area valve service units – closure and zoning test | 4c82e0c2-a1b8-40f4-bbc5-1ad1e7d32e4f
checkpoint-status |  |  | checkpoint | B5A - Area valve service units – closure and zoning test complete
text | 3f188841-27cb-5fe2-8010-d431ce8b9edb |  | textbox | Plant ref
text | d8fddecd-8b84-533f-8b37-36fc828ca71d |  | textbox | Test by
text | 21b05d50-8c3d-58e9-9abd-5b2c3022e457 |  | textbox | Test date
text | 2a0fe54e-529a-5080-ac6a-f32f9488fc7e |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the AVSUs was tested in accordance with paragraphs 15.63–15.68 on the pipeline system as follows:
text | 1d8c4c2e-d295-5b05-97de-94e7233c1264 |  | textbox | AVSU number
text | bf563092-dbd7-5afb-b8ed-b353a9db5152 |  | textbox | Test pressure (kPa)
text | 7f5ee32d-ea33-5a6f-96fe-fc3d08dcf775 |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | 09015f56-ddd9-507b-8161-10605e095e8e |  | textbox | Terminal units controlled (total no)
text | 33b28bc6-34f7-5b1a-b986-cd75eb33b712 |  | textbox | Terminal unit labelling
text | 583d9847-0dd5-5a13-bfad-c54ecb56372a |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 7c276675-ecaf-513d-84b1-571d29344e95 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | f182c6a2-c83a-5532-a0b2-477f07fe08b8 |  | textbox | Consultant Name
checklist-flat | 68c8296b-1494-4c30-991b-785b37ce0b40 |  | checklist | Project Details |  |  |  |  | Yes | Project Details | 51f170ee-0a3a-41ea-bf26-683743dc17d2
checkpoint-status | 08b8e56a-f13a-4198-99cc-0515de89b333 |  | checkpoint | Project Information
text | b6deda1f-d359-47ad-8507-719dc8afe130 |  | textbox | Project Name:
text | 2c5f2213-0e59-43bb-8f75-04b868c594a1 |  | textbox | Project Address:
text | bb311aed-d63c-427b-9031-081bb148d86b |  | textbox | AE Smith Site Manager:
text | 3ed7586f-75c1-49e4-82a2-88dd04bbeecb |  | textbox | Consultant:
text | 10ea1d41-1768-4262-a1aa-060af1a01618 |  | textbox | Client
checkpoint-no-status | 0d418e81-f3d0-47a5-9552-fb4b3cca3e14 |  | checkpoint | Quality Plan for the Project
checklist-flat |  |  | checklist | Passivisation |  |  |  |  | Yes | Flushing - Passivisation | 52f55ada-5e95-4345-b6bc-d4aee4334b16
checkpoint-status |  |  | checkpoint | Confirmed all terminals backward & forward flushed
checkpoint-status |  |  | checkpoint | Confirmed the system water quality is as close to the make-up water quality as possible.
checkpoint-status |  |  | checkpoint | Test make-up and system water to compare
checkpoint-status |  |  | checkpoint | pH
text | 29eea1a7-d0bb-5374-8eae-0acdfff710d1 |  | textbox | Make-up Water
text | d734bb5e-a767-5fdd-b913-b0e378238381 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Conductivity
text | 7dfe3dc6-7ed0-5168-bdf5-3aceb8861fc6 |  | textbox | Make-up Water
text | 1c771e38-c82d-50f5-abae-f13f72684c4b |  | textbox | System Water
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 37cf8be9-2958-5ac0-9d2b-2ecc2029e95c |  | textbox | Make-up Water
text | cd97be46-dc89-51d7-a64f-3c29e4d11950 |  | textbox | System Water
checkpoint-status |  |  | checkpoint | Inhibitor chemical(s) added.
text | d394c224-ee94-5803-b23e-197445ad7d27 |  | textbox | Enter Date & Time
text | 86a113ee-8710-568f-8662-ea985824b2e0 |  | textbox | Name of chemical and SDS
text | 24384c15-a1d6-5e31-a13e-b7134e2b46c5 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Biocide chemical(s) added.
text | a79de3c0-f46c-5086-83c9-7065b6203384 |  | textbox | Enter Date & Time
text | 93366bc8-f044-5fbe-8912-8fd786153837 |  | textbox | Name of chemical and SDS
text | f99e3c82-1cc4-51d4-95a0-ae60d15d14c9 |  | textbox | Name of chemical and SDS
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
select | e06a56af-888d-5d3c-9e80-e962c820755a |  | dropdown | Is there any neutralisation chemical added as per chemical specialist advise? | Yes,No
text | 4f4f0c1f-31cf-5eb2-9989-26bf390d501f |  | textbox | If Yes, enter name and quantiy
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Flushing" and dates.
text | e80533d2-f4bd-5037-ab4c-7d9bb5b15a93 |  | textbox | Enter Date & Time
checkpoint-status |  |  | checkpoint | Sulphate
text | c8ceb271-172f-5601-a923-eb9acea2edfa |  | textbox | Site measurement
text | de5bab15-c0b5-5743-8996-d4450727a254 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | 154b48e4-496e-578e-96c3-0918f6949803 |  | textbox | Site measurement
text | aa495f6e-3fb2-57cf-9b16-471eac81e60a |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 7a6d4ba6-c369-581b-891e-fb75ab3d55c6 |  | textbox | Site measurement
text | d3cc16ae-d29c-5ced-93a4-8bdf21dad3f9 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | fa4d484e-c238-552e-a32e-b77fd944f300 |  | textbox | Site measurement
text | 50ceee72-44a6-5357-8e13-5d429a9163a7 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 5fc3d547-c67d-54f2-8db5-0427a593fbf0 |  | textbox | Site measurement
text | 57527c50-7003-5c8f-a4c6-cec1787fc448 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | aaadba5e-43d6-57c5-9d73-37dd3eb364b7 |  | textbox | Site measurement
text | 52f86626-5e02-58c2-9e98-ef174b0304e4 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 383c61f1-2800-51aa-af61-113bd30c458a |  | textbox | Site measurement
text | 6cb914f7-171d-5ea8-89f0-07be8cfd56bf |  | textbox | Lab test results
checklist-flat | ef2c9b78-1c6d-4fa6-8494-8a3d34acbad1 |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation | 587a1ea2-2d98-4741-ba46-97a1e1066ff2
checkpoint-status | b1a4af62-9333-4280-a529-7825350fe64a |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | f5ba4de4-fc2b-425f-848e-50c68f6eafa6 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 3c37ebf1-7478-4272-ac50-916c999f0b14 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 1f5f14d0-0a46-5076-942c-70387bd78029 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 6a4a5612-500c-5daa-bd17-158ae30120b8 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 66dda95b-a0c2-480b-b08d-f6b2b72b9e26 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | a8c24b3e-58e0-422a-96b1-35c9232254ea |  | checkpoint | Location of pipe
label | 45226daf-6ddc-5f22-b9bb-9acd558e6145 |  | note | Shall be as shown on the drawings
label | a5246ab5-35fc-533a-b91d-6751d7cac815 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | 407771b4-c998-4e44-8c81-6fa5d0efcd52 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | d1cdc9b0-6e1e-4915-af80-0e2a8f247346 |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | f3722075-ca1e-4c00-9c18-2ab560e3d02e |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 199c706a-f340-46b6-9060-509c9f712a10 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | c85e8094-f833-4797-a369-0165404fe739 |  | checkpoint | Install valves, tees and bends
label | be38ee2f-c50f-5cd6-a263-61d2ff548f69 |  | note | Install all connections as per construction drawings
label | 854b0cf7-bceb-5a8c-bf65-f3f39f7a1bac |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | 7000a464-b8f7-44e7-ab56-bfe1c5e247a4 |  | checkpoint | Installation of ductile iron bends
label | 239721b3-cd49-5229-ad74-33b6b8f3e1fe |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | 870c7f91-0842-5318-ae66-2460a7e070f9 |  | note | Ensure correct gaskets are installed.
label | c89b836f-47cb-5356-9c6b-993f45c05393 |  | note | Washers installed on both sides of the flange.
label | 31696213-b74a-56ab-b33d-6caed3a04cbb |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | 50ba9efa-0143-40a0-b7fb-23772d49d35f |  | checkpoint | Install Thrust and Anchor Blocks
label | 8d55a9f7-0068-5557-9082-1fefd9343b29 |  | note | Minimum dimensions as per IFC drawings.
label | 03ef9c7c-b704-55b1-94a2-6735ab38d270 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 98962c2f-97c6-4dd8-9289-d82f083be9a5 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | d197186e-5f6a-4ac5-98e6-9da1a5d8fef6 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 61d9d852-7ecd-5861-a244-c91d0f6396dd |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | f7077cef-3021-58ed-b88e-8fec14790ab5 |  | note | Ensure each test length is capped and ball valve installed.
label | e444efc0-92d9-5d01-bda1-d6877f023ef8 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | adc2a524-0490-549e-bf2d-5fc9217af438 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 7b5cfb5a-3e20-44fa-8397-e16bc0dff973 |  | checkpoint | Introduction of Air to 300 kPa
label | 7f2d9410-77f4-5211-b135-0ceb2a497fd4 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | f54a9352-5577-55ab-9ff9-43c105880bad |  | note | Monitor for any drop-in pressure.
label | 4126733c-45e2-5e4c-8b7b-8576d8fe8f17 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 9a127470-f19d-4d84-854a-544d47b83642 |  | checkpoint | Increasing Test Pressure
label | 012fd3ad-5953-580b-b117-92a9225d48f5 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 9bce60e2-322f-4ae7-bf33-1d43167fcfbf |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 1f012bda-dc7f-49f3-bead-30c191a85678 |  | checkpoint | Installation of Trace Wire
label | 5f304721-e92b-5fbd-af5a-41c3fc4507fb |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 0e802672-3652-5d6e-8f9d-3987542f091c |  | note | Test Trace Wire following installation.
checkpoint-status | e1706b07-87c1-463b-8e8a-ec10239d8048 |  | checkpoint | As-Builts Completed.
holdpoint | 54c918c7-8c76-4c87-9a13-f313df2a3332 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 9d6c565b-f253-4596-bb05-46d6a691db41 |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation V2 |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation V2 | 63ebb7af-b746-469b-943a-e18a0b56d36d
checkpoint-status | 34baaa2e-b195-4a67-a624-f04b67940c9e |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 94bbd88b-f59d-439c-9e3c-8138f2eace48 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 0ded29b8-8e75-4abc-8d28-b168c8e0e5e5 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 8a2b5a6d-6a16-51fc-8067-377eda533c6f |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 2c450017-498e-5a10-9713-b3fde1bd0b7f |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | a8d9778b-60dc-40e2-877c-2192a8784454 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | f7b8eb7a-7638-4fce-9eb7-059ea2d19682 |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | cf578c5e-7fd3-4bb8-ad87-d100fcfbd2c9 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | 8757ff17-c394-435d-a1d1-ded3af645644 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | e00ef6bf-4638-49d0-8c8e-7b173652de7d |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | c83c7d6a-c204-4ef3-b1bc-5297bcbf8972 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 0eb2a4d0-1363-45c7-8ffb-4195d96ce303 |  | checkpoint | Install , valves , tees and bends
label | 6d2e75d6-6429-5360-851a-12d40b134091 |  | note | Connections are installed as per construction drawings ?
label | 64515719-b52b-5eef-af76-babf7be7b7f6 |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | 31f85ed0-8883-4f7d-a0c0-dee0986f4376 |  | checkpoint | Install Thrust and Anchor Blocks
label | a2a67560-6c6e-5da9-b268-2b1a6565fb6e |  | note | Minimum dimensions as per IFC Drawing
label | e788e86f-e60f-57fe-8360-15368cf44f9f |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
holdpoint | 0ee75971-9a71-42ee-b9a0-e90a332d8ee3 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | ba97e28a-bbdd-4c4a-a668-af8588fc39f7 |  | checkpoint | Installation of Trace Wire
label | 93d2ef52-fa63-5d43-ad9d-5e99fe896ad6 |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | 398d15e4-aece-5a93-80f8-23b5c5ef2e9e |  | note | Test Trace Wire as per Specification 5.20.4
holdpoint | 187ece12-6a1b-4cfd-8c3e-fadc9404c027 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | e97494c0-ffdc-4f2f-85ec-834abc8661b5 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 252ef7a2-d5b5-4173-ac05-ddcc94f0d077 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 57378776-d20c-57c3-9325-b2ba8795fca7 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | d817ff62-916b-5332-b981-0862e132787e |  | note | Ensure all valves in the system are in the correct position and tagged �DO NOT OPEN� or �DO NOT CLOSE�
label | 26576f00-a654-5bad-bb74-62c05da02aa5 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | c176e0a9-0b3b-4f4a-8a8c-42d9fc239024 |  | checkpoint | Introduction of Air to 300 kPa
label | 0b082f78-8d69-5c70-a875-2f07632fe8c2 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 45904687-04a4-50ae-8bd5-ad93d97c16bd |  | note | Monitor for any drop-in pressure.
label | a7896bf2-fbca-5ab4-8168-bba00fd2dc92 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | f6cb6737-964f-4d95-855c-25624eae2d6c |  | checkpoint | Increasing Test Pressure
label | 7f371678-a8dd-585c-98d0-f62792bed120 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | a505c522-0a1f-438e-9990-ebc2242518a3 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 56a83a8a-3baa-4ab7-9c15-7ed835d2c74d |  | checkpoint | As-Builts Completed.
holdpoint | c034202d-d567-46e6-ab66-2b06808412be |  | signoff | Request Signoff/ Raise Remedial
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0025 - Combined Services Fire Hydrostatic Pressure Test | 6b798733-a1f8-4a1b-829d-557b63ec8fe2
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | ddaac82d-73b2-5c3e-9463-82880025c123 |  | note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | 9ea9f9e7-02d1-540c-a2d3-d54b82df1b82 |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | d389eef1-2bbd-59c8-b9ca-498542d615a4 |  | note | • Specifications & QA Documents Approved
label | fe930a65-cb5a-507b-9e98-d1d78b272249 |  | note | • Drawings are confirmed
label | c13facd0-89e9-5a5b-a5ee-15126d6ef9c6 |  | note | • Equipment fit for purpose
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | fe040b4e-7209-53c2-bcf1-a764d9db1984 |  | note | CRITERIA - 1. Check pump is rated for pressure test
label | 6803b4f2-5fa3-50b7-ae7e-2d8b16407810 |  | note | 2. Check all supplied attachments are correct and in good order
label | 872337b3-eb67-5fd0-ab35-491ece31610d |  | note | 3. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Connect pump to Fire ring mains
label | 326d31c6-c948-5a59-adaf-97aae3666e09 |  | note | CRITERIA - Confirm connections are safe and correct
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | ba12ba2c-be4e-5057-87bf-17ab6bc1ae0e |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill Fire ring mains with domestic water
label | 8c5bd040-6556-5bb1-bdbd-80df0591b002 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Valves at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 15.5 Bar
label | 96e9d537-0b2b-5fa9-a622-62b947f474f3 |  | note | CRITERIA - Slowly raise system pressure to 15.5 Bar
label | f19c49b2-1b68-5036-91dd-0bdb6fe5b9e9 |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 15.5 Bar pressure (START WITNESSED) - CPB/IR Hold Point
label | d5ffe3d4-7faf-5eb8-a46d-bfc68fca32f6 |  | note | CRITERIA - Record START time & photograph gauge
label | d68bcc9f-8e2f-5f9d-af92-fb3d0877bdb8 |  | note | • All relevant parties to witness starting pressure of 15.5 Bar
checkpoint-status |  |  | checkpoint | Hold 15.5 Bar pressure for 4Hours (END WITNESSED) - CPB/IR Hold Point
label | febe1665-48b1-5749-b600-01b1a1ee88dc |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 7b33bf0a-b13e-5949-94e3-a8c8ff3078ad |  | note | • All relevant parties to witness pressure of 15.5 Bar
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | a9a2c56d-01cd-5110-9c9c-0747b5b0ebf5 |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | d23527c9-b446-5f11-a84c-632e77a94fe3 |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results - CPB/IR Hold Point
label | a2fb66b0-f5a1-5260-aa10-ddae29eea7d3 |  | note | CRITERIA - All pipework pressure test reports shall be provided
checklist-flat |  |  | checklist | Dynamic Flushing Checklist |  |  |  |  | Yes | Flushing - Dynamic Flushing Checklist | 6e084e02-c297-4d38-868d-1afab78fe6ea
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | bf1da581-0bc0-5961-bb5e-695e242da15a |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Turn the pump on and run it at 20 Hz (or at minimum speed)
checkpoint-status |  |  | checkpoint | Increase the pump speed to 50 Hz and measure the total waterflow
text | 04945ed9-f33a-54c6-b8fa-773fadeed295 |  | textbox | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Circulate water for 2-4 hours by sampling the drain water quality. Record the duration.
label | 966c6db6-3f90-5a24-845b-b7451889c68d |  | note | The duration of this process depends on the size of the system and may required to be extended.
text | afd1ffd9-1337-5990-bf41-199543925580 |  | textbox | Duration
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the dynamic flushing
checklist-sectioned |  |  | checklist | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test | 7dc8f696-8230-456a-9c5a-4ecbc25d9be7
checkpoint-group |  |  | section | MATERIAL COMPLIANCE
checkpoint-status |  |  | checkpoint | RDM & Consent Approval - CPB Hold Point
label | 364328f9-36a3-5b2c-b5cf-b416e1b186ab |  | note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint-status |  |  | checkpoint | General - CPB Hold Point
label | ce747cb2-e1c8-5540-8d92-8f22bcebfa57 |  | note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | 4fb45bcd-b4d3-55bb-9dbd-e1ccdddfa270 |  | note | • Specifications & QA Documents Approved
label | d8f67274-af4d-5138-aea2-bb1cc149c713 |  | note | • Drawings are confirmed
label | 7d77392b-8a6f-5aec-8fa0-6e48207e31a3 |  | note | • Equipment fit for purpose
checkpoint-group |  |  | section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint-status |  |  | checkpoint | Confirm Flushing & Disinfection of Pipework - CPB Hold Point
label | a60a0407-ab24-5f78-be6b-954ca045075d |  | note | CRITERIA - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
label | 994be114-e3ab-52de-89d7-ce0cd6d49480 |  | note | 2. Ensure system sterilization completed.
label | b485c896-359f-5f89-bba8-4fa6cfa5026e |  | note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
label | 32c4a5f8-605d-5d8e-a6e9-77175e27353b |  | note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
checkpoint-status |  |  | checkpoint | Accept delivery of pump to site
label | f9d9c6a7-3227-5983-a048-5b6172f6d839 |  | note | CRITERIA - 5. Check pump is rated for pressure test
label | 59f5d9e9-066c-59b6-ab08-5060f029ea75 |  | note | 6. Check all supplied attachments are correct and in good order
label | a7b6e816-dda9-51fd-9789-85ff8f2561c2 |  | note | 7. Check fluid levels & fill as necessary
checkpoint-status |  |  | checkpoint | Isolate: Mains water Storage Tanks
label | c25712bf-054f-50e7-8135-54711ba9d83b |  | note | CRITERIA - 1. Check Mains water is isolated
label | 36222563-a925-571e-9519-14208fb7356f |  | note | 2. Check Storage Tank is isolated
checkpoint-status |  |  | checkpoint | Connect pump to DWC ring mains
label | 7e05a974-1972-5212-b6d7-0e204a268122 |  | note | CRITERIA - Confirm connections are safe and correct
checkpoint-status |  |  | checkpoint | Connect calibrated gauges for pressure test
label | 757c45f0-e77a-5282-900a-e4b97ec950f1 |  | note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
checkpoint-group |  |  | section | HYDROSTATIC TEST
checkpoint-status |  |  | checkpoint | Fill DWC ring mains with domestic water
label | 7e8a7c6b-2bbb-504c-b3a2-d584133afd71 |  | note | CRITERIA - Completely fill closed loop system with water releasing all air from the Taps at each Building
checkpoint-status |  |  | checkpoint | Gradually increase system pressure to 1550kPa
label | 6d49d15a-9b6f-531b-b20f-9958bab70ec5 |  | note | CRITERIA - Slowly raise system pressure to 1550kPa
label | 9cdb3d70-962a-5792-ae35-c3e299e90ff5 |  | note | • Checking for any signs of leaks or pressure drops
checkpoint-status |  |  | checkpoint | Stabilize 1550kPa pressure (START WITNESSED) - CPB/IR Hold Point
label | 37b3a49f-da39-550e-8e99-0225cbff528c |  | note | CRITERIA - Record START time & photograph gauge
label | cf1337ba-4af2-5025-8e77-542bf1312484 |  | note | • All relevant parties to witness starting pressure of 1550kPa
checkpoint-status |  |  | checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED) - CPB/IR Hold Point
label | 098842f1-fda4-5f48-8596-d48949ed1291 |  | note | CRITERIA - Record FINISH time & photograph gauge
label | 0bb33407-1f47-5c7a-b0b4-e697f568f0b4 |  | note | • All relevant parties to witness pressure of 1550kPa
checkpoint-status |  |  | checkpoint | Pressure released or reduced for next test
label | 33ad2453-b7dd-57f4-ba94-bb9a0d9cf603 |  | note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint-status |  |  | checkpoint | Discharge pressure leave system in a safe state
label | a3d38a40-98e1-5506-858f-9cf6a9606d8b |  | note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
checkpoint-group |  |  | section | COMPLETION RECORDS
checkpoint-status |  |  | checkpoint | Testing Results - CPB/IR Hold Point
label | b93d702f-285b-5ca3-8c45-c5e9072cdb50 |  | note | CRITERIA - All pipework pressure test reports shall be provided
checklist-flat |  |  | checklist | Cleaning Agent Removal |  |  |  |  | Yes | Flushing - Cleaning Agent Removal | 88f94467-38bf-4c09-9437-fd27b1bfa3c2
checkpoint-status |  |  | checkpoint | All sections' valves are opened.
text | 387f5a8c-2f8e-5e6a-9e8a-fa39172fd1a6 |  | textbox | Make-up valve is opened.
text | 8d5310cb-a910-59b5-8234-bcecf1ef5549 |  | textbox | Date
text | d2ea0897-4501-5d58-abcb-c8957369731b |  | textbox | Main drain valve at the pump is open.
text | a4f73f37-6b8d-54d4-a97d-dff96b3bd8c2 |  | textbox | Drain waterflow (l/s)
text | 15f59b9d-2764-505b-9263-2e1b7e7f6d97 |  | textbox | Drain location
text | aaf21114-f0e7-5bf4-bd23-809d7689cccb |  | textbox | Drain duration (minutes)
text | d1e2ff21-e1e5-5fb2-b542-ba8023b53806 |  | textbox | Calculated drain water volume (L)
text | 691538c3-36fd-5b77-89d2-bb77b58ec313 |  | textbox | Special trade waste water permit obtained.
checkpoint-status |  |  | checkpoint | Adequate make-up water available. System's static pressure is not decreasing.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | Circulate and replace water until the water runs clear.
checkpoint-status |  |  | checkpoint | Water sample is taken, and labeled as "End of Cleaning" and dates.
text | ffe255f3-ba7b-531b-89a6-062d8dac1ef5 |  | textbox | Date
checkpoint-status |  |  | checkpoint | Sulphate
text | 5629241d-2130-55e0-9981-aa28ab6cbef8 |  | textbox | Site measurement
text | 27344e09-ff70-5e5d-abb4-9376deec5d8a |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | 8b7a15ba-8508-58e6-a508-e248db0145d6 |  | textbox | Site measurement
text | 195fa390-3107-56a8-b657-0797378c1594 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | 787d0cb3-f582-5c9a-93a4-8f63eeae9463 |  | textbox | Site measurement
text | d2ac8f0e-4a93-59ee-9204-b0c81caee30f |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 351d69dc-7bf0-5c3b-bf68-655f1573ee41 |  | textbox | Site measurement
text | f3fbb227-d8c7-571b-9fc2-3086859d0ab2 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | c0c7f750-e8a5-534b-bb9f-8576d4558e2f |  | textbox | Site measurement
text | da491b7b-fe93-5576-882c-f34bede50622 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | 2ac92b2d-fa2f-5b6b-8dbb-e56178b3558a |  | textbox | Site measurement
text | e473df91-c8cf-5eae-920d-15693433e6f2 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | c1f0c42e-c889-56cc-99c6-f4ad3991acd1 |  | textbox | Site measurement
text | 72395e68-6a16-5c9c-8100-b29a8a279e12 |  | textbox | Lab test results
checklist-flat | 1e4c9fdb-23f5-4942-9283-beedac22379e |  | checklist | Seismic Joint Building Connection |  |  |  |  | Yes | Seismic Joint Building Connection | 8a92446d-ecde-49ab-a73c-0796d9480c2a
checkpoint-status | 1f32e5d5-30b0-415a-b8d7-3f49d342cd3d |  | checkpoint | Waterproofing
checkpoint-status | 89d06f4c-a404-434d-bb8e-1a114c793e78 |  | checkpoint | Insulation
checkpoint-status | dd96b2a5-6f90-486d-8755-e1b19ac86661 |  | checkpoint | Victaulic Coupler
checkpoint-status | f3343bde-d02f-4dc5-8e50-fe6002d420bb |  | checkpoint | Installed Correctly
holdpoint | eb96817a-c3a9-4635-a337-935db9c0b1a5 |  | signoff | CPB signoff
checklist-flat | 85ad3acf-6ec0-4009-ae36-2612ad0b3aac |  | checklist | LV Installation |  |  |  |  | Yes | LV Installation | 92f81516-5133-4c71-af8a-3bae8e6119d3
checkpoint-status | a4a34d94-38f9-4de9-b965-5d0dcb1c8ca4 |  | checkpoint | ROM & consent approval received by the client and approved?
checkpoint-status | 5735e288-6279-4ac0-ab24-02a7073f1aee |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
label | 07bdac21-abd5-5e80-a89a-9430e2d78bb0 |  | note | Attach: material inspection checklist
checkpoint-status | 42776c8c-8a3a-4d87-a687-c5bbbfa4720b |  | checkpoint | Inspect trench depth, width & cable rout
label | d2ebccb7-58b5-50fe-a07a-fec41fecd601 |  | note | Shall be as shown on the drawings,
label | e5f3c9cc-6e5a-52cf-90d7-aa2735d8abea |  | note | Attach: Excavation Checklist & Photos
holdpoint | 8454d5cd-e85b-44dd-b050-8057ca15b79d |  | signoff | CPB HP - Documents
checkpoint-status | 27eafdae-f547-4dbd-b485-2a92733404d8 |  | checkpoint | Drum Delivery Test Certificate
label | 2e75b697-bb1b-5d75-9e49-5c076f9e391a |  | note | Attach documentation
checkpoint-status | de2ae530-8dff-4b45-809c-d310f9c5d51d |  | checkpoint | Pre-haul Checks
label | 2229b277-8f9e-526c-bb4e-7d8dcad0329b |  | note | Verify Cable is in good order and condition prior to haulage
checkpoint-status | 5d22eea0-2485-4d5b-bae6-7a04f0a77533 |  | checkpoint | Confirm correct lubricant available for use, where applicable
label | 78d4f6dd-5816-584e-b005-65552b8169fe |  | note | Verify correct type, and that sufficient quantities are available
checkpoint-status | 75bad943-9d1a-4706-9e07-13620d7d2910 |  | checkpoint | Observe the Haul
label | 91824d22-848e-5a3a-a62f-1306d4379388 |  | note | Stop the haul if a potential risk of damage is identified
checkpoint-status | e27153ec-e28e-4006-900e-c89436220c60 |  | checkpoint | Inspect cable sheath during the haul
label | d6af3928-ca22-5b19-80d3-a2aec4ba7402 |  | note | Stop the haul if any damage is identified
checkpoint-status | d8eadef8-8402-45d8-a03a-75b05dc952ab |  | checkpoint | Inspect cable sheath at the completion of the haul
label | c28f0d56-1ca8-5360-81a7-e9aa35512b62 |  | note | identity an signs of damage
checkpoint-status | 9b0716d6-a5d5-4950-bac9-831745d9d997 |  | checkpoint | Install Seismic Loop
label | 96dc1008-cb58-5c10-8cb4-1506d9e3a828 |  | note | Visual Inspections
checkpoint-status | dc466216-a5d8-443a-b5d9-68e08e8187cb |  | checkpoint | Install cables into building and contain to prevent damage
label | a90fc230-b220-5e4c-984b-580195f98211 |  | note | Visual Inspections
checkpoint-status | d4900e25-eb4f-4b64-babb-05e9fd035a81 |  | checkpoint | Install lime & compact
label | 4454efa7-45dc-5b8d-b4ca-9b650e131a8c |  | note | Visual Inspections
label | 77afeb66-9833-5312-a05d-82bfe5ca149f |  | note | Check bedding depth
checkpoint-status | 73587f22-dca1-4886-8099-cb6f25f33c7d |  | checkpoint | Install Mag slab
label | 27582eb0-74f6-5cb3-a968-2439914c3043 |  | note | Visual Inspections
label | 97f9c548-72f5-5799-a8cc-2949d4f3b956 |  | note | Make sure Mag slab is covering the buried cabes
checkpoint-status | b3d63323-2c3f-4af9-b38b-c6f268e8f0ee |  | checkpoint | Test cables installed
label | 95fd9dab-f128-5040-bfa9-7f13d1212576 |  | note | Insulation Resistance Test
label | 88dc4eaa-9fed-5e54-a085-f710ffb49f72 |  | note | Continuity Test
checkpoint-status | d0b52220-902e-4912-a931-9f54bdc817cb |  | checkpoint | ITP Sign off Witness Points
label | c1e0bdf6-f949-5be1-9432-3c3c03b281de |  | note | 2.1 Inspect trench, depth, width & cable route
label | 407088aa-4c80-532e-90fb-496114fc03e6 |  | note | 2.2 Testing of cable prior to cable pulling/laying
label | bd4ed04e-886e-5050-b61f-1010ce5f6f99 |  | note | 3.1 Pre-haul checks
label | 1977695a-984a-52b6-a0e0-87f2a2d5e93b |  | note | 3.2 Confirm correct lubricant is available for use where applicable
label | 9d9a88d7-a53d-5711-928d-1bb68ca8864c |  | note | 3.3 Observe haul
label | f6f832bf-01f1-5eb1-a314-651bb4e4d30d |  | note | 3.4 Inspect cable sheath during the haul
label | 2eb0d5ad-b79d-5923-9eb0-8377437f3f84 |  | note | 3.5 Inspect cable sheath at the completion haul
label | e933b0d3-6929-5600-943c-85412a3a8504 |  | note | 3.6Install Seismic Loop
label | b80ce3be-95e6-5d23-82c1-07b137e1070f |  | note | 3.7 Install cables into Building and contain to prevent damage
label | c8e71726-69e5-5647-88dc-cb61bc8d1806 |  | note | 3.8 Install lime & compact
label | a849ac92-90e9-54a5-9f50-61d2028a2c58 |  | note | 3.9 Install Mag slab
label | 43f91434-cbca-58cc-950c-5b3efa0ac3e4 |  | note | 3.10 Test cables installed
holdpoint | 66edd581-05ae-481f-aba8-8cf42cd1aaab |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | 3da0192f-d716-413f-8ddc-bb034ad30a6a |  | checkpoint | Inspection by Supervisor
label | b334795e-0947-5c4f-8657-b1841d5677cb |  | note | QA check sheets, visual inspection and test requirements to AS/NZS 3000:2007 measurements verified
holdpoint | 46d70418-5a60-4f09-a514-1863abc1a3e8 |  | signoff | CPB & AES signoff / raise remedial
checkpoint-status | 15fca81c-8054-4c3c-ad4a-c9155efcca7d |  | checkpoint | Notice of completion
label | 2f7b1305-99c8-50d4-9427-889cd959eaf2 |  | note | Had back trench to CPB at Mag slab demarcation point.
holdpoint | add75cb1-6b27-48e5-8586-aca0ff64a214 |  | signoff | CPB & AES signoff / raise remedial
checklist-flat | cbaefad1-e904-48f8-8b3e-3e056a893a34 |  | checklist | Diesel Fuel Line Installation |  |  |  |  | Yes | Diesel Fuel Line Installation | 96b524d8-bc93-49d8-b675-6db0cb8722a3
checkpoint-status | c6e067d2-0ef4-4489-85c3-c9ea14fe6b36 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 21262c6d-74cd-4ef7-b133-346cc38d3982 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | f68685a3-d58e-42ab-b261-a03a5ec6de90 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | d513202f-7c46-5ff9-a5a1-665f7753bfc2 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 0d3564ab-54b9-5cfe-abc8-5580bb72a7ef |  | note | Ensure Trench complies with HSNO Regulations.
label | 069c0207-0e05-5c9e-8046-4d775e628768 |  | note | Trench Inspection Check Sheet to be completed.
holdpoint | 470a6195-9b40-4121-bc1b-1a7e4e1b4684 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 9d8ceb8d-add6-40ba-b540-a1b6e8b0d6f9 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
holdpoint | 5992b432-a468-45e6-9648-47cc90af6d5c |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | c15d1f41-2d83-4f90-b812-984c39bee08e |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | 3debae8a-1ffd-4386-8eb9-4ada205b279f |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | d73cb365-8823-440e-8e9a-e7ee98b9df29 |  | checkpoint | Pneumatic Pipework Pressure Testing.
label | 687b7cd7-afe8-556d-8a7e-f51eb6ba65ec |  | note | To be pressure tested to 1.5 times working pressure or not less than 350 kPa.
checkpoint-status | 164ef4d9-c064-4ae3-af0c-ce2ccd755af5 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 4892bb26-e5ac-5b2e-8a5d-639a4eacf5c7 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 61045abd-44dd-5403-9792-992883002d07 |  | note | Ensure each test length is capped and ball valve installed.
label | d9d2339e-d876-54d7-adfa-a57cd2d842f9 |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 37f8b629-9a2e-5351-b843-13df4e9c63ca |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | c949f0f0-f793-4ed9-802c-ab7e19a5605c |  | checkpoint | Introduction of Air to 300 kPa
label | 2e6d804f-7b18-5687-9ba5-ae5f83c9226c |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 6d795f7f-535d-5ef8-8cb4-3d73f34ac2ae |  | note | Monitor for any drop-in pressure.
label | 2bb6bdf3-d7a7-501e-9696-2f0684927d9c |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 80d4b49a-87b8-4628-821f-fbfb741ca8c5 |  | checkpoint | Increasing Test Pressure
label | 115cfb32-ac2a-5126-b2db-5cc9ba019ae9 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | dc685a2e-1287-4d91-bb2c-0a125a752d8a |  | checkpoint | Line Test Data Sheet Completed
checkpoint-status | ff61953e-1145-40f2-9b9e-338a946fe4a8 |  | checkpoint | Pipe Markers
label | a6ac4dd2-1857-5d9e-b904-cd58937b2a44 |  | note | Mark pipe route by markers set flush in ground above.
label | 51e997bd-82a5-5b8b-82de-e22469bd0809 |  | note | Markers shall by minimum 200 x 200 x 50 thick concrete slab with a brass plate fixed to top surface engraved: "FUEL PIPES UNDER" and directional arrows to indicate route.
label | 1eb1f3fb-e7fc-5606-963b-ad40d20b3019 |  | note | Marker Installation: Install at maximum 15m intervals and at all changes in direction.
label | b862928c-1085-59b0-a0b4-ea9f2a8f8e99 |  | note | Note: Pipe Markers are not required where pipe route is covered by a concrete slab
holdpoint | c89bedb6-0920-4583-abb6-f39c229ba531 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 578f8d43-a703-41ea-b5f1-2a622739d4cf |  | checkpoint | As-Builts Completed.
holdpoint | fd550b02-d98d-40cd-8fe2-d56a5815ad37 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | B5B - Line Valve Assemblies – Closure and Zoning Tests |  |  |  |  | Yes | B5B - Line Valve Assemblies – Closure and Zoning Tests | b1e8f073-aed9-420a-9096-aec1ce2162e8
checkpoint-status |  |  | checkpoint | B5B - Line Valve Assemblies – Closure and Zoning Tests complete
text | 543e1a20-032b-5a6f-b761-52d749f8d44f |  | textbox | Plant ref
text | 145c0be8-a724-5cc9-a6b9-682459374ace |  | textbox | Test by
text | 33bd98f6-aebe-5002-adff-bb0e2c6b1fa3 |  | textbox | Test date
text | 99b44c9f-a59a-5be6-b2cc-84295531a299 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | This is to certify that CLOSURE and ZONING of the LVAs was tested in accordance with paragraphs 15.63–15.65 on the pipeline system as follows:
text | 8c743915-cb5f-539f-a3b0-2c6599ff56ca |  | textbox | LVA number
text | 04b0648d-4767-597c-8501-a3acfe01523e |  | textbox | Test pressure (kPa)
text | 49652d50-7460-5491-b823-007374f6015c |  | textbox | Downstream/upstream pressure change after 15 min (kPa)
text | 6c90f2ec-b21c-58da-8526-db0d83dce625 |  | textbox | Terminal units controlled (total no)
text | 761a7300-3594-5b15-aaad-dae739848510 |  | textbox | Terminal unit labelling
text | 2800bf77-f483-5ce0-9bb7-dcc2102ddaca |  | textbox | Contractors representative:
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | e148d60f-4d12-550a-8680-1d3fa23ba2e1 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | a2076155-399a-5ef0-adc0-3f0fe6f06d17 |  | textbox | Consultant Name
checklist-flat | ec1354de-7626-474b-a8b4-fc7cbed034c0 |  | checklist | Combined Services HDPE Natural Gas Installation Part 2 of V3 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation Part 2 of V3 | b2405e2e-a40b-4a18-81df-b8c5cb899718
checkpoint-status | 2eabd90c-616f-4fa4-a244-03681f75bba5 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 731c5841-9b8d-5389-ac3f-4fdb57c311d1 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | f34c87b3-0d5a-507b-9f85-ff3614ed1abc |  | note | Excavation Checklist to be completed prior to installing services.
checkpoint-status | 5d6048c1-3f68-4a1b-b7cb-c22c5ff395cd |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | bbdafedc-5f86-4625-9ada-b5f44c70a9c6 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 6c7b726e-11b3-4735-836a-7b59b777bb87 |  | checkpoint | As-constructed survey
label | e5a27f82-a093-56bb-af59-74e85a6a61d7 |  | note | As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
checklist-flat |  |  | checklist | B7A - Functional Tests of Terminal Units |  |  |  |  | Yes | B7A - Functional Tests of Terminal Units | b6f5598b-5430-4e16-8d35-233160702798
checkpoint-status |  |  | checkpoint | B7A - Functional Tests of Terminal Units complete
text | 9a67787d-6889-5cbb-b55a-425de5093385 |  | textbox | Plant ref
text | 40f9a459-ddc9-54bb-ac4b-e703b14aa22e |  | textbox | Test by
text | 48d9a5af-8550-5da1-9c7e-9ef9983769d0 |  | textbox | Test date
text | 137cb4f0-e39e-5ad8-8f69-20521c738715 |  | textbox | Revision
text | 8c999aa7-ccd9-5d39-8a2c-efc38d0f16e3 |  | textbox | System
text | b18ebc36-50e2-5c4f-b961-5df90cb20496 |  | textbox | Specified flow (L/min)
text | 57905ed5-e904-5829-8deb-87eb11274873 |  | textbox | Specified pressure drop (kPa)
checkpoint-status |  |  | checkpoint | In accordance with the contract specification and paragraphs 15.77–15.78
text | 8825d3d9-109a-5065-9161-34211d6a312a |  | textbox | Terminal unit number
text | 0ff6ceaa-3e39-5d98-8e18-8d1f275171f4 |  | textbox | Room number
checkpoint-status |  |  | checkpoint | Specified flow achieved
boolean | 65874016-53bf-5c53-9f7b-053db7771b11 |  | tickbox | Yes
boolean | 02f98d83-7591-5883-a676-f9d3f8f608ba |  | tickbox | No
checkpoint-status |  |  | checkpoint | Specified pressure drop achieved
boolean | fc779ae7-2f8d-5e4b-bd7a-23a8dd479472 |  | tickbox | Yes
boolean | 5c695c01-371d-52d6-9595-1b9000b42b67 |  | tickbox | No
text | 8813e6c9-3b36-5991-9966-11954dc1196d |  | textbox | Mechanical function
text | 8cf6cae5-6333-5945-9b59-e346d3c2faab |  | textbox | Gas specificity
checklist-flat |  |  | checklist | Back-Flush |  |  |  |  | Yes | Flushing - Back-Flush | c62ec6e8-2d77-4347-874b-0e3f10c4ebc7
checkpoint-status |  |  | checkpoint | Chemical cleaning is completed and clear water is visible at the main drain valve.
checkpoint-status |  |  | checkpoint | Terminals backward and forward flushed and water drained at the terminals until clear water is visible.
text | d49dd505-4c4e-5084-a4a2-783c652aaf28 |  | textbox | List the terminals backward & forward flushed.
checkpoint-status |  |  | checkpoint | Water sample is taken from the furthest terminal, and labeled as "Back-flushed terminal" and dates.
text | adb804e5-53f1-58fc-aba2-fa20701ee5dc |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Sulphate
text | de4c374f-6437-5e67-bcb1-8790bb7401a6 |  | textbox | Site measurement
text | eaa17554-ac01-53ae-9009-6b60bbbcedbc |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Chloride
text | c48ebf69-9d9c-5048-ad87-6b8894b60eda |  | textbox | Site measurement
text | 45ff9395-d374-5724-91e1-cee651cc6ffe |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | pH
text | df66cd6c-d509-5230-b240-b74698acf78c |  | textbox | Site measurement
text | 0c9e1659-ca8e-5f93-83f5-7e4d7409d5a1 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Conductivity
text | 33a03400-1b6c-5e7f-a582-fa9c2ee7ddde |  | textbox | Site measurement
text | d384fdd5-9c67-5eea-a559-72fa2b3e4a47 |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | 131c1acd-22ac-5344-b05a-76ecf6c6de36 |  | textbox | Site measurement
text | c302f9ac-dfdc-5517-86c9-26c6c1afa98b |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | TVC (Total viable count: the total numbers of microorganisms, such as bacteria, yeast or mould species)
text | da2a0a0f-e64d-58c5-b0d1-c9517929ad1f |  | textbox | Site measurement
text | 4947459c-a226-5032-a45f-f31ee29facad |  | textbox | Lab test results
checkpoint-status |  |  | checkpoint | Pseudomonads (microorganism that can create biofilm)
text | 23f58ef3-141e-5e9f-a393-b4aee80df3e2 |  | textbox | Site measurement
text | 1e8c30a3-cdeb-5482-8cfd-2045883702ec |  | textbox | Lab test results
checklist-flat |  |  | checklist | Flushing Site Details |  |  |  |  | Yes | Flushing Site Details | c64ff571-f38f-4400-8bf4-de79888e05cc
checkpoint-status |  |  | checkpoint | Flushing Information collected correctly
text | 6a8b8e6c-7cac-5954-bb1e-09eba409ca1e |  | textbox | Job number
text | 1fcbd0f6-265e-5319-a884-d1d478242448 |  | textbox | Job name
text | 9a95aedf-ccc9-5fb5-b13a-ee883d8707a2 |  | textbox | Builder
select | c4a812da-14c7-5c3a-a2cf-0db4cf8b90b3 |  | dropdown | System Type | Domestic Cold Water, Chilled Water, Heating Hot Water, Low Temperature Heating Hot Water, High Temperature Heating Hot Water, Fire Hydrant
text | fdca6cd6-7dc9-591d-8e33-ed2f9bbe1d8a |  | textbox | System Volume (Litre)
text | c8584f47-3114-5ef0-a9de-de4f492a9f90 |  | textbox | Location
text | 3abf0074-3562-5dc6-a1f0-1cf0cfc1098c |  | textbox | Drawing
boolean | 0ab3c987-bced-5a02-b69a-c72faf0cf64d |  | tickbox | CIBSE Commissioning Code W
boolean | 4c3eea86-6a38-52a1-b1db-9fddeef806d6 |  | tickbox | BSRIA BG 29/2012
checklist-sectioned |  |  | checklist | Ductwork Leakage Test Certificate |  |  |  |  | Yes | Ductwork Leakage Test Certificate | ca88c439-b9c7-4db7-b2fe-cd03cd30325c
checkpoint-group |  |  | section | Part 1- Physical details
checkpoint-status |  |  | checkpoint | Physical details captured correctly
label | ea42365e-f135-5ee1-83a7-e639177b7cc4 |  | note | The issue of this certificate is notification that this sytem has passed and ready for witnessing. Its is to be witnessed within 7 days following the test.
text | ec9a5f62-b89c-52bb-bbb6-a342d9577cdf |  | textbox | Section of Ductwork Tested
text | 200fd813-25e2-5dd6-b4d9-99fd96caf9ca |  | textbox | Test Standard, Class & Pressurisation
text | 82d0cf53-d789-5afe-8b90-ea5f610bab52 |  | textbox | Test Static Pressure (Pa)
text | 046aed2f-6067-549a-83eb-a4a6d5ff1493 |  | textbox | Leakage Factor (l/s/m²)
text | 92d8ff73-0706-5676-9be3-5ec22db5ba41 |  | textbox | Surface area of duct under test (m²)
text | c15a36f6-bf98-543d-8a02-2f2c5b191e1e |  | textbox | Maximum permitted leage (l/s)
checkpoint-group |  |  | section | Part 2 - Results
checkpoint-status |  |  | checkpoint | Part 2 Completed
text | a93f8c43-92c3-51c1-948c-4f68f2bd03a8 |  | textbox | Test Rig Details
text | 6268d56f-497b-571d-a623-0d4ad0ee345c |  | textbox | Test Instrument Manufacturer / Model
text | b137233a-50c7-52b4-bf4e-12cd65ae0d3c |  | textbox | Serial number / Calibration date
text | c5aa1a5c-bbb5-5eb3-8594-aaead450afbd |  | textbox | Actual Duct Static Pressure (Pa)
text | 7c10b4cb-7ef3-5d77-8a3b-b12ec3de6e3a |  | textbox | Actual Airflow Leakage Rate (l/s)
text | ec8313fc-099f-54be-bfce-fdb7c213b812 |  | textbox | Calculated Leakage rate per m2 (l/s/m²)
text | e1379d3a-70cb-54cc-8954-9805fd99ae68 |  | textbox | Duration of test ( Airflow reading taken at end of test duration )
text | 42bbd8f4-9585-51c5-a3b9-29e1ef9a6483 |  | textbox | Test Outcome
checkpoint-group |  |  | section | Sign Off
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 63452085-e27c-586b-9bca-aace1c7b74ac |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | 247120d3-fbb2-5a2a-a5df-0affd35f3acb |  | textbox | Consultant Name
checkpoint-group |  |  | section | Photos
checkpoint-status |  |  | checkpoint | Start of Pressure test
checkpoint-status |  |  | checkpoint | Pressure test after recorded Duration
checkpoint-status |  |  | checkpoint | Photos Attached
checklist-flat | 72829b13-3b71-4657-9fd9-7a46d3546fec |  | checklist | Combined Services HDPE Natural Gas Installation V2 |  |  |  |  | Yes | Combined Services HDPE Natural Gas Installation V2 | cccb74e9-3fc9-4d16-9c75-7e19f0e9c3d5
checkpoint-status | b35ab8bb-c1a5-4ee4-ba7a-f63528d77335 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 8f02f971-344c-420a-90ea-28276d335e28 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 34082faf-cbc2-41cb-ac9b-80626a19f5a9 |  | checkpoint | Confirm trench depth, width and pipe alignment.
label | 32ee451f-e385-5ceb-a393-70a4ebc7e811 |  | note | QA documents to be received from sub-contractor prior to installation of conduit in trench.
checkpoint-status | a291efef-cba3-4457-9b22-25fc0e51f8b6 |  | checkpoint | Number of pipe dimensions shown on the drawings.
checkpoint-status | 80a292fb-c565-4dd5-948a-ebb823bbe794 |  | checkpoint | Location of pipes shall be shown on the drawings.
checkpoint-status | ec0aa8ef-f829-43d7-81d1-8ac537b2482a |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | f7ae6566-9eb5-4a52-a78f-fd3edf1ffa36 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 59f4663e-1ac5-42a5-a232-384930ab523e |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 48bc7fa5-cc04-4199-a0bc-0120197e118b |  | checkpoint | Installation of Valves
label | 746c7ac7-b9d4-5a8a-93e1-aab322b7a07d |  | note | Valves Installed as per approved drawings
label | 5c1c5cd0-c99a-55d4-8f6a-17411d9fe1ca |  | note | All works have been completed by a registered gas fitter ?
holdpoint | a794da90-1bec-4348-83d4-28552e8195e5 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 330d8c2c-dfe9-475f-9010-b12f9ff73da0 |  | checkpoint | Pipework Pressure Test Report Completed ?
checkpoint-status | 8869bad3-1fbb-4853-baf7-b1f53af53a2c |  | checkpoint | As-Builts Completed.
holdpoint | 62e55167-5755-49c8-b75a-f0fe1ca50a01 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | 1ff1eda9-e246-49ea-a63d-3f7a003a5cf1 |  | checklist | Electrofusion Welding |  |  |  |  | Yes | Electrofusion Welding | e00c3fcb-b742-46a8-a0d3-4bd7bb54b706
checkpoint-status | d12c9200-3934-4fd5-affd-13103cb9a054 |  | checkpoint | Welding details
select | e77830ce-f45a-55a8-8a52-5f6d69e4ba95 |  | dropdown | EF Coupler completed by and recorded. | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw, Restituto Escalada, Jerwill Peralta, Allan Alco
label | 5fd56b78-e9f7-5af6-a50a-a60b0b6e3bcb |  | note | Fusion Machine Used - SR No 402-1348 Caldertech EF welder
text | 3fa48e41-db68-52ab-81c9-804fc5e2807e |  | textbox | Record EF Coupler Used (Size)
checkpoint-status | 1b9c4532-8cf6-4ea3-8480-c96ebb6cfb55 |  | checkpoint | Pipe surface free from scratches, deeper than 10% of the wall thickness ?
checkpoint-status | 7858b33b-4783-4870-b4ea-aed0845ff578 |  | checkpoint | Pipe scraped and marked ?
checkpoint-status | fa06c62f-e8b1-412f-9c43-6714ed83820c |  | checkpoint | Pipe surface cleaned with Isopropyl alcohol?
checkpoint-status | e4e0cca8-6df2-4a79-b3df-d2fd3da92938 |  | checkpoint | Barcode scanned by machine?
checkpoint-status | 2973a4d7-4cbd-4427-b90d-a928bb1181f2 |  | checkpoint | Record cooling time achieved?
checkpoint-status | 053000d2-41d2-4afd-b182-92257266546c |  | checkpoint | Details of E.F Coupler Operator
select | 25ea69af-78dd-5a8e-bc52-08898dcaa0f7 |  | dropdown | Name | Benjamin Habon, EB Lindayao, Jefferson Calla, Redennis Teves, Steve Reeves, William Sabino, Calvin Cheyne, Mark Bateman, John Chingkaw, Restituto Escalada, Jerwill Peralta, Allan Alco
holdpoint | c555ef4d-303c-46cb-954b-57b8228b5e25 |  | signoff | Signature
checkpoint-status | c2efb854-1674-40de-9085-fa6ab7efb7f1 |  | checkpoint | Post weld checks completed
holdpoint | c62849b8-1925-4dce-a8a5-ea4583b835af |  | signoff | Post weld checks by Client and AE Smith - Request Signoff
checklist-flat | 10ed7224-c711-4507-9897-7f27ab667212 |  | checklist | Combined Services HDPE Fire Pipework Installation |  |  |  |  | Yes | Combined Services HDPE Fire Pipework Installation | e09c19c4-f149-42ee-a51e-24c713d97a1c
checkpoint-status | 8022e9fd-0aa8-40e4-b447-451b1340c5ab |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 697497df-c6fd-4c50-a7ba-01daccadcc52 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | b7edc8b5-9cd9-4ab6-badb-3ce5419219ce |  | checkpoint | Inspect trench depth, width and pipe alignment
label | ba51a8d2-8504-5e37-b3ba-d1d60c9f3349 |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | b066f345-ca72-5060-aa63-a1d2218c4aad |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 8821beff-0771-4f4b-b472-80a336648a61 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 83f5d64d-2c67-449d-804e-409f76640c0f |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | 19a7d8c9-46b4-45f7-8a92-80b7fba56b53 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | 43e9ca16-c620-463b-a4e6-31ff9c21c8e2 |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 675a37db-f46f-4999-844b-a19492446763 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | 2e7c517a-6630-4d4c-9f35-c39b71dc9d99 |  | checkpoint | Installation of tees and bends
label | 5829e92a-c37e-5b9c-b12c-9750e2b9ec8a |  | note | Install all connection tees as per construction drawings
label | 6b3eea05-4075-56c7-94ff-341987301bca |  | note | Ductile iron bends to be installed on pipework above 300ND
checkpoint-status | bb98b517-ae47-44dd-9126-61d2f259c681 |  | checkpoint | Installation of Hydrants and Hydrant Valves
label | f3b2e1c5-8ef0-5303-9483-9a983e177ad6 |  | note | Mount hydrants on approved types of hydrant tees with risers if necessary so that the top of each hydrant is within 100mm of the finished ground surface level
label | 81829216-8aa1-5604-8fe9-c0a077d8703d |  | note | In-ground hydrants and hydrant valves are installed in secure toby boxes and on isolation spurs.
checkpoint-status | 4fd587cb-7603-4b00-83e1-e114d3ac1749 |  | checkpoint | Install Thrust and Anchor Blocks
label | dd6e72d1-065c-55b8-93e0-97ea38ddba0e |  | note | Minimum dimensions as per IFC drawings.
label | 9645f101-c57a-5f3b-bf48-2e5cbc987eda |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
checkpoint-status | 33bc3bce-aa56-4bb5-9420-3d899912c43d |  | checkpoint | Installation of Trace Wire
label | 5eeda8b3-da8c-5a3e-9923-82b712c44fd6 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | 2f79e2d4-5294-58e3-8f5e-b7d3b92ad862 |  | note | Test Trace Wire following installation.
checkpoint-status | 3c335720-2666-47ab-8c1e-0937e7627ff3 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | 737feebe-f37b-4742-8fbd-ad0653cea5f2 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 439a9998-c367-5685-8e62-fd18afcd4b86 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 1d153018-38ac-5852-ae19-c7ec6607660b |  | note | Ensure each test length is capped and ball valve installed.
label | beff4f06-94da-5d94-83db-ef98f6d4004d |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 057e71b5-c379-52e2-8b62-bf8d89f736b6 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 393f7ca7-7580-424b-acad-adf968ac53c5 |  | checkpoint | Introduction of Air to 300 kPa
label | 3815b57e-a832-56b4-9683-0ff70760e3cc |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | 269a0052-2d5a-5769-865d-5cdbb745c26c |  | note | Monitor for any drop-in pressure.
label | ffb241e8-2908-5f9f-b29e-e700fdf574b0 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 30df5c34-da48-446e-be8d-a9f8b5337ebe |  | checkpoint | Increasing Test Pressure
label | 34bba2a1-fc69-5d6a-8b65-f2b4d5467462 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 2c204f13-a04c-4849-a220-22c6afbe940c |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | cd4c256c-d202-4b65-b743-1cad32ad3393 |  | checkpoint | As-Builts Completed.
holdpoint | b5d480b0-8354-4f62-a3ba-04b22a6d7f1f |  | signoff | Request Signoff/ Raise Remedial
checklist-sectioned |  |  | checklist | Combined Services - Heating Hot Water and Chilled Water Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | Combined Services - Heating Hot Water and Chilled Water Pipework Hydrostatic Pressure Test | ede7cc01-1d8f-42c7-a87a-d546b5f4afd7
checkpoint-group |  |  | section | Details
checkpoint-no-status |  |  | checkpoint | Reference Documentation:
label | bb086dab-0dc2-516c-8b4d-6247feef0073 |  | note | Medium duty black steel to AS 1074
label | 51c9ccc8-d02d-5075-9ec2-6be72cb8a5ac |  | note | Welded: To ANSI/API Spec 5L grade B.
label | 9f97e5ba-876a-5b88-a5d9-ae5e1981aa3a |  | note | Seamless: To ANSI/API Spec 5L grade B or ASTM A106 grade B.
label | f6cdf33d-f013-5088-8c5c-ac3c3208f5d6 |  | note | Standard: To AS 4041.
checkpoint-no-status |  |  | checkpoint | Project Specifications:
label | df1b069a-4ba3-5955-877d-98dca1fbff4e |  | note | NZT5007-STE-MSSP-0001
checkpoint-no-status |  |  | checkpoint | Drawings:
label | 80e96b02-f4d6-53fd-9300-d54add1063e7 |  | note | AES-NZ1005-STE-SHD-MEC-1101-in sequence up to- AES-NZ1005-STE-SHD-MEC-1142
checkpoint-status |  |  | checkpoint | Prepared by:
text | f73ee928-7bf7-55ab-b1b9-15ccd0779379 |  | textbox | Name:
text | ab35c446-39f4-53fc-93e1-bdbbb38a8619 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB Engineer
text | 6c504778-7faa-5753-bbea-a169d461733f |  | textbox | Name:
text | ae79674d-f7e0-5d89-9255-b30223168989 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB QA Rep
text | 80727b0f-ea45-553f-a467-0f890c57b5c9 |  | textbox | Name:
text | f28fc6b0-22c9-521e-89bb-c08da2797312 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: CPB Completions Rep
text | 1e30565a-a797-5df6-b4d5-dd4d6c4747f5 |  | textbox | Name:
text | 89def435-abd0-5359-bba9-744ee002a64c |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Reviewed by: Consultant (If applicable. N/A for Architects)
text | 76b7f731-5e6f-50a5-a8da-83eaf63ab8c1 |  | textbox | Name:
text | cc013d67-b513-5acc-906c-963584371c90 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Approved by: CPB SPE or higher
text | e464c100-3ebb-540f-bccb-1168b6586109 |  | textbox | Name:
text | a6608166-b090-57b2-ade1-96270d7d9981 |  | textbox | Date:
checkpoint-group |  |  | section | Preliminary Inspections and Tests
checkpoint-status |  |  | checkpoint | 1 - RDM & Consent Approval
label | 21066d99-f7fd-5257-be8f-8a599bbe6e53 |  | note | Responsibility - CPB
label | 13f1c779-2c51-5ddf-bbcb-3a0a3128075f |  | note | Specification Reference - RDM Tracker Consent Tracker
label | e4e3f8f2-5475-54fc-bae9-05a36fe2606d |  | note | Conformance Criteria - RDM approval tracker
label | b450cdf8-3e94-532f-9e95-30ae8f79ebe7 |  | note | Consent approval tracker
label | 03e6ff37-8035-565e-a693-4f3b2dfd8014 |  | note | Method - Document Review
label | 799df283-daca-5464-b690-5e8fc496fafb |  | note | Frequency - By Building/Area
label | 6262a00d-9266-5a80-8022-ed3a9957cce2 |  | note | CPB - HP
label | f545c91f-00b4-57ff-a134-9862b5954c48 |  | note | Records - Receipt of Approval by Client
holdpoint |  |  | signoff | CPB - HP
checkpoint-status |  |  | checkpoint | 2 - Define LOT Area
label | b33d37be-bc6c-5506-8dd5-9adb3437fa4a |  | note | Specification Reference - IFC Drawings
label | 3114f44c-9f82-53f0-9f19-3059c44546dd |  | note | Conformance Criteria - Lot areas clearly defined
label | bf7531c1-388a-5680-8291-d1b68f216f2b |  | note | Records - LOT Map / Register
checkpoint-group |  |  | section | Quality Control Checklists
checkpoint-status |  |  | checkpoint | QUALITY CONTROL CHECKLIST – ATTACH ALL CHECKLIST TEMPLATES USED FOR THIS ITP
label | e4559ce6-17bc-5aa5-bcc4-e40caf0abeb4 |  | note | *NAME OF CHECKLIST MUST BE INCLUDED ON ITP PART 1 LAST COLUMN (RECORDS OR CHECKLIST REFERENCE)
checkpoint-group |  |  | section | Lot Verification Checklist
checkpoint-status |  |  | checkpoint | Lot Verification
text | 8e6791fe-de35-5dbe-863b-8024007d15d1 |  | textbox | Lot Number:
text | a4e1c64c-b49d-5599-aff6-04f2c03a52de |  | textbox | Lot Description:
label | 659009f9-fd50-56de-b0cd-d84037ea00a7 |  | note | Note: Item / # records to be filled out by CPB Engineer - minimum is to match ITP, extra documents can be added
checkpoint-status |  |  | checkpoint | 1.0 - ITP / Quality Control Checklists
text | bed16bf0-f91f-5757-84ec-ab54befcddfb |  | textbox | Item
text | 2071d2c1-ca31-559f-806b-ef15670b18be |  | textbox | Number of Records Required
text | bc1d8af2-990b-5df5-bc13-ee81ccb35640 |  | textbox | LOT Subfolder No:
text | ca4b9cee-e044-5cde-a821-b3ba29d09679 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 1.1 - ITP / Quality Control Checklists
text | 12d83f82-1a34-55ae-916b-26f4c75a7bd9 |  | textbox | Item
text | 24f19147-c95d-51a1-850e-9378228e03e7 |  | textbox | Number of Records Required
text | 963ffd90-3be0-5655-9f9a-2201993f352a |  | textbox | LOT Subfolder No:
text | def94f73-8b06-53b2-8d97-13d33fcc4126 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 2.0 - Survey Results
text | 7d62a15f-9336-5292-8e73-186711a25e1b |  | textbox | Item
text | 50c69a23-cca7-532e-b65a-a6a6ef2e33ea |  | textbox | Number of Records Required
text | d15af1cb-b28c-506f-8da2-0a5d0e94caa5 |  | textbox | LOT Subfolder No:
text | cff67f59-dad0-5413-b5c3-0c6e5fcce084 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 2.1 - Survey Results
text | 5ac87e0d-c635-545a-8faf-bbc3063610b7 |  | textbox | Item
text | 6316e338-2581-56e7-a852-f519d134b1eb |  | textbox | Number of Records Required
text | 99fac6ae-a090-5557-adb0-e6f04f69f6ae |  | textbox | LOT Subfolder No:
text | 5d8a5cb2-7489-5f06-90fe-46a674cc871d |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | 3.0 - Test Results
text | f411064d-660e-54dc-ad92-7afc682828dd |  | textbox | Item
text | 2650de94-6738-51c9-8dd2-f7dd0e015ab8 |  | textbox | Number of Records Required
text | 99fbe50c-2689-55d0-83fa-ec967c540c2f |  | textbox | LOT Subfolder No:
text | f12dcb7e-6e0c-5b2b-bd5e-afd9e9f479c3 |  | textbox | Remarks (initial / date)
checkpoint-status |  |  | checkpoint | Conformance of Work Statement (if required ie if some docs not signed):
label | 584e6a7c-ef4e-5dcd-9ec2-7f3912395cc6 |  | note | The works for this construction lot conforms in respects to the ITP.
text | f048972d-795d-54de-abad-f1cc9eeee9cf |  | textbox | Name:
text | 09bf669d-fea8-5c2a-bca7-bcafc1a6990e |  | textbox | Subcontractor:
text | 1206c771-d7cd-5a7e-b3d8-24604bd053c6 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Conformance of Work Statement:
label | 2a4a2008-ea93-5e01-a362-cc62ba20983b |  | note | The works for this construction lot conforms in respects to the ITP.
text | c652ee5f-bfe3-548d-9495-d721483db055 |  | textbox | Name:
text | a3d15fc7-e928-59c1-8756-d15902fabc58 |  | textbox | Subcontractor:
text | 68928dbd-d116-5649-8307-1680df3756b8 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Conformance / Verification of Construction Lot Statement:
label | 585af9df-ea06-5166-8e68-056e03ac0728 |  | note | This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete and attached. Any non-conformances have been dispositioned in accordance with the contract requirements.
text | c8829be9-5376-50f1-b1d4-103d1b1b11c4 |  | textbox | Name:
text | 76a69824-7b3f-5707-a168-d3f3815cdf9c |  | textbox | Subcontractor:
text | 6fa140bb-0997-56db-9bb9-96c2998a7496 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Quality Review:
text | 85177680-3972-5ab3-9d85-082855108f46 |  | textbox | Name:
text | e9f2df66-8953-569b-95bb-6ab9278ad4f5 |  | textbox | Subcontractor:
text | 88f7adb6-b745-5a34-ab86-2c91c4631b4b |  | textbox | Date:
checklist-flat | 571a3b07-8d5d-40aa-9696-0a31d2574559 |  | checklist | RBG Combined Services HDPE Potable Water Pipework Installation V2 |  |  |  |  | Yes | RBG Combined Services HDPE Potable Water Pipework Installation V2 | f5052216-390d-450a-a1c8-d7527d477801
checkpoint-status | fe8cded6-ba65-4ae9-9897-ba4bc1de99d8 |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 488ca63e-7229-44b3-a7d9-cbf8ef333a3d |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | d02e13a6-ea41-45e9-afa9-d2d80e2f1517 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | 72313036-4a0b-52c4-8084-3a519b6e151a |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | dd05ef9b-4c34-5ef2-9588-54ee6d5212c2 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 38d24aee-fc84-4d49-bf45-0ef0476d02b5 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | fc064b72-2ab9-4f56-84b0-4d513f138de2 |  | checkpoint | Location of pipe
label | 66f6b723-dd59-5059-9595-8332cca840d2 |  | note | Shall be as shown on the drawings
label | e85da10a-bd59-5716-96a1-ae3f9ecfcca5 |  | note | Ensure correct clearances between water service and other underground services.
checkpoint-status | fa8ffbc1-d651-44e2-acf0-dd67aa5247e5 |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
holdpoint | e4964aab-44ef-4ac8-94d6-4329358dbce0 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 40247658-c80b-4e3d-abf4-022ab12a780b |  | checkpoint | Jointing of pipes only via. Rotatable steel flanges, EF Coupling and Butt Welding.
checkpoint-status | e578511e-7c39-4402-8825-1017985972ae |  | checkpoint | Electrofusion Welding Checklist completed for each joint?
checkpoint-status | 32f5e6d0-d891-42f4-b514-af821d77f0e5 |  | checkpoint | Butt welding checklist completed for each joint ?
checkpoint-status | 43b96ad7-8450-4e4e-a391-7038c8eb9bdb |  | checkpoint | Install valves, tees and bends
label | 1d8109f2-52ee-5218-b9a6-7c7a6a8a6776 |  | note | Install all connections as per construction drawings
label | 55801b8f-698f-5d71-9fce-3fe1f0fa8b73 |  | note | All valve 100mm and above will require a 1050mm manhole.
checkpoint-status | e6ea9a03-5d1c-4613-8c4f-b77ede055b84 |  | checkpoint | Installation of ductile iron bends
label | bce209f0-b938-530a-83f3-c6395020c26a |  | note | Inspect pressure class on fittings and ensure correct pressure rating prior to installation.
label | 6140da88-cee5-5ada-92b3-383d89664afa |  | note | Ensure correct gaskets are installed.
label | cf1d4bbb-af4f-5689-a4c8-53da05df932e |  | note | Washers installed on both sides of the flange.
label | 05cb8e10-b85d-507a-b7cc-38cdf0b47ab2 |  | note | Bolts to be tightened in correct tightening sequence.
checkpoint-status | f590ef3b-482d-44cc-a132-8114fd1f0c3c |  | checkpoint | Install Thrust and Anchor Blocks
label | c28a88a6-1f58-5170-b61d-06cb2938569d |  | note | Minimum dimensions as per IFC drawings.
label | 07a11e9d-6310-5382-bdbd-40b8f2aa77e5 |  | note | A protective Denso or black coating membrane is to be installed around the pipe and the concrete anchor/thrust blocks to prevent abrasive damage.
holdpoint | e8fbc5e4-65e7-4bda-b513-7c4984cc5c98 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 25c52cfc-621e-42b3-bfd1-d222e64466f4 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | a0c57ed0-d106-44e8-8675-286d57c4d2c7 |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 8d9ac74b-2f9a-5f34-8f2a-f3b0d4f39187 |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | dbfdad5d-b06f-578f-b6c8-ffacffcb139d |  | note | Ensure each test length is capped and ball valve installed.
label | 50e65a73-be5d-5491-bbd9-02dcd80779ff |  | note | Ensure all valves in the system are in the correct position and tagged �DO NOT OPEN� or �DO NOT CLOSE�
label | 6a1fe423-2c51-5673-a785-9901a5ed2fd9 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 3c0c7263-7d25-43d5-bcca-0427e9182e21 |  | checkpoint | Introduction of Air to 300 kPa
label | 081b0fc4-7c2d-51cd-9d7a-427b818f9b19 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | ebaad3ee-d529-5438-b068-6c34dd090b67 |  | note | Monitor for any drop-in pressure.
label | ca54cbb0-d8ac-5cb6-973c-18a529b876a8 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 4ed85e5b-5342-4010-8ab7-5a541c0a61a7 |  | checkpoint | Increasing Test Pressure
label | c35183f8-0a0a-59c0-803d-b30e034ef731 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 9372d54d-da9b-41dd-bd07-2fdaf383550e |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | ff8aa28e-3e39-4833-92d1-315dc5de583d |  | checkpoint | Installation of Trace Wire
label | 7332b864-ccb7-5a53-9808-dd156da63211 |  | note | Install Trace Wire and ensure tracer wire is continuous between valves and any excess coiled in valve box.
label | bc2eda57-0b02-5778-9b05-465eb84eecad |  | note | Test Trace Wire following installation.
holdpoint | 81d6d228-6d6e-4d08-840a-62b5c07456d2 |  | signoff | Request Signoff/ Raise Remedial
checkpoint-status | 63fbd9fb-3644-4f9b-98f8-d5386f02bef1 |  | checkpoint | As-Builts Completed.
holdpoint | aabf0c2e-332d-46e4-a175-647d19b017e7 |  | signoff | Request Signoff/ Raise Remedial
checklist-flat |  |  | checklist | Chemical Flushing Checklist |  |  |  |  | Yes | Flushing - Chemical Flushing Checklist | fa9ad2f0-ecf6-4a17-b8ba-296186859330
checkpoint-status |  |  | checkpoint | Uploaded highlighted drawing.
text | ed743669-4b61-52bc-8d33-09bc6abc145a |  | textbox | List the zones / terminals / branches flushed during this step.
checkpoint-status |  |  | checkpoint | Confirm all other terminals isolated
checkpoint-status |  |  | checkpoint | Test the water conditions prior adding chemical
checkpoint-status |  |  | checkpoint | pH
text | 500f3920-3ed9-5737-a7d9-be0fd1aa0188 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | c77c3d59-9696-5b89-9f3c-aaebd42cab13 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | ba3bafb6-7a90-5e7d-8e6f-c8d344ee7435 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
text | d1d5a516-c86d-5775-b1d0-2d7386647dc7 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Pump is operating at 50 Hz.
checkpoint-status |  |  | checkpoint | Required cleaning chemical (L)
text | 89fc66ba-dbe0-5c24-b8c0-01705492824b |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Cleaning chemical(s) added.
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | 329485a3-b011-5093-b5ef-ece915a8bb11 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | ef1dc252-32e0-5ab3-ae84-c0c53b2ac2c1 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Name of chemical and SDS
text | 9fa4fb04-2ce9-54bc-9fa3-a6e87d62f58c |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Circulate water 2 - 4 hours
checkpoint-status |  |  | checkpoint | Test the water conditions at the completion of the circulation.
checkpoint-status |  |  | checkpoint | pH
text | a8ce18fa-64ce-54f4-bd53-32e0131a5d79 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Conductivity
text | 7147cdf9-ffa4-5708-bfa7-72a1b9bdcfe9 |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | TDS (Total dissolved solids)
text | a72a0f7e-e019-5bc8-b2dd-0113de58619b |  | textbox | Site Measurement
checkpoint-status |  |  | checkpoint | Chloride
checkpoint-status |  |  | checkpoint | Photo of water sample at the end of the circulation before draining water.
checkpoint-status |  |  | checkpoint | Is there any neutralisation chemical added as per chemical specialist advise? If yes enter name and quantity
checkpoint-status |  |  | checkpoint | Record total and terminal waterflows on the "Flushing Water Flows" test sheet and upload here.
checkpoint-status |  |  | checkpoint | Clean strainers as required. Upload dirt and clean strainer photos here.
checkpoint-status |  |  | checkpoint | If this is last section to be flushed, then continue draining process.
checklist-flat | a75cc64e-f2a8-45bd-bbf8-6cd7efeb512c |  | checklist | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation |  |  |  |  | Yes | AECOM Combined Services HDPE Domestic Cold Water Pipework Installation | fbced108-f12a-4800-ad8e-d0376cb6e7e5
checkpoint-status | e57ac699-37ed-40a8-af1c-95d009258e3e |  | checkpoint | ROM & Consent Approval received by the client and approved?
checkpoint-status | 9a5ef586-1c17-46f9-835c-74f8827c3bd0 |  | checkpoint | All material certificates of compliance are provided to the client before the materials are incorporated into the works.
checkpoint-status | 5fb1a867-904c-440c-ae42-6ffd48b0ee15 |  | checkpoint | Inspect trench depth, width and pipe alignment
label | bd86b772-91b1-5516-aaf3-430092bfbbeb |  | note | Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | 340bb2cf-63d5-5038-8fa2-8393e82c83e7 |  | note | QA documents to be provided prior to installing pipework in trenches . CPB to provide to AE Smith.
checkpoint-status | 5dce97c1-d53d-49dd-9a3d-ec787da6a837 |  | checkpoint | Number of pipes and dimensions of pipes shall be shown on the drawing
checkpoint-status | 52e75023-11f0-4884-bc6e-a073d68506a0 |  | checkpoint | Location of pipes shall be shown on the drawing
checkpoint-status | eb457a76-570c-45cb-a47a-f9edf8535cac |  | checkpoint | Sample Test Weld & Non-Destructive Testing completed and issued to CPB ?
checkpoint-status | 73b7bb1b-f542-4c91-8d72-56f40cb8f1df |  | checkpoint | Joining of pipework only to be done by Rotable steel flanges and EF Coupling.
checkpoint-status | 3e0384e4-dd54-4119-a873-e6577ab8acd2 |  | checkpoint | Electrofusion Welding Checklist completed for each joint ?
checkpoint-status | d72fc974-1064-4ef6-abdf-78761b999925 |  | checkpoint | Install , valves , tees and bends
label | 408311cb-7f62-5b73-add9-e3ecf88eb41e |  | note | Connections are installed as per construction drawings ?
label | a883a627-977a-5d91-b9a0-fb5a261f5c3a |  | note | All valves 100mm and above have a 1050 manhole ?
checkpoint-status | b12f6259-87ed-4e1a-b22d-6c18b9f6b5ee |  | checkpoint | Install Thrust and Anchor Blocks
label | 67afe993-b3cb-5b94-8f90-a2b8df9d9297 |  | note | Minimum dimensions as per IFC Drawing
label | f43801c6-0d3a-53b0-ba67-25ef90f64f24 |  | note | A protective Denso or black coating membrane has been installed around the pipe and the concrete anchor / thrust block to prevent abrasive damage ?
checkpoint-status | 1dc0082d-ec1f-4dcd-afcb-a974a15027d6 |  | checkpoint | Installation of Trace Wire
label | 8b3c931e-faec-500b-b009-4a02572ea8a6 |  | note | Install Tracer wire as per Specification 5.21 of the Hydraulic Services Specification and ensure tracer wire is continuous between valves and any excess coiled.
label | 25ea4ac4-fcaf-51a4-93a9-497c049f6d1b |  | note | Test Trace Wire as per Specification 5.20.4
checkpoint-status | f93b4866-5dd6-4802-8d10-516b49dd8874 |  | checkpoint | Completed Construction Pressure Testing with Air
checkpoint-status | e953634b-65e5-4603-8ee1-86b001fe3fdd |  | checkpoint | Pre-Pipework Pressure Testing Inspection
label | 984adba8-2548-554a-a29b-b4f8d734c1cc |  | note | Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 4d8b8721-75f2-5626-96e2-83258da2544d |  | note | Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 44ace4fe-3833-5ddf-bae0-fa22b1287421 |  | note | All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing.
checkpoint-status | 7aff1875-a018-4444-b835-20cca4627b2c |  | checkpoint | Introduction of Air to 300 kPa
label | 253bf578-0d5b-5044-b22a-13c0dc8f1cf1 |  | note | Gradually introduce air into the system to a pressure of 300 kPa and hold for 1 hour.
label | bc73d770-7db7-5b7d-ab31-f99e3138abe6 |  | note | Monitor for any drop-in pressure.
label | 08cc7696-c589-5018-b308-3be0ca200b60 |  | note | If a leak is identified discharge the air prior to rectifying any leaks.
checkpoint-status | 81017817-8534-4d04-8e0c-a749428a2992 |  | checkpoint | Increasing Test Pressure
label | 841fc52c-458a-5575-80cf-dbb9222bf756 |  | note | If no leaks are identified Increase pressure by 10% increments until test pressure is achieved.
checkpoint-status | 82b71a36-57ec-4178-a931-e676098064c2 |  | checkpoint | Pipework Pressure Test Report Completed
checkpoint-status | 313021d6-ce05-4a30-887e-ed972dcf8b2d |  | checkpoint | As-Builts Completed.
holdpoint | 694b58d3-10c9-481b-8bf1-c759727cd37e |  | signoff | Request Signoff/ Raise Remedial
checklist-flat | fcea9140-d73f-42a3-910c-b265c91f2a41 |  | checklist | Line Test Data Sheet |  |  |  |  | Yes | Line Test Data Sheet | ff9a00a0-b581-4df8-b3f8-d2ee5a5fdc8f
checkpoint-status | 05f198e8-7502-4f10-bfec-0736ebf8e69c |  | checkpoint | Line Test Data Sheet attached
holdpoint | bb8b7fcd-f767-4c35-9c69-dcea2beae238 |  | signoff | Request Signoff/ Raise Remedial