## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test |  |  |  |  | Yes | AES-NZ1005-STE-ITP-PMT-0024 - DCW Pipework Hydrostatic Pressure Test
section | MATERIAL COMPLIANCE
checkpoint | RDM & Consent Approval - CPB Hold Point
note | CRITERIA - RDM approval tracker Consent approval tracker
checkpoint | General - CPB Hold Point
note | CRITERIA - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
note | • Specifications & QA Documents Approved
note | • Drawings are confirmed
note | • Equipment fit for purpose
section | CONNECT PRESSURE PUMP TO DCW RING MAINS
checkpoint | Confirm Flushing & Disinfection of Pipework - CPB Hold Point
note | CRITERIA - 1. Air should be removed at each building prior to the DCW water supply water entry assembly to prevent debris from entering building.
note | 2. Ensure system sterilization completed.
note | 3. Ensure TNK filtration is cleaned/ inspected if not isolated from test.
note | 4. Ensure all screens/ strainers are cleaned/ inspected if not isolated from test.
checkpoint | Accept delivery of pump to site
note | CRITERIA - 5. Check pump is rated for pressure test
note | 6. Check all supplied attachments are correct and in good order
note | 7. Check fluid levels & fill as necessary
checkpoint | Isolate: Mains water Storage Tanks
note | CRITERIA - 1. Check Mains water is isolated
note | 2. Check Storage Tank is isolated
note | 3. Check Filters are isolated (10 Bar max rated)
checkpoint | Connect pump to pipework under test
note | CRITERIA - Confirm connections are safe and correct, Supervisor to confirm section under test is correct and all other parts of the system not under test correctly isolated
checkpoint | Connect calibrated gauges for pressure test
note | CRITERIA - Confirm position is correct, gauge is in good order for test & calibrated
section | HYDROSTATIC TEST
checkpoint | Fill DWC ring mains with domestic water
note | CRITERIA - Completely fill closed loop system with water releasing all air from the Taps at each Building
checkpoint | Gradually increase system pressure to 1550kPa
note | CRITERIA - Slowly raise system pressure to 1550kPa
note | • Checking for any signs of leaks or pressure drops
checkpoint | Stabilize 1550kPa pressure (START WITNESSED) - CPB/IR Hold Point
note | CRITERIA - Record START time & photograph gauge
note | • All relevant parties to witness starting pressure of 1550kPa
note | • IR to be invited for witness at the reviewer’s discretion (Aconex hold point mail)
checkpoint | Hold 1550kPa pressure for 35min (END WITNESSED) - CPB/IR Hold Point
note | CRITERIA - Record FINISH time & photograph gauge
note | • All relevant parties to witness pressure of 1550kPa
note | • IR to be invited for witness at the reviewer’s discretion (Aconex hold point mail)
checkpoint | Pressure released or reduced for next test
note | CRITERIA - Supervisor to ensure energy (pressure) is only stored while under test
checkpoint | Discharge pressure leave system in a safe state
note | CRITERIA - Discharge system pressure, ensure area is left in a safe state meeting site requirement
section | COMPLETION RECORDS
checkpoint | Testing Results - CPB Hold Point
note | CRITERIA - All pipework pressure test reports shall be provided
checkpoint | Works Completion Test WCT 68 - CPB/IR Hold Point
note | CRITERIA - PDS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the pressure test all cold and domestic hot water pipe lines