## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | AES-NZ1005-STE-ITP-PMT-0016 - Combined Services - Diesel Fuel Lines | [5 empty] | AES-NZ1005-STE-ITP-PMT-0016 - Combined Services - Diesel Fuel Lines
section | MATERIAL COMPLIANCE
checkpoint | RDM & Consent Approval
label | Resp. - CPB
label | Referenced Documentation - RDM Tracker Consent Tracker
label | Conformance Criteria - RDM approval tracker Consent approval tracker
label | Method - Document Review
label | Frequency - By Building/ Site Wide
label | WP - AE Smith
label | Records - Receipt of Approval by Client
checkpoint | General
label | Resp. - SE
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001
label | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
label | • Diesel Duel Pipe, jointing, Including electrofusion couplers and fittings.
label | • Stainless steel piping
label | • Specifications & QA Documents Approved
label | • Drawings are confirmed
label | • Equipment fit for purpose
label | Method - DR
label | Frequency - Each material
label | WP - AE Smith
label | Records - Aconex approval, Incoming Inspection Checklists, Drawing Register
section | INSTALLATION
checkpoint | Inspect trench depth, width and pipe alignment - CPB Hold Point
label | Resp. - SRV
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001
label | Conformance Criteria - Confirm trench depth, width and pipe alignment shall be as shown on drawing.
label | • Ensure Trench complies with HSNO Regulations.
label | • Trench Inspection Check Sheet to be completed.
label | Method - V
label | Frequency - Once
label | WP - AES (MEL)
label | Hold Point - CPB
label | Records - Check Sheet + Trench Inspection Check Sheet
checkpoint | Inspect trench depth, width and pipe alignment. Number of pipes and dimensions of pipes and location.
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-SHD-ELE-6011, AES-NZ1005-STE-SHD-ELE-6015, AES-NZ1005-STE-SHD-ELE-6101
label | Conformance Criteria - Shall be as shown on drawings.
label | Method - V + FM
label | Frequency - Each section
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Location
label | Resp. - SRV
label | Referenced Documentation - AES-NZ1005-STE-SHD-ELE-6011, AES-NZ1005-STE-SHD-ELE-6015, AES-NZ1005-STE-SHD-ELE-6101
label | Conformance Criteria - Shall be as shown on drawings. or as agreed on site with CPB
label | Method - S
label | Frequency - Every 20 m or change in direction
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Location UT1
label | Referenced Documentation - AES-NZ1005-UT1-SHD-ELE-0003
label | Conformance Criteria - Shall be as shown on drawings or as agreed on site with CPB
label | Method - V
label | Records - Check sheet/As Built
checkpoint | Jointing of Pipework (PLX)
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001, AES-NZ1005-STE-DSH-ELE- 0002
label | Conformance Criteria - 1. Jointing of pipes shall be completed in accordance with the manufacturers requirements
label | Method - V+M
label | Frequency - Each Weld/Joint
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Welding of Pipework (SS)
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001
label | Conformance Criteria - Jointing of stainless steel pipes shall be welded by a certified welder
label | Method - V+
label | Frequency - Each Weld/Joint
label | WP - AES (MEL)
label | Records - Check Sheet, Welders certificate
checkpoint | Seismic Joints
label | Referenced Documentation - AES-NZ1005-STE-DSH-SEI- 0001
label | Conformance Criteria - 1. Confirm seismic joint is as approved submission
label | 2. Joints are installed as detailed on the drawings
label | 3. Pipe work connections are complete tightened in accordance with manufacturers requirements and without leak
label | Method - V
label | Frequency - Once
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Transition Sump
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-DSH-ELE- 011
label | Conformance Criteria - 1. Confirm sumps are as the approved submission
label | 2. Confirm sumps are installed to the manufacturers requirements
label | Method - V FT
label | Frequency - Once
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Leak Detection System
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-STE-DSH-HYD-011, VLR 410E installation manual
label | Conformance Criteria - 1. Confirm Leak detection components are as the approved submission
label | 2. System is installed in accordance with the installation instructions
label | 3. Confirm equipment is adequately supported
label | Method - V FT
label | Frequency - Once
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Bracketing UT1
label | Resp. - SUP
label | Referenced Documentation - KCL-NZ1005-UT1-DWG-NSS- 0016-FC-1, KCL-NZ1005-UT1-DWG-NSS- 0017-FC-1
label | Conformance Criteria - 1. Confirm Bracketing has been installed as per KCL documentation
label | 2. Variance in pipe work routes / bracketing shall be reviewed by KCL
label | Method - V
label | Frequency - Once
label | WP - AES (MEL) KCL
label | Records - Check sheet KCL report
checkpoint | Stainless steel valves
label | Resp. - SUP
label | Referenced Documentation - AES-NZ1005-UT1-DSH-ELE- 0001
label | Conformance Criteria - Confirm valves are as approved submission
label | • Valves are located as per approved drawings
label | • Pressure reducing valve(s) is set to the nominated out put pressure
label | • Valve connections are tightened and without leak
label | Method - V
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Mechanical Joints
label | Resp. - SUP
label | Conformance Criteria - Confirm all joints are secure and tightened in accordance with manufacturers/ industry practice
label | Records - Check Sheet
checkpoint | Pipe Markers
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001
label | Conformance Criteria - 1. Mark pipe route by markers set flush inground above.
label | 2. Markers shall by minimum 200 x 200 x 50thick concrete slab with a brass plate fixed to top surface engraved: "FUEL PIPES UNDER" and directional arrows to indicate route.
label | 3. Marker Installation: Install at maximum 15m intervals and at all changes in direction. (Pipe Markers are not required where pipe route is covered by a concrete slab)
label | Method - V
label | WP - AES (MEL)
label | Records - Check sheet
checkpoint | Pipework Purge
label | Conformance Criteria - Purge pipework with compressed air to confirm conduits are clear of debris.
label | Method - V
label | Frequency - Each circuit
label | WP - AES (MEL)
label | Records - Check sheet
section | PLX PIPEWORK FIELD ELECTROFUSION WELDING
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE- FSSP-0001 3.4.2.
label | Conformance Criteria - Welding details completed
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - EF Coupler completed by and recorded.
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Fusion Machine Used
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - EF Coupler No. (Add picture)
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Materials Used (Size)
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Pipe surface free from scratches, deeper than 10% of the wall thickness?
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Pipe scraped and marked?
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Pipe surface cleaned with Isopropyl alcohol?
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Barcode scanned by machine.
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Record cooling time achieved.
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - Cooling time - start time/finish time:
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Electrofusion Welding
label | Resp. - SUP
label | Conformance Criteria - E.F Coupler Operator Signature Required
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
checkpoint | Final Inspection of Weld
label | Resp. - SUP
label | Conformance Criteria - CPB and AE Smith to inspect completed welds.
label | Method - M+V+FTR
label | Frequency - Each Weld
label | WP - AES
label | Records - Check Sheet
section | COMPLETION TESTING
checkpoint | Pneumatic pipework pressure testing
label | Referenced Documentation - NZT5007-STE-SPC-ELE-0001, AES-NZ1005-STE-DSH-ELE-0002, PLX installation Guide
label | Conformance Criteria - 1. Pressure test to 1.5 times working pressure or not less than 350kPa
label | Method - V+FTR
label | Frequency - Each test
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Primary pipe Pre-Pipework Pressure Testing Inspection
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001, AES-NZ1005-STE-DSH-ELE-0002, PLX installation Guide
label | Conformance Criteria - 1. Conduct a visual inspection of pipework to be tested, checking all connections to ensure they are tight.
label | 2. Ensure all valves in the system are in the correct position and tagged “DO NOT OPEN” or “DO NOT CLOSE”
label | 3. Secondary containment pipe work shall be open to atmosphere
label | 4. Test heads are fixed to transition fittings (at the dispenser) to allow pressure to be introduced and for the internal pressure to be measured. The other end (at the tank) must be closed off using spade connections between the compact flange/ flange connections to ensure that the tank is both isolated and that the pressure test is not also being applied to the tank.
label | 5. All installation Hold Points have been signed off by CPB & AECOM prior to pressure testing commencing
label | Method - V
label | Frequency - Once
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Introduction of air to 50 kPa
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001, AES-NZ1005-STE-DSH-ELE-0002, PLX installation Guide
label | Conformance Criteria - 1. Introduce air/nitrogen to an initial V pressure of 0.5bar (10psi).
label | • Examine all the electrofusion joints and threaded joints for any leakage using soap solution (where possible).
label | Method - V
label | Frequency - Each Circuit
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Increasing Test Pressure to 350 kPa
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001, AES-NZ1005-STE-DSH-ELE-0002, PLX installation Guide
label | Conformance Criteria - The pressure may then be raised in 0.5bar increments over 15 minute intervals to a maximum pressure of 4.0bar (60psi)
label | • Once the target pressure is reached, measurements should be taken from the pressure gauge:
label | – The minimum duration of test shall be 1 hour.
label | Frequency - Each circuit
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Pipework Pressure Testing (Line Test Data Sheet)
label | Resp. - SUP
label | Referenced Documentation - MEL Line test data sheet
label | Conformance Criteria - 1. Complete pressure test to verify no leaks and complete Line Test Data Sheet.
label | Frequency - Each circuit
label | WP - AES (MEL) CBR
label | Records - Line Test Data Sheet
checkpoint | Pressure testing procedure for the secondary containment lines
label | Referenced Documentation - NZT5007-STE-SPC-ELEC-0001, AES-NZ1005-STE-DSH-ELE-0002, PLX Installation Guide
label | Conformance Criteria - Introduce air to an initial pressure of 0.5bar (10psi).
label | • Examine all the electrofusion joints and threaded joints for any leakage using soap solution (where possible).
label | • The pressure may then be raised in 0.5bar increments over 15 minute intervals to a maximum pressure of 2.0bar (30psi).
label | • Once the target pressure is reached, measurements should be taken from the pressure gauge:
label | – The minimum duration of test shall be 1 hour.
label | Frequency - Each Circuit
label | WP - AES (MEL)
label | Records - Check Sheet
checkpoint | Secondary Containment Pipework Pressure Testing (Line Test Data Sheet)
label | Resp. - SUP
label | Referenced Documentation - MEL Line test data sheet
label | Conformance Criteria - Complete pressure test to verify no leaks and complete Line Test Data Sheet.
label | Frequency - Each circuit
label | WP - AES (MEL) CBR
label | Records - Line Test Data Sheet
checkpoint | Leak Detection system Proving
label | Conformance Criteria - Simulate leak to prove system
label | – Local audible visual alarm activated
label | – Output to shut down diesel transfer pumps
label | Method - V, FT
label | Frequency - Once
label | WP - AES (MEL) CBR
label | Records - FTR
section | AS CONSTRUCTED SURVEY
checkpoint | As-constructed survey
label | Resp. - AES
label | Referenced Documentation - NZT5007-STE-SPC-ELEC- 0001
label | Conformance Criteria - As-constructed survey must capture the horizontal and vertical locations of all newly constructed or relocated underground trenches and pipework.
label | Method - S
label | Frequency - Each Lot
label | WP - CPB
label | Records - Survey drgs
checkpoint | As Built Drawings, Above Ground installation
label | Resp. - AES
label | Referenced Documentation - NZT5007-STE-SPC-ELEC- 0001
label | Conformance Criteria - Mark up construction drawings with as constructed changes
label | Method - S
label | Frequency - UT1 TNK
label | WP - AES
label | Records - As built drgs
section | COMPLETION RECORDS
checkpoint | Test results - CPB/AEC Hold Point
label | Conformance Criteria - Line Test Data Sheets shall be provided FTRs will be provided
label | Method - DR
label | Frequency - Witness
label | WP - AES
label | Hold Point - CPB/AEC
checkpoint | Conformance records - CPB/AEC Hold Point
label | Resp. - SUP
label | Referenced Documentation - NZT5007-STE-HSSP-0001
label | Conformance Criteria - As Built drawings with constructed changes.
label | Method - V
label | Frequency - Each Lot UTI TNK
label | WP - AES
label | Hold Point - CPB/AEC
label | Records - Calibration Register, Individual calibration certificates
checkpoint | HSNO Certification
label | Resp. - SE
label | Referenced Documentation - HSNO Regulations
label | Conformance Criteria - HSNO Certification
label | Method - FTR
label | Frequency - On completion of installation
label | WP - AES
label | Records - HSNO certificate
checkpoint | As-built survey - CPB Hold Point
label | Referenced Documentation - NZT5007-STE-SPC-ELEC- 0001
label | Conformance Criteria - As built completed.
label | Method - DR
label | Frequency - Once
label | WP - AES
label | Hold Point - CPB
label | Records - Survey Drawings UT1 as constructed
checkpoint | Schedule WCT 12 Penetrations - CPB Hold Point
label | Referenced Documentation - Schedule 11
label | Conformance Criteria - All penetrations from and between secure areas, above and below ground, are less than 125mm in at least one plane, and in circular ducts no greater than 225mm in diameter (or have high tensile steel bars to reduce the aperture to no greater than 125mm in at least one plane).
label | Method - DR
label | Frequency - On completion of the installation if applicable.
label | Hold Point - CPB
label | Records - WCT Inspection by IR