## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP 008 - Bund Liner Fabrication & Installation | itp |  |  |  |  | ITP 008 - Bund Liner Fabrication & Installation
section | 1.0 Documentation
checkpoint | 1.1 IFC drawings
label | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
label | Acceptance Criteria - Approved IFC/RFI responses
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
checkpoint | 1.2 Design Report complete
label | Type of inspect / Test and Frequency - Design report from fabricator
label | Acceptance Criteria - Design report from fabricator
label | Inspection Responsibility: BCL - D
label | Verification Records of Inspection(s) / Test(s) - Upload design report
section | 2.0 Construction
checkpoint | 2.1 Tank Construction
label | Type of inspect / Test and Frequency - PE Tank fabricated by approved/competent fabricator
label | Acceptance Criteria - Visual inspection
label | Inspection Responsibility: BCL - D
label | Verification Records of Inspection(s) / Test(s) - Upload tank construction documentation from Placon. Photos.
section | 3.0 Testing
checkpoint | 3.1 Leak test tank
label | Type of inspect / Test and Frequency - Fill to overflow level, hold for 24 hours. No level change, no visual leaks
label | Acceptance Criteria - Leak Test passed
label | Inspection Responsibility: BCL - T
label | Verification Records of Inspection(s) / Test(s) - Upload Leak Test report
checkpoint | 3.2 Spark test tank
label | Type of inspect / Test and Frequency - Spark test all welds
label | Acceptance Criteria - Spark Test passed
label | Inspection Responsibility: BCL - T
label | Verification Records of Inspection(s) / Test(s) - Upload Spark test report
section | 4.0 Certification
checkpoint | 4.1 Stationary Container Tank Compliance Certificate
label | Type of inspect / Test and Frequency - Worksafe authorised certifier to provide compliance certificate
label | Acceptance Criteria - Compliance certificate
label | Inspection Responsibility: BCL - D
label | Verification Records of Inspection(s) / Test(s) - Upload certificate