## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP014 - AGL General Works, Testing & Commissioning | itp |  |  |  |  | ITP014 - AGL General Works, Testing & Commissioning
section | 1.0 Preliminary Works
checkpoint | 1.1 - Functional Description
note | Frequency: Prior to Start
note | Acceptance Criteria:
note | • Prior to final AGLCS programming, the Contractor shall produce a complete detailed Functional Description of the AGLCS detailing the proposed modifications to the existing AGLCS control logic and software, display screens, control equipment and method of implementation.
note | • The Contractor shall make allowance for a minimum of three (3) weeks for the review of the submitted Functional Description and on-going consultation with Melbourne Airport operational personnel (including Airservices Australia) to ensure all required functionality and operational modes are understood and feedback incorporated.
note | Reference Documents: Appendix K- Technical Specifications )5.3.2
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | HP
note | Responsibility: FH Engineer / AGLCS Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.2 - Equipment Inventory
note | Frequency: Prior to Start
note | Acceptance Criteria:
note | • Provide an inventory of all control and processing equipment required to complete the works. The inventory shall include details of the product code, description, and quantity.
note | • Include equipment types and quantities supplied as Principal Supplied Items in the inventory.
note | • The inventory shall be submitted at the time of the Functional Description submission
note | Reference Documents: Appendix K- Technical Specifications )5.3.4
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | HP
note | Responsibility: FH Engineer / AGLCS Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Final AGLCS Display Graphic Design
note | Frequency: Prior to Start
note | Acceptance Criteria: A draft graphic display will come from AGLCS Simulator that will be prepared to the requirements that are set out by Airservices.
note | Reference Documents:
note | • Appendix K
note | • HP
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | HP
note | Responsibility: FH Engineer / AGLCS Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.4 - Confirmation of INTAS Interfacing
note | Frequency: Prior to Start
note | Acceptance Criteria:
note | • Prior to final AGLCS programming and site installation, the Contractor shall obtain written advice from Airservices Australia confirming the suitability of the configuration of the modified interface between the modified AGLCS and Airservices Australia’s INTAS (as proposed by the Contractor).
note | • Any subsequent changes to the Contractor’s proposed interface configuration, as may be required during software or hardware development, shall be verified by Airservices Australia with supporting written confirmation obtained by the Contractor and submitted to the Contract Administrator.
note | Reference Documents: Appendix K- Technical Specifications )5.3.5
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | HP
note | Responsibility: FH Engineer / AGLCS Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.5 - Interim Works during Construction
note | Frequency: Prior to Start
note | Acceptance Criteria:
note | • The Contractor shall coordinate any interruption to or modification of the existing AGLCS with the ATC operational personnel (Airservices Australia) and the Contract Administrator.
note | • The Contractor shall provide two (2) weeks’ notice to Airservices Australia and the Contract Administrator prior to the commencement of any interruption to or modification of the existing operational AGLCS. Provide full written details of the date, time, expected duration, configuration and available control modes during interim periods of limited control (i.e. where facilities cannot be controlled from the ATC Tower or SCADA terminals).
note | Reference Documents: Appendix K- Technical Specifications )5.3.6
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | AP
note | Responsibility: FH Engineer / AGLCS Subcontractor / Principal’s Representative
textbox | Date Completed:
checkpoint | 1.6 - Site Acceptance Testing and Post Installation Modifications
note | Frequency: Prior to Start
note | Acceptance Criteria:
note | • In commissioning the AGLCS, the Contractor shall observe the operation of all systems and shall tune operation for optimum performance.
note | • During the commissioning phase, the Contractor shall make all necessary modifications to control circuits, the PLC program, and the SCADA configuration as a result of tuning of the AGLCS to meet these Specification requirements.
note | Reference Documents: Appendix K- Technical Specifications )5.3.7
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | IP
note | Responsibility: FH Engineer / AGLCS Subcontractor
textbox | Date Completed:
section | 2.0 Testing & Commissioning
checkpoint | 2.1 - Constant Current Regulators
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • The lights must be powered from field series circuit primary cabling for airfield lighting.
note | • Electricity supply for the runway lighting series circuits will be supplied and from CCRs located in the ALER and tested as per the criteria listed below:
note | – Line Current (Maximum): 6.6 A
note | – Line Voltage (Nominal); 1,135 V (on basis of 7.5 kVA CCR)
note | – Phase: Single
note | – Frequency: 50Hz
note | • The waveform and characteristics of the output of the Constant Current Regulators must be considered and all equipment must be suitable for operation with modern phase controlled thyristor Constant Current Regulators.
note | Reference Documents: Appendix K- Technical Specifications )3.3
note | Inspection/ Test Method: Verify
note | Record of conformity: Commission-ing Checklist / Test Report
note | TP
note | Responsibility: FH Engineer / AGL Subcontractor
textbox | Date Completed:
checkpoint | 2.2 - Commissioning Plan
note | Frequency: Prior to commission
note | Acceptance Criteria:
note | • Contactor must submit a detailed commissioning plan summarising all aspects of commissioning the AGL system.
note | • The contractor must give Contract Administrator 2 weeks’ notice of the date of Commissioning. This date must be updated and confirmed on a weekly interval from the date of notice being submitted.
note | Reference Documents: Appendix K- Technical Specifications )6.4
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex Submission Reference
note | HP
note | Responsibility: FH Engineer / AGL Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Mobile photometric testing
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria:
note | • As part of the commissioning phase, the Contractor must liaise the Principal to arrange for photometric testing of the runway’s lighting systems utilising the Principal’s MALMS system.
note | • The Principal will arrange updates to the associated system data / software files and perform the testing.
note | • The Contractor must provide the Principal with any required information to enable updating of the system data / software files, e.g., survey data capturing installed light locations, light configurations (colours, orientations, etc.), in a format requested by the Principal.
note | • The contractor to arrange for Principal (via Contract Administrator) to undertake mobile photometric testing (3 weeks) prior to commencing commissioning
note | Reference Documents: Appendix K- Technical Specifications )6.4.1
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex
note | HP
note | Responsibility: FH Engineer / AGL Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.4 - Acceptance testing
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria: Contractor to submit test results from acceptance testing, prior to the award of Practical Completion
note | Reference Documents: Appendix K- Technical Specifications )6.5
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex
note | HP
note | Responsibility: FH Engineer / AGL Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.5 - CASA flight test and ground check
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria:
note | • After completion of all works under the Contract as detailed in CASA AC 139-04(0) Commissioning of Aerodrome lighting systems, certification of the new airfield lighting must be carried out
note | • This requirement must include a flight test by a pilot who has the appropriate letter of competence issued by CASA.
note | • The contractor to arrange the time for the flight test with the Contract Administrator and pay all costs.
note | Reference Documents: Appendix K- Technical Specifications )6.6
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex
note | HP
note | Responsibility: FH Engineer / AGL Subcontractor / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 Post Construction Submissions
checkpoint | 3.1 - AGL Maintenance Manuals
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria:
note | • The Contractor must prepare and deliver to the Contract Administrator the following documents:
note | – Operation and Maintenance Manuals - Two volume set
note | • Airfield Lighting Fieldworks
note | • Control System
note | – Airfield Lighting and Control System As-Constructed drawings - Copies of drawings.
note | Reference Documents: Appendix K- Technical Specifications )7.1 to 7.5
note | Inspection/ Test Method: Verify
note | Record of conformity: Maintenance Plan Submission Reference
note | IP
note | Responsibility: FH Engineer / AGL Subcontractor
textbox | Date Completed:
checkpoint | 3.2 - AGL Components List & Spare Parts
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria:
note | • Provide operational spares for equipment supplied under this Contract. All spare equipment must be to the same conditions, specifications and test requirements as contained within the documents.
note | • The minimum quantities to be supplied for minimal spares holdings must be as per Table 2.1 “Minimum Spares Quantity Provided by Project” in Appendix K- Technical Specifications )2.9.
note | • The Contractor must supply a schedule of spares provided for each equipment type detailing part numbers, description, per unit cost and quantity with reference to their associated equipment type (e.g. runway elevated light, inset light, etc.), correlated with the quantity installed during the project.
note | Reference Documents: Appendix K- Technical Specifications )2.9
note | Inspection/ Test Method: Verify
note | Record of conformity: Component List Submission Reference
note | IP
note | Responsibility: FH Engineer / AGL Subcontractor
textbox | Date Completed:
checkpoint | 3.3 - AGL Training
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria:
note | • AGL Contractor to training with all the necessary equipment, manuals, videos and notes using trained and experienced staff.
note | • Training for the operation and maintenance of the CCRs and AGLCS must also be provided by the CCR manufacturer and AGLCS Contractor (if applicable) respectively.
note | • Prior to final inspection and after all commissioning tests have been completed, the operation of each of the systems is to be demonstrated to not less than two (2) persons nominated by the Contract Administrator.
note | Reference Documents: Appendix K- Technical Specifications )6.8 & 6.9
note | Inspection/ Test Method: Verify
note | Record of conformity: Training Plan Submission Reference
note | IP
note | Responsibility: FH Engineer / AGL Subcontractor
textbox | Date Completed:
checkpoint | 3.4 - Certificate of Electrical Safety
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria: Submission of a certificate of electrical safety for all new electrical systems installed in the project
note | Reference Documents: Appendix K- Technical Specifications )1.7.3
note | Inspection/ Test Method: Verify
note | Record of conformity: Certificate of Electrical Safety
note | IP
note | Responsibility: FH Engineer / AGL Subcontractor
textbox | Date Completed:
checkpoint | 3.5 - Handover Documentation
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria:
note | • Submission of all quality assurance documentation including as builts and schedules to the project manager.
note | • Information provided shall include:
note | – Circuit details including cable route, loading, Quantity per conduit, origin & destination.
note | – Number of series transformers and location of joints.
note | – Equipment and materials used.
note | – Testing and commissioning values for all modified or new equipment.
note | Reference Documents: Appendix K- Technical Specifications )Section 6
note | Inspection/ Test Method: Verify
note | Record of conformity: Submission Reference
note | HP*
note | Responsibility: FH Engineer
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: