## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP016 - AGL Removal of Luminaires and Install of foundations | itp |  |  |  |  | ITP016 - AGL Removal of Luminaires and Install of foundations
section | 1.0 Preliminary Works
checkpoint | 1.1 - Check for correct documentation
note | Frequency: Prior to commencing any activity
note | Acceptance Criteria: Ensure that all employees and subcontractors are using the latest and complete set of drawings
note | Reference Documents:
note | • IFC Drawings
note | • Appendix K- AGL Specification
note | Inspection/ Test Method: Verify
note | Record of conformity: Drawings
note | IP
note | Responsibility: Subcontractor Representative
textbox | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
note | Frequency: Prior to commencing any activities
note | Acceptance Criteria: All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
note | Inspection/ Test Method: Verify
note | Record of conformity: Site and Office Inspection
note | HP*
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 1.3 - Material/Equipment Approvals and Certification
note | Frequency: Prior to Start
note | Acceptance Criteria: All materials shall be proven to meet contractual requirements prior to acceptance.
note | Reference Documents: Appendix K- AGL Specification Section 2.3.3
note | Inspection/ Test Method: Verify
note | Record of conformity: Datasheet/ Material Submission
note | HP*
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 1.4 - As-built location
note | Frequency: Prior to commencing any activity
note | Acceptance Criteria: Surveyor to pick up existing location of all AGL Luminaires and position of foundations are prescribed based on design RL.
note | Reference Documents: Survey Documentation
note | Inspection/ Test Method: Verify
note | Record of conformity: Survey as Built
note | SPC
note | Responsibility: Site Engineer
textbox | Date Completed:
section | 2.0 Removal of AGL Luminaires and installation of Foundation (All light types)
checkpoint | 2.1 - Confirmation of pre-works
note | Frequency: Each Light
note | Acceptance Criteria: Ensure that the light to be removed corresponds to project drawings and documentation.
note | Reference Documents: IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.3 - Isolation of lights
note | Frequency: Each Light
note | Acceptance Criteria: Prior to commencement of removal, the subcontractor shall ensure that the light has been isolated from power.
note | Reference Documents: APAM Electrical Isolation Standards
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.4 - Light removal
note | Frequency: Each Light
note | Acceptance Criteria: Remove existing light and AGL cables from conduits as per Sub-Contractor ITC for the Method 1- 8 lights.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | • Sub-Contractor ITC
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.5 - Light storage
note | Frequency: Each Light
note | Acceptance Criteria: After removal of the light, the subcontractor must ensure that the light number and position is recorded and stored accordingly for re-installation.
note | Reference Documents: IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
section | 3.0 Installation of Light Foundation
checkpoint | 3.1 - Coring
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Core pavement to required depth as per subcontractor ITC for relevant Method. Remove base and clean void.
note | • Existing AGL secondary cables removed after coring.
note | Reference Documents:
note | • AGL Subcontractor ITC
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Subcontractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 3.2 - Installation of foundation
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Method 1:
note | 1) Position bung/spacer in 150mm diameter hole of foundation. Ensure cables and conduits are clear and clean.
note | 2) Apply Nitrobond to face of existing foundation.
note | 3) Mix and position quick set concrete onto the top of the existing foundation and let cure.
note | • Method 2:
note | 1) Conduits repaired after coring of light base to subgrade level. Where 2 conduits are parallel with limited spacing for exterior coupling, a stainless steel sleeve inside the conduits is to be placed, this will be glued into each end. - The thickness of the stainless steel sleeve is 1.6mm ensuring. A Coupling is then used to connect the conduits on either side of the foundation void.
note | 2) Mix and position quick set concrete onto the top of subgrade and let cure.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | • Sub-Contractor ITC
note | • FHPL-RFI-000135
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 3.3 - Blanking Plate
note | Frequency: Each Light
note | Acceptance Criteria: As required, luminaire fittings to be safeguarded to allow for placement of asphalt with a Blanking plate.
note | Reference Documents: IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This Signed ITP & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 3.4 - Asphalt Backfill
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Place hotmix asphalt in void above new foundation and compact using hand tools.
note | • Ensure asphalt is finished flush with surrounding surface.
note | Reference Documents: IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & AGL Sub-Contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: