## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP020 - AGL Precast Pits | itp |  |  |  |  | ITP020 - AGL Precast Pits
section | 1.0 Preliminary Works
checkpoint | 1.1 - Check for Correct Documentation
note | Frequency: Prior to commencing activity
note | Acceptance Criteria:
note | • Ensure that all employees and subcontractors are:
note | – using the correct and complete set of drawings
note | – all drawings are the latest revision
note | Reference Documents: Drawings / Aconex Register
note | Inspection/ Test Method: Verify
note | Record of conformity: Drawings and drawing registers
note | HP*
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
note | Frequency: Prior to commencing activity
note | Acceptance Criteria: All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP
note | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP signed
note | HP*
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 1.3 - Definition of the work Area & Survey check
note | Frequency: Prior to commencing activity
note | Acceptance Criteria: Work area has been cleared and surveyed (marked on site). Work area to be clearly defined as per For Construction drawings prior to trenching and install.
note | Reference Documents: IFC Drawings 12554937-E014 to E028
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Sub-contractor ITC
note | SCP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 1.4 - Excavation Works
note | Frequency: Prior to commencing activity
note | Acceptance Criteria:
note | • Location of services to be found and marked on the ground within the works;
note | • Obtain excavation permit from APAM prior to any excavation works.
note | • Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
note | Reference Documents:
note | • APAM- DBYD Job:32711991 Seq:215891341
note | • FH Permit
note | • Appendix K- Technical Specifications Cl.3.9.3
note | Inspection/ Test Method: Verify
note | Record of conformity: Melbourne Airport Excavation Permit
note | HP*
note | Responsibility: Site Engineer / Surveyor
textbox | Date Completed:
checkpoint | 1.5 - Native Grass Protection
note | Frequency: Prior to commencing activity
note | Acceptance Criteria: Native grass protection installed. As per native grass model, 8m wide corridor delineated by bollards/ fencing.
note | Reference Documents: Relevant Native Grass Permit
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP signed
note | IP
note | Responsibility: Site Engineer/Site Supervisor
textbox | Date Completed:
checkpoint | 1.6 - Service Locating/Proving
note | Frequency: Prior to commencing Excavation Works
note | Acceptance Criteria:
note | • Location of services to be found and marked on the ground within the works;
note | • Obtain excavation permit from APAM prior to any demolition works.
note | • Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
note | Reference Documents:
note | • APAM- DBYD Job:32711991 Seq:215891341
note | • FH Permit
note | • Appendix K- Technical Specifications Cl.3.9.3
note | Inspection/ Test Method: Verify
note | Record of conformity: Melbourne Airport Excavation Permit
note | HP*
note | Responsibility: Site Engineer / Surveyor
textbox | Date Completed:
checkpoint | 1.7 - Native Grass Protection
note | Frequency: Prior to commencing activity
note | Acceptance Criteria: Native grass protection installed. As per native grass model, 8m wide corridor delineated by bollards/ fencing.
note | Reference Documents: Relevant Native Grass Permit
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP signed
note | IP
note | Responsibility: Site Engineer/Site Supervisor
textbox | Date Completed:
section | 2.0 Supply of Materials
checkpoint | 2.1 - Materials & source Approval
note | Frequency: Pre-commencement
note | Acceptance Criteria:
note | • Provide full details of pit types to the Contract administrator including, but not limited to:
note | – Manufacturer
note | – Model Number
note | – External Dimensions
note | – Internal Dimensions
note | – Maximum number of penetrations of each conduit size for each pit wall
note | – Depth of penetrations
note | – Label recess dimensions
note | – SIT tray details/ installation details
note | – Installation requirements
note | – Lid details including
note | ○ Model Number
note | ○ Dimensions
note | ○ Materials
note | ○ Lifting points / mechanism
note | ○ Load rating
note | ○ Removal tools
note | Reference Documents: Appendix K- Technical Specifications - Section 2.7
note | Inspection/ Test Method: Verify
note | Record of conformity: Aconex correspondence Reference Approval
note | AP
note | Responsibility: Site Engineer and Principal’s Representative
textbox | Date Completed:
section | 3.0 Excavation
checkpoint | 3.1 - Excavation Obstruction
note | Frequency: Each lot
note | Acceptance Criteria:
note | • Any rock found to impose significantly on excavations (i.e. rock that cannot be excavated by means of a Rock Saw, Caterpillar D7 with single tyne ripper or similar suitably equipped machine) must be brought to the attention of the Contract Administrator
note | • Cable pits must be relocated as necessary to avoid significant areas of rock that cannot be excavated. Provide details of proposed pit relocations to the Contract Administrator for approval.
note | Reference Documents:
note | • Appendix K- Technical Specifications )3.9.7
note | • AGL Conduit Install ITC
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP signed
note | HP
note | Responsibility: Site Engineer / Foreman / Principal’s Representative
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Confirm Ground
note | Frequency: Each Lot
note | Acceptance Criteria: Pits shall be constructed on firm subgrade as per methods listed in item 3.3, in accordance with manufacturer’s instructions
note | Reference Documents:
note | • IFC Drawings
note | • Manufacturer installation guide
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP signed
note | HP*
note | Responsibility: Site Engineer / Foreman
textbox | Date Completed:
checkpoint | 3.3 - Blinding
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Blinding to be installed in either of the following methods:
note | – 50mm 20Mpa Concrete
note | – 100mm Class 2 Wet Mix Crushed Rock – Compacted to refusal using handheld mechanical aid (DPU / Wacker Plate).
note | • Installed blinding layer is to be stable and level to ensure the precast pit is vertical
note | Reference Documents:
note | • IFC Drawings
note | • Manufacturer installation guide
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP signed
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
section | 4.0 Precast Pit Fabrication & Delivery
checkpoint | 4.1 - Pit Delivery
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Ensure each pit component is inspected upon arrival ensuring:
note | – Dimensions are as shown on manufacturer drawings
note | – All blockouts in correct positions and to dimensions.
note | – No damage to any pit component to the satisfaction of Site Engineer
note | • No modifications to the pits are to be made without written approval from manufacturer.
note | • Conduit entries to be drilled on site, with defined area defined by pit manufacturer.
note | Reference Documents: Appendix K- Technical Specifications
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP Signed
note | HP*
note | Responsibility: Site Engineer
textbox | Date Completed:
section | 5.0 Pit Installation
checkpoint | 5.1 - Positioning Pit Components
note | Frequency: Each Lot
note | Acceptance Criteria: Pits must be constructed at the locations shown on the drawings.
note | Reference Documents: IFC Drawings
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed
note | HP*
note | Responsibility: Surveyor
textbox | Date Completed:
checkpoint | 5.2 - Construction / Levels
note | Frequency: Each Lot
note | Acceptance Criteria: Install new pits as shown on drawings such that its collar and lid is level and at the same level as the finished adjacent surface.
note | Reference Documents: Appendix K- Technical Specifications - Section 3.8
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed
note | HP*
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 5.3 - Pit Entries
note | Frequency: Each Lot
note | Acceptance Criteria: Seal buried entries to all pits with a waterproof compound where necessary to prevent the ingress of soil and mud after backfill. Seal spare pit entries immediately after installation with a temporary cap.
note | Reference Documents: Appendix K- Technical Specifications - Section 3.8
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed
note | HP*
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 5.4 - Bedding & Backfilling
note | Frequency: Each lot
note | Acceptance Criteria:
note | • In trenches, the lower layers to the level of 300 mm above the top of the conduits must be carefully bedded and consolidated at the appropriate moisture content under, around and on top of the conduits to not less than 90% MDD in accordance with test No. 5.1.1 of Australian Standard 1289 in the case of cohesive material, and not less than 70% of the density index in accordance with test No. E6.1 of Australian Standard 1289 in the case of cohesionless material.
note | • If the excavated soil is not compactible material free of rocks or will not pass through a 25 mm sieve then:
note | – The bottom of the trench must comprise a bed of 50 mm of sand placed before the first enclosure or cable is laid; and
note | – A layer of sand must be placed to cover the conduit with 75 mm of sand before backfilling
note | • Compaction Testing under roads must be carried out at a rate of not less than:
note | – Bedding: 1 test per 25 m of backfill laid
note | – Backfill: 1 test per 25 m of backfill laid per 0.5 m of backfill depth
note | – Subgrade: 1 test per 25 m of backfill laid – Base: 1 test per 25 m of backfill laid
note | Reference Documents:
note | • Appendix K- Technical Specifications )3.9.9
note | • AGL Conduit Install ITC
note | Inspection/ Test Method: Verify
note | Record of conformity: Test Report and This ITP Signed
note | TP/IP
note | Responsibility: Site Engineer / Foreman
textbox | Date Completed:
checkpoint | 5.5 - Pit Fit out
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Ensure that all installation requirements are as detailed in drawings including:
note | – Pit ID plate & label
note | – Conduit directions markers
note | – Earth Bar
note | – SIT tray
note | Reference Documents: IFC Drawings 12554937-E045 & E050
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 5.6 - Lid Encasement Slab Installation
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Seal Pit Wall and Lid encasement slab using mastic type sealant ensuring no gaps remain.
note | • Any encasement slab on a slope is to be checked by the surveyor and achieved using packers and infilled using non-shrink grout.
note | Reference Documents: Manufacturer Guide
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP Signed
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 5.7 - Earth Pit Installation
note | Frequency: Each Lot
note | Acceptance Criteria: Install earth pit next to AGL pit as shown in IFC drawing.
note | Reference Documents: IFC Drawing 12554937-E050
note | Inspection/ Test Method: Visual Inspection
note | Record of conformity: This ITP Signed
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
section | 6.0 Post Installation
checkpoint | 6.1 - As-built Documentation
note | Frequency: Prior to Practical Completion
note | Acceptance Criteria: Record the location of all new pits, as well as any existing pits utilised by the works. Prior to backfilling accurately record the location of routes of underground cables.
note | Reference Documents: Appendix K- Technical Specifications 3.18
note | Inspection/ Test Method: Verify
note | Record of conformity: As-built Survey Report
note | SCP
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: