## ITP
|  |  | Inspection and Test Plan - Watermain Construction | [7 empty] | Document # 1145-C200-FUL-QAC-ITP-0079
[11 empty] | Revision: 02 | Date : 13/02/2023
Client: | MRPV |  | Construction Process: | Watermain Construction |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: | Craigieburn Road Upgrade |  | Specifications: | WSA 03-2011 |  | Name: | Carlo Urpis | Name: | Matthew Lee Archer |  | Name: | Babak Rudd
Contract No: | 1145 |  | Structure / Component: | Pipeline |  | Position: | Site Engineer | Position: | SPE/Area Manager |  | Position: | Quality Manager
|  |  | Location: |  |  | Date : | 2022-03-16 | Date : | 2022-03-16 |  | Date : | 2022-03-18
Lot No: | ITP-079-AX-LOT-XXX |  | Lot Title: | ITP-079-AX-LOT-XXX - Desc | Location: From ( ) to ( ) |  |  | Lot Size/ Quantity: |  |  | Lot Opened Date:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Superintendent | Fulton Hogan | FH's Sub-contractor | Date
Preliminary Works
1 | Issued for construction drawings |  | Prior to commencement | Ensure the most current revision of drawings is used to conduct the works. | IFC drawings | Review | Compliance checklist - Daily Prestart Form | HP* | Project Manager/Engineer | N/A |  | N/A
2 | Permits with relevant authorities |  | Prior to commencement | Permits to be obtained by relevant authorities | DBYD | Review DBYD | Compliance checklist –Excavation Permit | HP* | Project Manager/Engineer | N/A |  | N/A
SURVEY, SETOUT & LOCATION OF EXISTING SERVICES
3 | Survey set-out |  | Prior to commencement | Building line pegs to be installed prior to any excavation | IFC drawings | Visual check | Compliance checklist - Pipeline construction | SCP | Surveyor | N/A |  | N/A
4 | Service location |  | Prior to Excavations onsite | All existing services to be located and protections in place | DBYD | Review drawings and DBYD | Compliance checklist –Excavation Permit | WP | Site Manager/Engineer/Superintendent | N/A |  | N/A
4.1 | Installation of property service conduits |  | Prior to commencement | All service ducts required by road contractor to be installed prior to works to be inspected and ensure they meet MRWA standards | MRWA-W-110 | Visual check | Site Daily Diary Entry | HP* | Site Manager/Engineer | N/A |  | N/A
MATERIAL CONFORMANCE
5 | Correct pipe and fittings onsite |  | When delivered | Inspect materials in delivery against order. Pipe size matches plans | Delivery docket/ IFC drawings | Visual check | Compliance checklist - Pipeline construction | HP* | Site Manager/Engineer | N/A |  | N/A
6 | Correct embedment / backfill materials onsite |  | When delivered | Inspect bedding material to ensure suitability | MRWA-W-201 to 203 | Visual check | Compliance checklist - Pipeline construction | HP* | Site Manager/Engineer | N/A |  | N/A
ENVIROMENTAL & SAFETY
7 | Environmental controls |  | Daily | Ensure environmental controls in place and being maintained as per the site EMP (if the civil contractor is responsible for managing the site then as long as we do not distrust their controls this item can be ticked as N/A) | EMP | Visual | Compliance checklist - Daily Prestart Form | HP* | Site Manager/Engineer | N/A |  | N/A
8 | Safety controls |  | Daily | Ensure safety controls are in place as per the relevant safety instructions and SWMS | SMP | Visual | Compliance checklist - Daily Prestart Form | HP* | Site Manager/Engineer | N/A |  | N/A
TRENCHING & EXCAVATION
9 | Trenching |  | Prior to entry into open trench | Ensure trench width and depth are within tolerance | IFC drawings / MRWA-W-202 | Visual | Compliance checklist - Pipeline construction | SCP | Site Manager/Engineer | N/A |  | N/A
10 | Trenching |  | Prior to entry into open trench | Ensure trench foundation & wall firm, stiff & suitable | MRWA-W-202 | Visual | Compliance checklist - Pipeline construction | HP* | Site Manager/Engineer | N/A |  | N/A
11 | Placement of embedment material |  | Prior to backfilling of specified area of trench | Ensure pipe bedding depth is acceptable | MRWA-W-202 | Visual | Compliance checklist - Pipeline construction | HP* | Site Manager/Engineer | N/A |  | N/A
PIPE INSTALLATION
12 | Pipe laying |  | Prior to backfilling of specified area of trench | Ensure pipe joint deflection is acceptable and witness marks are applied and visible | MRWA-W-103 | Visual | Compliance checklist - Pipeline construction | HP* | Site Manager/Engineer | N/A |  | N/A
13 | Property services |  | Prior to backfilling of specified area of trench | Ensure tapping collars are installed as per measurements on plans | IFC drawings | Visual | As constructed information / Compliance checklist - Pipeline construction | SCP | Site Manager/Engineer | N/A |  | N/A
14 | Dual water property services |  | Prior to backfilling of specified area of trench | Ensure tapping collars are installed as per dual water specifications (to the left of the DW) | IFC drawings / MRWA-W110 & 111 | Visual | As constructed information / Compliance checklist - Pipeline construction | WP | Site Manager/Engineer/Superintendent |  |  | N/A
15 | Valve installation |  | Prior to backfilling of specified area of trench | Ensure valves are installed correctly. | IFC drawings / WSA page 233 15.4 | Visual | As constructed information / Compliance checklist - Pipeline construction | SCP | Site Manager/Engineer | N/A |  | N/A
16 | Hydrant installation |  | Prior to backfilling of specified area of trench | Ensure hydrants are installed correctly. | IFC drawings / WSA page 233 15.4 | Visual | As constructed information / Compliance checklist - Pipeline construction | SCP | Site Manager/Engineer | N/A |  | N/A
17 | Washout installation |  | Prior to backfilling of specified area of trench | Ensure washouts are installed correctly. | IFC drawings / WSA page 233 15.4 | Visual | As constructed information / Compliance checklist - Pipeline construction | SCP | Site Manager/Engineer | N/A |  | N/A
CONCRETE ANCHOR BLOCKS
18 | Acceptance of concrete delivery |  | When concrete is required | Concrete delivered to site to be acceptable. WIN 25 WSA approved mix (20Mpa, 20mm rock , 80 slump) | Concrete delivery docket | Visual | Watermain Anchor Block Checklist – Procedural Verification Checklist ITC-803(SEW .018) | HP* | Site Manager | N/A |  | N/A
19 | Installation of anchor blocks and thrust restraints |  | When concrete is required | Installed anchor blocks / thrust restraints are acceptable | MRWA-W-204,205A & 205B | Visual | Watermain Anchor Block Checklist – Procedural Verification Checklist ITC-803(SEW .018) | WP | Site Manager/Engineer/Superintendent |  |  | N/A
19.1 | Correct steel reinforcement used in restraint |  | Prior to anchor blocks being poured | Reinforcement is as per MRWA 205-A, 205-B and according to thrust area as noted in face sheet of project plan | MRWA – W – 205-A and 205-B | Visual | Watermain Anchor Block Checklist – Procedural Verification Checklist ITC-803 (SEW .018) | WP | Site Manager/Engineer/Superintendent |  |  | N/A
BACKFILL OF TRENCHES
20 | Placement of embedment overlay |  | Completion of pipelaying | Ensure overlay depth & installation is acceptable | MRWA-W-202 | Visual | Compliance checklist - Pipeline construction | HP* | Site Manager | N/A |  | N/A
21 | Installation of detectable marker tape |  | Completion of pipelaying | Detectable marker tape to be installed in first layer of backfill | MRWA-W-202 | Visual | Compliance checklist - Pipeline construction | HP* | Site Manager | N/A |  | N/A
22 | Placement of compactable material in trafficable areas |  | Completion of pipelaying | Backfill material to be acceptable & compaction of trench line completed | MRWA-W-202,202 | Visual / NATA if required | Compliance checklist - Pipeline construction | HP* | Site Manager | N/A |  | N/A
23 | Monitoring of WC1 works |  | Once per week | Crews compliance with all Fulton Hogan Procedures and SWMS | Pipelines SMP, SWMS, Trenching Procedure | Visual | Weekly Site Safety Inspection Checklist | HP* | Project Manager/Engineer | N/A |  | N/A
24 | Monitoring of WC2 works |  | Twice per week | Crews compliance with all Fulton Hogan Procedures and SWMS | Pipelines SMP, SWMS, Trenching Procedure | Visual | Weekly Site Safety Inspection Checklist | HP* | Project Manager/Engineer | N/A
QUALITY
25 | Swabbing and flushing, Pressure test and Chlorination works |  | Completion of pipelaying | Pressure testing held for 5hr duration | WSA 03-2011 - 18.3, 19.2 | Visual | Compliance checklist - Pipeline construction | HP* | Site Manager | N/A |  | N/A
26 | Water quality testing. |  | Completion of pipelaying | Conduct a bacteriological test on all new mains following satisfactory completion of swabbing/flushing and pressure testing of the water main | WSA 03-2011 19.7 | Written | The test results fall within the water quality parameter | HP* | Site Manager | N/A |  | N/A
Notes
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Work Completed On:
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
AP | Approval Point | Written or verbal approval given by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
[5 empty] | WP | Witness Point |  | An inspection which must be witnessed by the Superintendent