## PROJECT STRUCTURE
Folder Structure |  |  |  | Checklists
FLAT BUSH SCHOOL | PROJECT: HORIZON RADIOLOGY
INTERIOR FITOUT
CONTAINMENT
|  |  | IT ROOM | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | RECEPTION/SEATING | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | HALLWAY | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | WC 1-B | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | WC 2-B | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | ADMIN OFFICE | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | CHANGE ROOM 01 | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | CHANGE ROOM 02 | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | STAFF BREAK OUTROOM | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | X-RAY & CONTROL ROOM | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | ULTRASOUND 1 | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | ULTRASOUND 2 | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | ULTRASOUND 3 | CONTAINMENT - CATNERY WIRE INSTALL
|  |  | ULTRASOUND 4 | CONTAINMENT - CATNERY WIRE INSTALL
ROOM
|  |  | IT ROOM | 1ST FIX
2ND FIX
IT ROOM
|  |  | RECEPTION/SEATING | 1ST FIX
2ND FIX
|  |  | HALLWAY | 1ST FIX
2ND FIX
|  |  | WC2-B | 1ST FIX
2ND FIX
|  |  | WC 1-B | 1ST FIX
2ND FIX
|  |  | ADMIN OFFICE | 1ST FIX
2ND FIX
|  |  | CHANGE ROOM 01 | 1ST FIX
2ND FIX
|  |  | CHANGE ROOM 02 | 1ST FIX
2ND FIX
|  |  | STAFF BREAK OUTROOM | 1ST FIX
2ND FIX
|  |  | X-RAY & CONTROL ROOM | 1ST FIX X- RAY ROOM
2ND FIX
|  |  | ULTRASOUND 1 | 1ST FIX - ULTRASOUND ROOM
2ND FIX
|  |  | ULTRASOUND 2 | 1ST FIX - ULTRASOUND ROOM
2ND FIX
|  |  | ULTRASOUND 3 | 1ST FIX - ULTRASOUND ROOM
2ND FIX
|  |  | ULTRASOUND 4 | 1ST FIX - ULTRASOUND ROOM
2ND FIX
DISTRIBUTION
SWITCHBOARD
DISTRIBUTION BOARD DB-0-PG
COMMISSIONING - DISTRIBUTION BOARD DB-0-PG

## CHECKPOINTS
TYPE | NAME
CHECKLIST | CONTAINMENT - CATENERY WIRE INSTALL
CHECKPOINT | WOOD EYE/CONCRETE ANCHORS INSTALLED AND CORRECTLY FIXED ONTO CONCRETE SLABS
CHECKPOINT | SUFFICIENT CATENERY WIRE SUPPORTS INSTALLED AT APPROX 1.2M INTERVALS
CHECKPOINT | CATENRY WIRES INSTALLED AT HIGH LEVEL AND MEETS CLEARENCE FROM OTHER SERVICES
CHECKPOINT | TURNBUCKLES IS TIGHTENED AND CATENERY WIRE IS WELL SECURED
CHEECK POINT | EXISTING CATNERY WIRES ARE SUPPORTED AND FIXED CORRECTLY WHERE REQUIRED
CHECKLIST | 1ST FIX
CHECKPOINT | CABLING INSTALLED AS PER LGHTING AND POWER LOCATIONS REFLECTED
CHECKPOINT | DATA CABLES INSTALLED, CABLE LABELLED AND CONFIRMED AS PER DATA LAYOUT
CHECKPOINT | DATA CABLES ARE RUN ON A SEPARATE CAT WIRE, VELCRO TIED IN 24 DATA CABLES PER BUNDLE
CHECKPOINT | DATA CABLES RAN BACK TO COMMS CABINET.
CHECKPOINT | CORRECT SIZE POWER/LIGHTING CABLE INSTALLED AS PER CABLE CALC TO LOADS AND VOLTAGE DROP
CHECKPOINT | FLUSH BOXES MOUNTED AS PER ARCHITECTURAL ELEVATION
CHECKPOINT | RFIs TO SET OUT AND LOCATION ARE CONFIRMED
CHECKPOINT | FLUSH BOXES FOR ISOLATORS INSTALLED ABOVE BENCH OR AT ACCESSIABLE LOCATION TO APPLIANCE
CHECKPOINT | FEED AND SWITCH WIRES INSTALLED AND CONFIMRED FOR LIGHTING
CHECKPOINT | HOTWATER CABLE INSTALLED AND LOCATION CONFIMRED WITH PLUMBER
CHECKPOINT | PUMP CABLING INSTALLED AND LOCATION CONFIMRED WITH PLUMBER
CHECKPOINT | STAFF AREA KITCHEN APPLIANCE LOCATION CONFIMRED AS PER APPROVED SET OUT
CHECKPOINT | CORRECT CABLE SIZE IS INSTALLED AS PER APPLIANCE SPEC
CHECKPOINT | APPLIANCE ISOLATORS INSTALLED A/B OR AT ACCESSIBLE LOCATION
CHECKPOINT | LCP FLUSH BOX MOUNTED AND SWITCH CONTROL WIRES INSTALLED BETWEEN LCP AND DB CONTROL
CHECKPOINT | LIGHTING LOOPS INSTALLED AS PER LIGHTING LAYOUT
CHECKPOINT | SWITCH LOCATIONS CONFIRMED AND IS ACCESSIABLE UPON ENTRY TO ROOM
CHECKPOINT | EMERGENCY CIRCUITS AND LOOPS CHECKED AND COMPLETED.
CHECKPOINT | LIGHTING AND POWER CIRCUITS TO THIS ROOM IS CONFIRMED AND ALL LOOPS ARE CHECKED AND CONFIMRED
CHECKPOINT | BOND CABLE TO CEILING GRID/SINKS AND STRUCTURE IS RAN AND CONFIRMED
CHECKPOINT | HALLWAY POWER CIRUITS WIRED AS CLEANING PURPOSE ONLY OUTLETS
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKLIST | 2ND FIX
CHECKPOINT | LIGHT SWITCHES INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | POWER OUTLETS INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | DATA OUTLETS INSTALLED, LEVELLED, LABELLED AND TESTED.
CHECKPOINT | HALLWAY OUTETS DEEMED CLEANERS OUTLETS INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | SURFACE SOCKETS FITTED OFF FOR PAN FITTINGS, DOWNLIGHTS AND EMERGENCY LIGHTS
CHECKPOINT | SURFACE SOCKETS ARE LABELLED TO ALLOCATED CIRCUITS CORRECTLY
CHECKPOINT | PAN FITTINGS, DOWNLIGHTS AND EMERGENCY LIGHTS ARE INSTALLED IN CORRECT LOCATIONS.
CHECKPOINT | LCP PANEL IS FITTED OFF AND LIGHTS ARE SWITCHING CORRECTLY.
CHECKPOINT | EMERGENCY LIGHTS INSTALLED, LABELLED, LIVE AND WORKING CORRECTLY.
CHECKPOINT | CONDUIT INSTALLED, PLUMMBED AND LEVEL TO MOUNTING BLOCK FOR OUTLETS WHERE REUIRED.
CHECKPOINT | CEILING GRID/SINKS/ BUILDING STRUCTURE IS BONDED AND TEST RESULTS < 0.5 OHMS TO DB
CHECKPOINT | MACHINE OUTLETS INSTALLED, LEVELLED, LABELLED AND WORKING CORRECTLY.
CHECKLIST | 1ST FIX - ULTRASOUND ROOM
CHECKPOINT | DEDICATED POWER CIRCUITS TO ROOM
CHECKPOINT | CABLING INSTALLED AS PER LGHTING AND POWER LOCATIONS REFLECTED ON ARCHITECTURAL
CHECKPOINT | FLUSH BOXES MOUNTED AT CORRECT LOCATIONS TO APPROVED ELEVATION
CHECKPOINT | RCD FLSUH BOX IS MOUNTED AT 1800MM AFFL AND IS INSTALLED AT A ACCESSIABLE LOCATION
CHECKPOINT | RFIs TO SET OUT AND LOCATION ARE CONFIRMED
CHECKPOINT | DATA CABLES INSTALLED, CABLE LABELLED AND CONFIRMED AS PER DATA LAYOUT
CHECKPOINT | DATA CABLES ARE RUN ON A SEPARATE CAT WIRE, VELCRO TIED IN 24 DATA CABLES PER BUNDLE
CHECKPOINT | CORRECT SIZE POWER&LIGHTING CABLE INSTALLED AS PER CABLE CALC TO LOADS AND VOLTAGE DROP
CHECKPOINT | FEED AND SWITCH WIRES INSTALLED AND CONFIMRED FOR LIGHTING
CHECKPOINT | DIM FUNCTION EITHER PHASE OR DALI TO SWITCH CONSIDERED AND APPROVED.
CHECKPOINT | SWITCH LOCATIONS CONFIRMED AND IS ACCESSIABLE UPON ENTRY TO ROOM
CHECKPOINT | EMERGENCY CIRCUITS AND LOOPS CHECKED AND COMPLETED.
CHECKPOINT | LIGHTING AND POWER CIRCUITS TO THIS ROOM IS CONFIRMED AND ALL LOOPS ARE CHECKED
CHECKPOINT | BONDING CABLE TO CEILING GRID/STRUCTURE AND MSP IS RAN AND CONFIRMED
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKPOINT | CONFIRM BPA ROOM POWER OUTLETS ARE RCD PROTECTED FROM RCD POINT WITHIN ROOM
CHECKPOINT | BONDING CABLE TO CEILING GRID AND STRUCTURE IS RAN AND CONFIRMED
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKPOINT | BPA ROOMS MEET AS/NZS 3003:2018 PATIENT AREA STANDARD
CHECKPOINT | BPA ROOM INSPECTED
CHECKLIST | 1ST FIX - X-RAY ROOM
CHECKPOINT | DEDICATED POWER CIRCUITS TO ROOM
CHECKPOINT | CABLING INSTALLED AS PER LGHTING AND POWER LOCATIONS REFLECTED ON ARCHITECTURAL
CHECKPOINT | FLUSH BOXES MOUNTED AT CORRECT LOCATIONS TO APPROVED ELEVATION
CHECKPOINT | RFIs TO SET OUT AND LOCATION ARE CONFIRMED
CHECKPOINT | DATA/VOICE CABLES INSTALLED, CABLE LABELLED AND CONFIRMED AS PER DATA LAYOUT
CHECKPOINT | DATA CABLES ARE RUN ON A SEPARATE CAT WIRE, VELCRO TIED IN 24 DATA CABLES PER BUNDLE
CHECKPOINT | CORRECT SIZE POWER & LIGHTING CABLE INSTALLED AS PER CABLE CALC TO LOADS AND VOLTAGE DROP
CHECKPOINT | FEED AND SWITCH WIRES INSTALLED AND CONFIMRED FOR LIGHTING
CHECKPOINT | CORRECT CABLE SIZE IS INSTALLED AS PER MACHINE SPEC
CHECKPOINT | SWITCH LOCATIONS CONFIRMED AND IS ACCESSIABLE UPON ENTRY TO ROOM
CHECKPOINT | DIM FUNCTION EITHER PHASE OR DALI TO SWITCH CONSIDERED AND APPROVED.
CHECKPOINT | LIGHTING LOOPS INSTALLED AS PER LIGHTING LAYOUT
CHECKPOINT | EMERGENCY CIRCUITS AND LOOPS CHECKED AND COMPLETED.
CHECKPOINT | LIGHTING AND POWER CIRCUITS TO THIS ROOM IS CONFIRMED AND ALL LOOPS ARE CHECKED
CHECKPOINT | BONDING CABLE TO CEILING GRID/STRUCTURE/SINKS CONFIRMED
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKPOINT | CONFIRM BPA ROOM POWER OUTLETS ARE RCD PROTECTED FROM RCD POINT WITHIN ROOM
CHECKPOINT | RCD FLSUH BOX IS MOUNTED AT 1800MM AFFL AND IS INSTALLED AT A ACCESSIABLE LOCATION
CHECKPOINT | DEDICATED CIRCUIT INSTALLED TO BREAST SCREENING MACHINE
CHECKPOINT | ISOLATOR FOR BREAST SCREENING MACHINE INSTALLED CLOSE TO MACHINE AT ACCESSIBLE LOCATION
CHECKPOINT | BREAST SCREENING MACHINE IS PROTECTED BY 30mA TYPE A RCCB IN E4 BOX.
CHECKPOINT | DEDICATED CIRCUIT RAN TO ISOLATOR AND TYPE A 30mA RCCB FOR X-RAY MACHINE AS PER SPEC
CHECKPOINT | X RAY ON LIGHTING RAN AND BROUGHT THROUGH AT CONFIRMED LOCATION.
CHECKPOINT | BONDING CABLE TO CEILING GRID AND STRUCTURE IS RAN AND CONFIRMED
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKPOINT | BPA ROOMS MEET AS/NZS 3003:2018 PATIENT AREA STANDARD
CHECKPOINT | BONDING CABLE TO CEILING GRID AND STRUCTURE IS RAN AND CONFIRMED
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKPOINT | BPA ROOMS MEET AS/NZS 3003:2018 PATIENT AREA STANDARD
CHECKPOINT | BPA ROOM INSPECTED
CHECKLIST | IT ROOM
CHECKPOINT | COMMS CABINET/RACKS MOUNTED AT AGREED LOCATION
CHECKPOINT | ALL FIED DATA OUTLETS ARE FITTED OFF AND LABELLED.
CHECKPOINT | ALL CAT6 CABLES TERMINATED INTO PATCH PANEL
CHECKPOINT | ALL CAT6 CABLES ARE TESTED AND LABELLED CORRECTLY
CHECKPOINT | FRONT OF PATCH PANELS ARE LABELLED CORRECTLY TO FIELD OUTELTS AND CONFIRMED
CHECKPOINT | POWER OUTLET FOR COMMS CABINET INSTALLED, LABELLED AND LIVEN
CHECKPOINT | DATA CABINET IS BONDED AND READING IS <0.5 OHMS
CHECKLIST | DISTRIBUTION BOARD DB-O-PG
CHECKPOINT | CABLE TRAY/TRUNKING INSTALLED ABOVE DB FOR SUB CIRCUITS AND NEW SUB MAINS.
CHECKPOINT | SUB CIRCUITS AND SUB MAINS CABLE TIED AND DRESSSED NEATLY ON CAT WIRE/CABLE TRAY/TRUNKING
CHECKPOINT | NEW SUB MAINS TERMINATED AT MSB AND AT NEW DB-O-PG
CHECKPOINT | DISTRIBUTION BOARD INSTALLATION COMPLETED AND SECURELY MOUNTED
CHECKPOINT | SUBCIRCUITS TERMINATED INCLUDING LABELLING/FERRULES TO ALL CORES
CHECKPOINT | EARTHING/BONDING TERMINATED
CHECKPOINT | STRUCTURAL BONDING CABLE TERMINATED AT SWITCHBOARD.
CHECKPOINT | DB SCHEDULE COMPLETED
CHECKPOINT | DISTRIBUTION BOARD TEST SHEET COMPLETED
CHECKPOINT | DB SCHEDULE INSTALLED
CHECKPOINT | CLEAN OF ALL DEBRI AND MARKS
CHECKLIST | COMMISSIONING - DISTRIBUTION BOARD DB-O-PG
CHECKPOINT | SWITCHBOARD TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | DB SCHEDULE COMPLETED, INSTALLED INTO DB AND ADDED TO DROPBOX
CHECKPOINT | DISTRIBUTION BOARD TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | SUBCIRCUIT COMMISSIONING RESULTS SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | DISTRIBUTION BOARD CHECK SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | EARTHING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | EMERGENCY LIGHTING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | TIMECLOCK TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | BOARD FREE FROM DEBRI, NO MARKS, ALL ACCESSORIES INSTALLED
CHECKPOINT | LABELLING COMPLETED ON ALL FIELD OUTLETS, SWITCHES AND ISOLATORS ETC
CHECKPOINT | EMERGENCY LIGHTING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | SUBCIRCUIT COMMISSIONING RESULTS SHEET COMPLETED AND ADDED TO DROPBOX