## QA Folder Structure
QA Folder Structure |  |  |  | checklists
DLP Maintenance
Back flow Prevention Device
Column J
|  |  | Column N - Column M - Column C - Column - K | Backflow Prevention Device Test Report
Gas OPSO Valve
Column J
|  |  | Column N - Column M - Column C - Column - K | QA 6D - Quality Control Gas Regulation Test Report
TMV
Column J
|  |  | Column N - Column M - Column C - Column - K | TMV 12 Month Service Log (use a separate checklist for each valve)
Fire Protection tanks
Column J
|  |  | Column N - Column T - Column C - Column - K | Add Project Photos
Grease Interceptor Trap
Column J
|  |  | Column N - Column T - Column C - Column - K | Hydraulic Inspection Test - Sewer (peq)
Billi Hot/Chilled Taps
Column J
|  |  | Column N - Column M - Column C - Column - K | QA23 Boiling Water Service Maintenance Log
Cooling Pit
Column J
|  |  | Column N - Column T - Column C - Column - K | Hydraulic Inspection Test - Sewer (peq)
Domestic Hot Water Service
|  | Column D | Column H - Column Q - Column Q - Column -Q | QA 31 Hot Water Service Maintenance Log

## Checklists
type | name | values | prefix | postfix | Template Name | Template Id
checklist | TMV Commissioning Log Sheet V.020522 |  |  |  | TMV Commissioning Log Sheet V.020522 | 081113b2-4785-4a9c-bbda-04c12d76a8a9
checkpoint | TMV Commissioning Log Sheet:
note | Building Name: Victorian Heart Hospital
note | Contact Person: David Geschke
note | Address: 631 Blackburn Road, CLAYTON
note | Lic: 50043
textbox | Registration number:
note | Phone number: 03 9798 1619
dropdown | Make of valve | Aquablend ATM700,FM Matterson 9230,ESQX ATM621
dropdown | Model number: | Aquablend ATM700,FM Matterson 9230,ESQX ATM621
dropdown | Valve location | Basement 1,Ground,Level 1,Level 2,Level 3,Level 4,Level 5,Level 6,Level 7
textbox | Room name:
note | Valve purchased from: Bentons
textbox | Installation date:
textbox | Valve installed by:
textbox | Number of outlets served - Baths:
textbox | Number of outlets served - Basins:
textbox | Number of outlets served - Showers:
textbox | Total number of mixing valves on site:
button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No,Yes
button | Does the installation comply with the current requirements of the local water supply authority? | No,Yes
textbox | Temperature of hot water supply? |  |  | °C
textbox | Temperature of cold water supply? |  |  | °C
textbox | Temperature of warm water delivery at outlet fitting? |  |  | °C
textbox | Dynamic pressure of hot water: |  |  | kPa
textbox | Dynamic pressure of cold water: |  |  | kPa
checkpoint | Check fail safe operation (hot water at least 20c above warm water)
checkpoint | Commissioned by
textbox | Commissioned by:
textbox | Company name:
checklist | Stormwater Drainage Inspection Report |  |  |  | QA 8B - Stormwater Drainage Inspection Report (July 2020) | 0d3103cb-1f79-4d1d-81f3-dc55d1e5246c
checkpoint | Stormwater Drainage Inspection Report Details
textbox | Date
textbox | Drawing No
textbox | Zone
checkpoint | Pipe Lines
textbox | Date Started
textbox | Drainage Line Number
button | Pipe Damaged? | No, Yes
textbox | Size & class
button | Jointing Require | Yes, No
note | Bedding and Haunching
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
textbox | Comments
note | Final Sign-Off (Initial & Date)
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
checkpoint | Drainage Pits
textbox | Date Installed
textbox | Pit Number
textbox | Pit Base
textbox | Step Irons - GPL Initial/Date
textbox | Bedding - GPL Initial/Date
note | Benching, Grouting & Patching
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
note | Placement of Cover
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
textbox | Comments
note | Final Sign-Off (Initial & Date)
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
checkpoint | SPEL HS180 Chamber Assembly
textbox | Date Installed
textbox | Chamber Assembly Line Number
button | Chamber Damaged? | No, Yes
textbox | Size & Class
button | Jointing Required | Yes, No
note | Bedding and Haunching
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
note | Backfill
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
textbox | Comments
note | Final Sign-Off (Initial & Date)
textbox | GPL - Initial/Date
textbox | Builder - Initial/Date
checkpoint | Compaction Test Report No
textbox | Compaction Test Report No
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | Commissioning Test Report |  |  |  | QA 7 - Commissioning Test Report | 172bd6e2-ab0b-432d-8990-2dce6e29c6fc
checkpoint | Commissioning Test Report:
textbox | Zone/Grid:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | Item: FIXTURE OPERATION - Pans, Basins, Sinks, Other
note | Test:
note | Performance Test CL 2.20
note | Fill fixture with water remove plug
note | Test for:
note | Leaks
note | Loss of water
note | Seal in Trap
note | Induce siphonage in trap of adjacent fixture
note | Complete draining of fixture
textbox | OK:
textbox | Not OK:
checkpoint | Item: Water Supply
note | Test:
note | Performance Test CL 2.20
note | Check for adequate water volume.
note | Flush out pipework
note | Clean aerator
note | Water hammer
textbox | OK:
textbox | Not OK:
checkpoint | Item: Flush Performance
note | Test:
note | Performance Test
note | Check for:
note | Water Volume
note | Duration of flush
note | Flush out pipework
note | Water hammer
textbox | OK:
textbox | Not OK:
checkpoint | Item: RO Tapware
note | Test:
note | RO Water flow
note | Test for:
note | Leaks
checkpoint | Item: Scrub Troughs
note | Scrub trough Installed as per KOP and RLS elevations
note | Scrub trough installed level
note | Mounted brackets secured as per manufactureres instructions
checkpoint | Item: Sensor Taps
note | Test:
note | Sensor operates as per manufactures requirements
note | Flow of water from tap
checkpoint | Other
checklist | QA 29 Periodic Flushing / Copper Protection Test Sheet |  |  |  | QA 29 Periodic Flushing / Copper Protection Test Sheet | 32350b03-9f6e-4691-8ead-18c45fd79da6
checkpoint | ITP QA 29 Periodic Flushing / Copper Protection Test Sheet
note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
checkpoint | Flushing Details:
textbox | Level / building being flushed:
radio | Time and Type of flushing: | Ring main –Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains – Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehau do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
textbox | Start time of flushing:
textbox | Zone/branch to be flushed:
textbox | Finish time of flushing:
textbox | Zone/branch to be flushed:
checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
checkpoint | Have you set a reminder for the next flushing of this pipework?
checkpoint | Have the hot and cold been interconnected for flushing purposes?
checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
textbox | Date for next flushing:
textbox | Test completed by:
textbox | Builder Representative:
checklist | Non-Conformance and Rectification Report |  |  |  | QA 9 - Non-Conformance and Rectification Report | 32a94ffc-ae7e-4ee5-b276-25d170edea21
checkpoint | Non-Conformance and Rectification Report Details:
textbox | Drawing No./Rev:
textbox | Zone or Grid:
textbox | Issued To:
textbox | Item Not Conforming
textbox | Reason For Non-Conformance
textbox | Consequences: Impact On Time, Cost Co-Ordination Etc
textbox | Action Required:
textbox | Date:
textbox | Rectification:
textbox | Date:
note | Note: Non-conformance register to be updated
checklist | Hot Water Service Maintenance Log |  |  |  | QA 31 - Hot Water Service Maintenance Log | 36636d75-f633-4191-acc4-a0aa000a57c6
checkpoint | Hot Water Service Unit Details
textbox | Purchased from:
textbox | Make:
textbox | Model No.:
textbox | Location:
textbox | Room Designation:
textbox | Installed by:
textbox | Installation Date:
textbox | Number of units in series:
textbox | Prescribed temperature set on unit or combined package:
checkpoint | Does installation comply with manufacturer’s instructions
checkpoint | Does installation comply with current requirements of the local water supply authority
checkpoint | Clean Pump Strainers
checkpoint | Clean Hot Water inlet Strainer
checkpoint | Clean Hot Water Return Strainer
checkpoint | Confirm all Valve Isolation reinstatement
checkpoint | Confirm Unit is Operational
checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
checkpoint | Commissioned By:
textbox | Name:
textbox | Date:
checklist | QA 8F Grease trap / pits checklist V.090421 |  |  |  | QA 8F - Grease trap / pits checklist V.090421 | 3a674b96-de9c-4344-b8c7-da7036742ba5
checkpoint | Set out of pits.
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
checkpoint | Bedding placement and compaction and material meets specification.
checkpoint | Laying and jointing of pipes R.Ls and falls
checkpoint | Connections to pits.
checkpoint | Baffle is in place.
checkpoint | Penetrations are patched and made watertight.
checkpoint | Suction line is installed as per spec.
checkpoint | Outlet pipework is installed as per spec.
checkpoint | Vents are connected and terminated to comply with Authority and Specification.
checkpoint | As built information updated onto drawings
checklist | QA 6D - Quality Control Gas Regulation Test Report |  |  |  | QA 6D - Quality Control Gas Regulation Test Report | 3af5c567-6575-42b2-ae9b-cc5a86d60912
checkpoint | Quality Control Gas Regulation Test Report:
textbox | Drawing No.
textbox | Rev:
checkpoint | Test - Flowing inlet pressure to project
textbox | Inlet Pipe and Size:
textbox | Spring range:
textbox | Orifice Size:
textbox | Model:
checkpoint | Section
textbox | Section:
textbox | Pressure (KPA)
checkpoint | Test upstream inlet pressure to regulation
textbox | Pressure (KPA)
checkpoint | Test downstream out pressure to regulation
textbox | Pressure (KPA)
textbox | Duration (hrs)
checkpoint | Adjust out pressure KPA as stated on GPL shop drawings
textbox | Reading (KPA)
checkpoint | Confirm outlet KPA does not fluctuate more than 0.8KPA
textbox | Repeat:
checkpoint | Sign Off
textbox | Geschke Pty Ltd. Representative:
textbox | Others Present:
textbox | Date of Satisfactory Completion:
checklist | QA 8C ITP Water Inground Inspection Report V.090421 |  |  |  | QA 8C ITP Water Inground Inspection Report V.090421 | 43b816e9-60a7-4264-a632-1feb35dfb0e3
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented/attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure water service pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Visual Inspection for copper brazed jointing
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Electro Fusion Welding Record QA16
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document & Bolt tightening to be completed using the correct sequence
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are watertight up to 1,500KPA for 2hrs | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Construction Company Representative Sign Off
signoff | Request Sign Off
checklist | QA 24 - Hose Reel Register |  |  |  | QA 24 - Hose Reel Register | 452da46d-17f0-43f3-b3d7-67e6ca263d58
checkpoint | Hose Reel Register
textbox | Ref No:
textbox | Building:
textbox | Zone:
textbox | Level:
textbox | Adjacent to:
textbox | Length:
textbox | Date Tested:
textbox | Flow Rate:
button | Obstructed Access | No,Yes
button | Operating instruction visible and legible | No,Yes
button | No leaks throughout hose reel mechanism | No,Yes
button | Hose runs freely through guides | No,Yes
button | No signs of corrosion | No,Yes
checkpoint | Result (Pass / Fail)
checklist | Below Ground Pipework Checklist - Fire |  |  |  | QA 8 - Below Ground Pipework Checklist - Fire (July 2020) | 46f432c5-51c8-4f59-ab11-416d760a8ed2
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of pits depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented - Attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure fire service pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are watertight up to 1,500KPA for 2hrs | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | Grease Trap Checklist |  |  |  | QA 8A - Grease Trap Checklist | 4e973c29-ecb7-4224-8145-d8a30d031a22
checkpoint | Set out of pits.
checkpoint | Pipes and fittings comply with relevant Authority and Specification.
checkpoint | Bedding placement and compaction and material meets specification.
checkpoint | Laying and jointing of pipes R.L’s and falls
checkpoint | Connections to pits.
checkpoint | Baffle is in place.
checkpoint | Penetrations are patched and made watertight.
checkpoint | Suction line is installed as per spec.
checkpoint | Outlet pipework is installed as per spec.
checkpoint | Vents are connected and terminated to comply with Authority and Specification.
checkpoint | As built information updated onto drawings
checklist | Hot Water Service Maintenance Log |  |  |  | QA 22 - Hot Water Service Maintenance Log | 4f3f0595-7666-4ed7-950c-758df4bd55df
checkpoint | Hot Water Service Unit Details
textbox | Purchased from:
textbox | Make:
textbox | Model No.:
textbox | Location:
textbox | Room Designation:
textbox | Installed by:
textbox | Installation Date:
textbox | Number of units in series:
textbox | Prescribed temperature set on unit or combined package:
checkpoint | Does installation comply with manufacturer’s instructions
checkpoint | Does installation comply with current requirements of the local water supply authority
checkpoint | Clean Pump Strainers
checkpoint | Clean Hot Water inlet Strainer
checkpoint | Clean Hot Water Return Strainer
checkpoint | Confirm all Valve Isolation reinstatement
checkpoint | Confirm Unit is Operational
checkpoint | Confirm Unit is Back to Operational Temp with no leaks on Strainer seals
checkpoint | Commissioned By:
textbox | Name:
textbox | Date:
checklist | QA 16 - PE Electrofusion Welding - Field Operational Sheet |  |  |  | QA 16 - PE Electrofusion Welding - Field Operational Sheet | 530615d4-4881-4901-9882-caceab5d8ca0
checkpoint | Operator Details
textbox | Name
textbox | ID No.
textbox | Company
textbox | Address
checkpoint | Welding Machine Details
textbox | Manufacturer
textbox | Type/Model
textbox | Serial Number
textbox | Year Built
checkpoint | Actual Pipe Size
textbox | Type
textbox | Brand
textbox | En
textbox | OD
textbox | Ovality %
checkpoint | Fitting Data
textbox | Brand
textbox | Type (Coupling, Tee, Reducer etc.)
checkpoint | Unit Setting
textbox | Manual
textbox | Automatic
checkpoint | Preparation
textbox | Cleaned and Peeled
textbox | Pipe/Fitting Clamped
checkpoint | Welding Times
textbox | Joining Seconds
textbox | Cooling Minutes
checkpoint | Conditions
textbox | Ambient Temp
textbox | Weather
textbox | Preventive Measures
checkpoint | Power
textbox | Mains
textbox | Gen Set
checkpoint | Operator Sign Off
checklist | QA 8E ITP Sewer Inground Inspection Report V.090421 |  |  |  | QA 8E ITP Sewer Inground Inspection Report V.090421 | 54fb6d73-a398-447b-89fa-aff6fbf9dbb4
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of pits depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented/attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Specification/Standard - Document to confirm coarseness & river-sand particle
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure fire service pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are airtight with the air test to show compliance | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Hold Point (Click to Attach below)
tickbox | JH Hold Point (Click to Attach/Request below)
tickbox | AECOM Hold Point (Click to Attach/Request below)
tickbox | Independent Certifier Hold Point (Click to Attach/Request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | VHH - Water Protection - |  |  |  | VHH - Water Protection ITP (V.090421) | 550fcd0f-a188-4cd1-8a9c-ac9ea191ce64
section | Part 1 - VHH Periodic Flushing / Copper Protection Test Sheet
checkpoint | ITP details
note | Copper systems are failing in the construction industry due to issues relating to design, water quality, the management of water during construction, long term maintenance of buildings with issues arising from building management team not following protocols outlined at hand over. Stagnant water being left in both hot and cold copper pipelines have been deemed to have been a contributing factor to recent copper failures. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water
note | Geschke Plumbing in consultation with John Holland & AECOM have put forward a proposal of periodic flushing of the systems during construction to mitigate the stagnant water issues that have arisen in the construction industry. The purpose of this ITP is to help create a strategy to ensure water is flowing through the piping system and flushed at nominated locations
note | Plans to flush to be submitted to John Holland prior to any flushing occurring on site
checkpoint | Flushing Details (Flushing to be Completed with Water ONLY)
textbox | Level being flushed
note | Stage of Flushing During the Project
tickbox | 1. Initial flush after installation of pipework and prior to Quality Control Pressure Test Report (Geschke QA 6)
tickbox | 2. Final flush post disinfection
tickbox | 3. Periodic flushing during construction (to be completed every 4 weeks – in line with AS 4809 clause 6.2.9)
tickbox | 4. Periodic flushing from final flush until PC (to be completed every 4 weeks – in line with AS 4809 clause 6.2.9)
checkpoint | Time & Type of Flushing (As per reference table below)
tickbox | 5. Ring main –Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush
tickbox | 6. Non ring mains – Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)
tickbox | 7. Short branches of copper that feed rehau do not need individual flushing
checkpoint | Which fixtures are being used to flush the system (Point of Connection & Point of Discharge)
note | Fixture 1
textbox | Start time of flushing
textbox | Zone/branch to be flushed
textbox | Finish time of flushing
textbox | Zone/branch to be flushed
note | .. ..
note | Fixture 2
textbox | Start time of flushing
textbox | Zone/branch to be flushed
textbox | Finish time of flushing
textbox | Zone/branch to be flushed
note | .. ..
note | Fixture 3
textbox | Start time of flushing
textbox | Zone/branch to be flushed
textbox | Finish time of flushing
textbox | Zone/branch to be flushed
note | .. ..
note | Fixture 4
textbox | Start time of flushing
textbox | Zone/branch to be flushed
textbox | Finish time of flushing
textbox | Zone/branch to be flushed
note | .. ..
note | Fixture 5
textbox | Start time of flushing
textbox | Zone/branch to be flushed
textbox | Finish time of flushing
textbox | Zone/branch to be flushed
note | .. ..
checkpoint | Sign-Off - Pass once entered
note | Add comments/photos below as applicable
button | a. Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated | Yes, No
button | b. Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case | Yes, No
button | c. Have you set a reminder for the next flushing of this pipework | Yes, No
textbox | Test completed by
textbox | Date for next flushing (Flushing to be performed every 4 weeks at a minimum)
signoff | Click to add Builders Signature(s)
checkpoint | Reference Table
note | 25mm Pipe / 0.49 (L/m) / Flush for 0.15 (Mins)
note | 32mm Pipe / 0.80 (L/m) / Flush for 0.25 (Mins)
note | 40mm Pipe / 1.26 (L/m) / Flush for 0.39 (Mins)
note | 50mm Pipe / 1.96 (L/m) / Flush for 0.61 (Mins)
note | 65mm Pipe / 3.32 (L/m) / Flush for 1.04 (Mins)
note | 80mm Pipe / 5.02 (L/m) / Flush for 1.57 (Mins)
note | 100mm Pipe / 7.85 (L/m) / Flush for 2.46 (Mins)
note | 150mm Pipe / 17.66 (L/m) / Flush for 5.53 (Mins)
note | NOTE: The table flushing time is based on 100 metres of pipework discharging through 16mm nozzle at 350KPa
section | Part 2 - Water Quality Testing Frequency
checkpoint | Water Quality Testing Details
note | Stage of water quality testing during the project
tickbox | 1. Periodic water quality testing during construction (to be completed every 3 months)
tickbox | 2. Water quality testing post final flush
checkpoint | Sign-Off - Pass once entered
note | Add comments/photos below as applicable
button | a. Geschke and John Holland management informed of sample / testing | Yes, No
button | b. Has the schematic / location of the sample collection been highlighted, attached, and nominated | Yes, No
button | c. Sample captured as per laboratory requirements | Yes, No
button | d. Time and date of sample recorded | Yes, No
textbox | Time of Sample
textbox | Date of Sample
textbox | Location of Sample
note | .. ..
textbox | Sample collected by
textbox | Date for next Water Quality Sample (Water quality testing to be performed every 3 months at a minimum during construction)
signoff | Click to add Builders Signature(s)
section | Part 3 - Disinfection of Pipework & Tank
checkpoint | Disinfection Checks - Pass once below completed
note | Add comments/photos below as applicable
button | a. Geschke and John Holland management informed of disinfection with plan provided | Yes, No
button | b. Has disinfection occurred for 6 hours as per AS/NZS 3500.1 appendix I | Yes, No
button | c. Time and date of disinfection | Yes, No
button | d. Flush all levels and branches until chlorination levels have reached safe chlorine levels as per Australian drinking water guidelines. | Yes, No
textbox | Time of Disinfection
textbox | Date of Disinfection
note | .. ..
textbox | Disinfection Completed by
signoff | Click to add Builders Signature(s)
checklist | Fire Penetration: |  |  |  | Add Fire Penetration Checklist | 5ee65cec-a1de-4742-8cf6-812fd695a969
checkpoint | Treatment Type
dropdown | Treatment Type: | 40Ø (HDPE - S),50Ø (HDPE -S),63Ø (HDPE-S),110Ø (HDPE-S),160Ø (HDPE-S),40Ø (PVC-DP),50Ø (PVC-DP),65Ø (PVC -DP),100Ø (PVC-DP),150Ø (PVC-DP),40Ø (PVC-S),50Ø (PVC-S),65Ø (PVC -S),100Ø (PVC-S),150Ø (PVC-S),80Ø (FWG-PVC-S),100Ø (FWG-PVC-S),110Ø (FWG-HDPE-S),32Ø CU,50Ø CU,100Ø CU,150Ø CU,100Ø (CIP-S),100Ø (RWO-DP),150Ø (RWO-DP)
checkpoint | Photo of penetration and sticker must be taken
textbox | Installed by:
textbox | Comments / Reasons why cannot complete:
checklist | Backflow Prevention Device Test Report |  |  |  | QA 13 - Backflow Prevention Device Test Report | 623e787e-99c3-49d2-964c-a301dd52efa3
checkpoint | Backflow Prevention Device Test Report Details:
textbox | Owner/Occupier:
textbox | Address:
note | Licence: 50043
radio | Type of Test: | Annual Test,Installation Test
textbox | Location of Device:
textbox | Authorized Tester Name:
textbox | Test Kit Serial No.
textbox | Tester Licence No.:
textbox | Test Kit Calibration Date:
textbox | Date of Test:
checkpoint | Device Details and Test Results
button | Permission to Isolate Water Supply | No,Yes
note | Device:
textbox | Make:
textbox | Size: |  |  | mm
textbox | Model No.:
textbox | Serial No.:
button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
tickbox | Containment Protection
tickbox | Individual Protection
tickbox | Zone Protection
button | Strainer Installed | No,Yes
button | Strainer Cleaned | No,Yes
radio | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
note | Valve
textbox | Check Valve 1
textbox | Check Valve 2
textbox | Relief Valve
note | Testing Results
textbox | Close tight at: |  |  | kpa (min 35kpa)
tickbox | Leaked
textbox | Close tight at: |  |  | kpa (min 7kpa)
tickbox | Leaked
textbox | Opened at: |  |  | kpa (min 14kpa)
tickbox | Leaked
note | Reason for the device failure
tickbox | Incorrect position
tickbox | Incorrect installation
tickbox | Foreign material in the device
tickbox | Spring wear damage
tickbox | Seal or Rubber Damage
tickbox | Other
textbox | Other:
note | Test after maintenance
textbox | Close tight at: |  |  | kpa (min 35kpa)
tickbox | Leaked
textbox | Close tight at: |  |  | kpa (min 7kpa)
tickbox | Leaked
textbox | Opened at: |  |  | kpa (min 14kpa)
tickbox | Leaked
button | Water turned back on | No,Yes
textbox | Describe the maintenance:
textbox | Parts used in repair:
button | Is the device installed correctly | No,Yes
checkpoint | Test Result
textbox | Tester Name:
textbox | Date:
signoff | Add Signature
checklist | Water Meter Accuracy Test |  |  |  | QA 17 - Water Meter Accuracy Test | 6a85fbcf-f3a5-4a88-8a07-a4cad1498cf1
checkpoint | Water Meter Accuracy Test Details:
textbox | Date:
textbox | Project:
textbox | Location of Water Meter:
textbox | ID Number of Water Meter:
textbox | Model & Manufacturer:
textbox | Current Counter Reading:
textbox | Zone/Appliances to be Metered:
textbox | Pulse Rate:
checkpoint | Measurement Apparatus
tickbox | Container
textbox | Measured Container Size:
tickbox | Water Meter
textbox | Calibrated Date:
textbox | Other
checkpoint | Measurement Method
note | Isolate all fixings
note | Place Measured Container at outlet of fixture and fill
note | Fill in completed counter reading and minus "current reading" to measure accuracy
textbox | Completed Counter Reading:
note | Accuracy
textbox | OK
textbox | FAILED
note | Replace Counter and Re-Test
textbox | OK
textbox | FAILED
checkpoint | Sign Off
textbox | Name - Geschke Representative
signoff | Signature - Geschke Representative
checklist | Boiling Water Service Maintenance Log |  |  |  | QA 23 - Boiling Water Service Maintenance Log | 6be24100-97b2-4aed-b9de-59b598874c6d
checkpoint | Boiling Water Unit Service Details
textbox | Purchased from:
textbox | Make:
textbox | Model No.:
textbox | Location:
textbox | Room Designation:
textbox | Installed by:
textbox | Installation Date:
checkpoint | Does installation comply with manufacturer’s instructions
checkpoint | Does the installation appear in good working order.
checkpoint | Confirm all warning lights working correctly
checkpoint | Confirm filter is clean
checkpoint | Confirm Unit is Fully Operational
checkpoint | Commissioned By:
textbox | Name:
textbox | Date:
checklist | TMV 12 Month Service Log (use a separate checklist for each valve) |  |  |  | TMV 12 Month Service Log V.040221 | 6ca83108-c1a7-4dab-91dd-82bf32b3cd7e
checkpoint | TMV 12 Month Service Log
textbox | Building name:
textbox | Contact person:
textbox | Address:
textbox | Phone number:
textbox | Make of valve:
textbox | Model number:
textbox | Valve location:
textbox | Room name:
textbox | Date of service:
textbox | Temperature: |  |  | °C
button | Element: | Ok, Faulty
button | O' rings: | Ok, U, S
button | Strainers: | Ok, Dirty
button | Non-return Valves | Ok, Faulty
button | Fail-safe test | Ok, Faulty
textbox | Serviced by:
note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
checkpoint | Completion
textbox | Plumber Name:
signoff | Add Signature
checklist | QA 6C - Quality Control Flow Test and Compliance Report - Safety Showers and Eyewash |  |  |  | QA 6C - Quality Control Flow Test and Compliance Report - Safety Showers and Eyewash | 6e800c85-b383-4b8e-b87a-5d6da6e48a09
checkpoint | QA 6C - Qaulity Control Flow Test and Compliance Report - Safety Showers and Eyewash:
textbox | Drawing nos/rev:
textbox | Appliance Tested:
textbox | Room No.:
checkpoint | Flow Rate and Pressure as per Australian Standard 4775
note | Safety Shower - The flow is to be at a minimum 75.7 litres/minute at 210KPa
note | Eyewash - The flow is to be at a minimum 1.5Litres/minute at 210KPa
textbox | Pressure: |  |  | KPA
textbox | Flow Rate: |  |  | LPS
checkpoint | Pipe Installed
textbox | Pressure set on each floor: KPA
textbox | Cold - Size: |  |  | mm
textbox | Capable Flow Rate: |  |  | LPS
checkpoint | Pull Lever Confirm Flow
checkpoint | Riser Valves Open
checkpoint | Safety Shower or Eye Wash Valve Open
checkpoint | Safety shower is installed between 2083mm and 2438mm
checkpoint | Spray pattern ensuring is at a minimum of 508mm in diameter at 1524mm above the surface
checkpoint | Sign Off
textbox | Name - Geschke Pty Ltd Representative
textbox | Others Present
textbox | Date of Completion of Satisfactory Test
checklist | QA 18 - Gasket Installation |  |  |  | QA 18 - Gasket Installation | 708890cb-3e10-4cf4-88c8-a350bf5c9d7c
checkpoint | Gasket Installtion:
textbox | Location/Identification:
textbox | Nominal Bolt Size:
textbox | Gasket Contact Surface Finish on Flange:
textbox | Lubricant used:
note | 1. Galvanised nuts and bolts – must use good quality lubricating oil on threads
note | 2. Below Ground Galvanised nuts and bolts– must denzo and plastic wrap full flange and cover bolts
note | 3. Stainless steel nuts and bolts – must use anti seize / molybond on threads – must return 24 hrs later to tighten in sequence and required torque
note | 4. Galvanised nuts and bolts on stainless steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
note | 5. Stainless Steel nuts and bolts on galvanised steel flanges / backing rings - Thinsulators (insulating top hats) or insulating washer with thin PE sleeve must be used, and complete flange must be denzo wrapped with plastic protection
note | 6. Zinc bolts, nuts and washers rust when used externally – use galvanised
checkpoint | Visually examine and clean flanges, bolts, nuts and washers. Replace components if necessary. Alignment of flange faces is very important and maintain support of the flange, pipework and valve at all times
checkpoint | Lubricate bolts, nuts AND flange surface AROUND BOLT HOLES, not on flange/gasket surface, or use hardened steel washers. Use anti-seize on stainless steel threads and nuts or on galvanised bolts and nuts lightly oil with good quality lubricating oil. Insert bolts in locations 1 to 4 as indicated in the below diagrams.
checkpoint | Install new gasket. DO NOT REUSE OLD GASKET, OR USE MULTIPLE GASKETS. Gaskets for water applications must be EPDM potable water gasket PN16 type. Gaskets for gas need to be AGA and GPL approved
checkpoint | Number bolts in cross-pattern sequence according to the appropriate sketch below with a marker pen, black or white
checkpoint | IMPORTANT! HAND TIGHTEN; then PRE-TIGHTEN BOLTS to 7Nm torque, but DO NOT EXCEED 20% of Target Torque. Target torque is required to be supplied by Gasket manufacturer / supplier – seek from GPL foreman
checkpoint | Check gap for uniformity.
checkpoint | Use the appropriate cross-pattern tightening sequence in the sketch below for Rounds 1,2 and 3 and/or Round 4 (each sequence constitutes a “Round”)
checkpoint | Final Torque
textbox | Final torque*: |  | (Nm)
note | * Refer to gasket manufacturer spec with torque chart on next page and GPL advice
note | Lubricate, Hand Tighten, Pre-Tighten bolts (5% of final torque) (as mentioned in item 5 above)
textbox | Round 1 – Tighten to: |  | (Nm) | 1st torque value in torque chart* (20% of final torque)
textbox | Round 2 – Tighten to: |  | (Nm) | 2nd torque value in torque chart* (50% of final torque)
textbox | Round 3 – Tighten to: |  | (Nm) | 3rd torque value in torque chart* (75% of final torque)
note | Check gap around the circumference between each of these rounds, measured at every other bolt. If the gap is not reasonably uniform around the circumference, make the appropriate adjustments be selective bolt tightening before proceeding.
note | Final Rotational Round – 100% of Final Torque (same as Round 3 or 4 above). Use ROTATIONAL, clockwise tightening sequence starting with Bolt No.1, for one complete round and continue by selective bolt tightening before proceeding.
note | Short-term bolt preload loss can occur between four to twenty-four hours after initial tightening due to bolt relaxation. Consider retightening to help recover this loss.
dropdown | Tightening Method Used: | Hydraulic Torque Wrench, Impact Wrench, Manual Torque Wrench, Other,Hand Wrench
textbox | Other:
textbox | Where was torque information provided from:
textbox | Joint Assembler Name:
signoff | Joint Assembler Signature
checklist | Below Ground Pipework Checklist - Sewer |  |  |  | QA 8 - Below Ground Pipework Checklist - Sewer (July 2020) | 733aa6e7-4390-451b-a588-ac5ef7921486
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of pits depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented/attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Specification/Standard - Document to confirm coarseness & river-sand particle
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure fire service pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are airtight with the air test to show compliance | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Hold Point (Click to Attach below)
tickbox | JH Hold Point (Click to Attach/Request below)
tickbox | AECOM Hold Point (Click to Attach/Request below)
tickbox | Independent Certifier Hold Point (Click to Attach/Request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | Below Ground Pipework Checklist - Water |  |  |  | QA 8 - Below Ground Pipework Checklist - Water (July 2020) | 7b9e0cfb-ddde-4eba-9c40-d55cde39d945
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented/attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure water service pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Visual Inspection for copper brazed jointing
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Electro Fusion Welding Record QA16
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document & Bolt tightening to be completed using the correct sequence
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are watertight up to 1,500KPA for 2hrs | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | Equipment Calibration Register |  |  |  | QA 11 - Equipment Calibration Register | 8a6f04da-bad2-4a6c-8c8e-7f6bdb622ab6
checkpoint | 1
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 2
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 3
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 4
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 5
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 6
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 7
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 8
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 9
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checkpoint | 10
textbox | Equipment Type:
textbox | Manufacturer:
textbox | Model and Type:
textbox | Serial No.:
textbox | Next Service Due:
checklist | Quality Control Pressure Test Report |  |  |  | QA 6 - Quality Control Pressure Test Report | 8d1bcd91-08a8-4015-8037-abf084c17427
checkpoint | Quality Control Pressure Test Report:
textbox | Drawing No
textbox | Rev
button | Test | Air,Water
textbox | Section
textbox | From
textbox | To
note | Specified System Working
textbox | Pressure (KPA)
textbox | Duration (HRS)
note | Specified System Test
textbox | Pressure (KPA)
textbox | Duration (HRS)
checkpoint | 1st Reading
textbox | Time
textbox | KPA
textbox | Ambient Temp
checkpoint | 2nd Reading
textbox | Time
textbox | KPA
textbox | Ambient Temp
checkpoint | Test Result
textbox | Repeat
checkpoint | Sign Off
textbox | Geschke Pty Ltd. Representative
textbox | Others Present
textbox | Date of Satisfactory Completion
checklist | Pre Cast Slab Penetration Placement Checklist |  |  |  | QA 15 - Pre Cast Slab Penetration Placement Checklist | 8ec51eeb-4dac-42a4-808a-e2fc01d900da
checkpoint | Pre Cast Slab Penetration Placement Details:
textbox | Drawing No. / Rev:
textbox | Slab No.
textbox | Total: Sewer - waste penetrations
textbox | Total: Stormwater penetrations
textbox | Total: Water
textbox | Other:
checkpoint | Geschke Representative Sign Off
signoff | Request Sign Off
checkpoint | Construction Company Representative Sign Off
signoff | Request Sign Off
checklist | QA 5B - Suspended Water Service Installation V.090421 |  |  |  | QA 5B - Suspended Water Service Installation V.090421 | 8f958ca0-cbb2-47d2-97f1-1519455de9b8
checkpoint | Installation Test Sheet:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | PIPE CLIP HANGERS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | MATERIAL AND SIZE
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | ALIGNMENT
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | noteLING AND IDENTIFICATION
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | JOINTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PENETRATION SEALING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | FIRE STOP COLLARS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | Seismic Bracing Installed - If Applicable
note | Reference design details below & take photos
textbox | Details
checkpoint | PRESSURE TESTING COMPLETED (QA6)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AUTHORITY INSPECTION (if applicable)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checklist | QA 14 Thermostatic Mixing Valve Commissioning V.090421 |  |  |  | QA 14 - Thermostatic Mixing Valve Commissioning V.090421 | 92a9a7aa-e18a-4b50-9556-fda865caa448
checkpoint | TMV Commissioning Log Sheet:
textbox | Building Name:
textbox | Contact Person:
textbox | Address:
textbox | Lic:
textbox | Registration number:
textbox | Phone number:
textbox | Make of valve:
textbox | Model number:
textbox | Valve location:
textbox | Room name:
textbox | Valve purchased from:
textbox | Installation date:
textbox | Valve installed by:
textbox | Number of outlets served - Baths:
textbox | Number of outlets served - Basins:
textbox | Number of outlets served - Showers:
textbox | Total number of mixing valves on site:
button | Does the installation comply with the manufacturer's/supplier's published installation instructions? | No, Yes
button | Does the installation comply with the current requirements of the local water supply authority? | No, Yes
textbox | Temperature of hot water supply?
textbox | Temperature of cold water supply?
textbox | Temperature of warm water delivery at outlet fitting?
textbox | Dynamic pressure of hot water:
textbox | Dynamic pressure of cold water:
checkpoint | Check fail safe operation (hot water at least 20c above warm water)
checkpoint | Commissioned by
textbox | Commissioned by:
textbox | Company name:
checklist | QA 9 Flushing V.090421 |  |  |  | QA 9 - Flushing V.090421 | 983d0581-e0bf-4b2d-aa5c-5f6cbb42e8d2
checkpoint | Periodic Flushing / Copper Protection Test Sheet
note | Copper systems are failing in the construction industry due to stagnate water being left in both hot and cold copper pipelines. Copper needs to form a protective layer of copper oxide on the internal surface which is formed by the contact with fresh aerated and oxygenated water. Periodic flushing of the systems is the only way to ensure this occurs.
note | The purpose of this ITP is to help you create the strategy to get this water out and replaced with fresh water every four weeks.
checkpoint | Flushing Details:
textbox | Level / building being flushed:
radio | Time and Type of flushing: | Ring main Single point for flushing; the entire loop can be achieved in a maximum 10-minute flush., Non ring mains Any copper sub-branch from the main feed requires individual flush time of 5 minutes (an example of this would be a corridor feed)., Short branches of copper that feed rehaul do not need individual flushing., Multi storey projects will require flushing on each level. Starting from the top and working your way down
textbox | Which fixtures are being used to flush the system (Point of connection and point of discharge):
textbox | Start time of flushing:
textbox | Zone/branch to be flushed:
textbox | Finish time of flushing:
textbox | Zone/branch to be flushed:
checkpoint | Has the schematic / layout of the flushed zone been highlighted, attached and flush points nominated.
checkpoint | Is the flushed water clear with no visible debris or dirt. If NO, discuss with project foreman and or head office on why this might be the case.
checkpoint | Have you set a reminder for the next flushing of this pipework?
checkpoint | Have the hot and cold been interconnected for flushing purposes?
checkpoint | Date for next flushing (Flushing to be performed every 4 weeks):
textbox | Date for next flushing:
textbox | Test completed by:
textbox | Builder Representative:
checklist | Installation Test Sheet (Waste, Vent, Downpipes etc) |  |  |  | QA 4 - Installation Test Sheet (Waste, Vent, Downpipes etc.) | 997c57ba-9d02-4ae5-af61-b603f0da76c0
checkpoint | Installation Test Sheet:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | PIPE CLIP HANGERS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | MATERIAL AND SIZE
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | ALIGNMENT
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | noteLING AND IDENTIFICATION
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | JOINTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PENETRATION SEALING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | FIRE STOP COLLARS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | TESTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AUTHORITY INSPECTION (if applicable)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checklist | QA 30 - Fixture/Hydraulic Installation (V.060921) |  |  |  | QA 30 - Fixture/Hydraulic Installation (V.060921) | 9cbb4370-4148-4469-946f-7f3233c784ce
checkpoint | What is being installed
tickbox | WC
tickbox | Shower
tickbox | Basin
tickbox | Sink
tickbox | Tapware
tickbox | RO Tapware
tickbox | Boiling Water Unit
tickbox | TMV Cover
tickbox | RPZD Cover
tickbox | Other (Specify below)
textbox | Other (Specify here)
checkpoint | Where is this fixture being installed
textbox | Location
checkpoint | Have all parts been connected/completed and tested - Pass=Yes / Fail=No (Detail why below)
checkpoint | Photos of installation taken and uploaded below
checklist | Butt Welding |  |  |  | QA 25 - Butt Welding Checklist | 9f4551a7-0ed0-4ff2-9a4f-2a09007c9eec
checkpoint | Operator Details:
textbox | Name:
textbox | Company:
textbox | Phone:
textbox | Address:
checkpoint | Welding Machine Details:
textbox | Manufacturer:
textbox | Type/Model:
textbox | Serial Number:
textbox | Year Built:
checkpoint | Pipe / Material Details:
textbox | Dn (OD)
textbox | SDR
textbox | En
textbox | Type
textbox | Parameter
textbox | SLP
textbox | SHP
checkpoint | 1
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 2
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 3
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 4
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 5
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 6
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 7
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 8
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 9
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 10
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 11
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 12
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 13
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 14
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 15
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checkpoint | 16
textbox | Time
textbox | Ambient °C
textbox | Heater Plate °C
textbox | Drag Pressure
textbox | Bead Up: P1 (Kpa/Bar)
textbox | Bead Up: t1 (Evidence)
textbox | Heat Soak: P2 (Kpa/Bar)
textbox | Heat Soak: t2 (Seconds)
textbox | Change Over: t3 (Seconds)
textbox | Pressure Up: t4* (Seconds)
note | *t4 not applicable for SHP situations
textbox | Weld and Cool: P3 (Kpa/Bar)
textbox | Weld and Cool: t5 (h:m)
textbox | Rough Handling: t6 (h:m)
textbox | Bead Size: Min
textbox | Bead Size: Max
textbox | Comments
signoff | Add Operator Signature
checklist | Installation Test Sheet (Cold Water, Hot Water & Flusher Line) |  |  |  | QA 5 - Installation Test Sheet (Cold Water, Hot Water & Flusher Line) | a382310a-5b1f-4709-95fa-8eefffbefab6
checkpoint | Installation Test Sheet:
textbox | Drawing No.:
textbox | Rev.:
checkpoint | PIPE CLIP HANGERS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | MATERIAL AND SIZE
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | ALIGNMENT
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | noteLING AND IDENTIFICATION
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | JOINTING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PENETRATION SEALING
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | FIRE STOP COLLARS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | PRESSURE TESTING COMPLTED (QA6)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AUTHORITY INSPECTION (if applicable)
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
textbox | Details:
textbox | Tester:
textbox | Date:
textbox | Notes:
checklist | TMV 12 Month Service Log |  |  |  | Safety Showers - TMV 12 Month Service Log V.040221 | a512a8bc-3021-4a67-a72e-23a6cebb67c7
checkpoint | TMV 12 Month Service Log
textbox | Building name:
textbox | Contact person:
textbox | Address:
textbox | Phone number:
textbox | Make of valve:
textbox | Model number:
textbox | Valve location:
textbox | Room name:
textbox | Date of service:
button | Element: | Ok, Faulty
button | O' rings: | Ok, U, S
button | Strainers: | Ok, Dirty
button | Non-return Valves | Ok, Faulty
button | Fail-safe test | Ok, Faulty
textbox | Serviced by:
note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
textbox | Temperature |  |  | °C
checkpoint | Completion
textbox | Plumber Name:
signoff | Add Signature
checklist | Backflow Prevention Device Test Report |  |  |  | Backflow Prevention Device Test Report | aff3105b-a6b7-4046-8ebc-9fa8b0b2fd13
checkpoint | Backflow Prevention Device Test Report Details:
note | Owner/Occupier: Victorian Heart Hospital
note | Address: 631 Blackburn Road, CLAYTON
textbox | Licence: 50043
dropdown | Type of Test: | Annual Test,Installation Test
textbox | Location of Device:
dropdown | Authorized Tester Name: | Tom,Glenn,Other (specify below)
textbox | Other (specify)
dropdown | Test Kit Serial No. | E4396-3-1,27946-1121,other (specify below)
textbox | Other (specify)
dropdown | Tester Licence No. | 106121,32503,other (specify below)
textbox | Other (specify)
textbox | Test Kit Calibration Date:
textbox | Date of Test:
checkpoint | Device Details and Test Results
button | Permission to Isolate Water Supply | No,Yes
textbox | Device:
note | Make (Watts):
textbox | Size: |  |  | mm
note | Model No.: 009M2QT
textbox | Serial No.:
button | Is the device installed high enough to prevent ingress of any possible contaminated water? | No,Yes
tickbox | Containment Protection
tickbox | Individual Protection
tickbox | Zone Protection
button | Strainer Installed | No,Yes
button | Strainer Cleaned | No,Yes
dropdown | Device Type | Double Check Valve,RPZD (Reduced Pressure Zone Device)
textbox | Valve
textbox | Check Valve 1
textbox | Check Valve 2
textbox | Relief Valve
textbox | Testing Results
textbox | Close tight at: |  |  | kpa (min 35kpa)
tickbox | Leaked
textbox | Close tight at: |  |  | kpa (min 7kpa)
tickbox | Leaked
textbox | Opened at: |  |  | kpa (min 14kpa)
tickbox | Leaked
textbox | Reason for the device failure
tickbox | Incorrect position
tickbox | Incorrect installation
tickbox | Foreign material in the device
tickbox | Spring wear damage
tickbox | Seal or Rubber Damage
tickbox | Other
textbox | Other:
textbox | Test after maintenance
textbox | Close tight at: |  |  | kpa (min 35kpa)
tickbox | Leaked
textbox | Close tight at: |  |  | kpa (min 7kpa)
tickbox | Leaked
textbox | Opened at: |  |  | kpa (min 14kpa)
tickbox | Leaked
button | Water turned back on | No,Yes
textbox | Describe the maintenance:
textbox | Parts used in repair:
button | Is the device installed correctly | No,Yes
checkpoint | Test Result
textbox | Tester Name:
textbox | Date:
signoff | Add Signature
checklist | VHH - Wall Rough-In Setout ITP (V.260321) |  |  |  | VHH - Wall Rough-In Setout ITP (V.260321) | c5837ee4-5cce-43a0-b52f-fad16f3ab7cf
checkpoint | Approved Drawing Number (FFE & RLS)
textbox | Drawing & Revision Number
checkpoint | Has setout been marked out on the floor
signoff | Click to add Builders Signature(s)
checklist | Rough-In ITP - VHH (V.070521) |  |  |  | Rough-In ITP - VHH (V.070521) | ced49076-74d5-4046-9f35-14ee2a15d0c2
checkpoint | Level of Rough In Installation
checkpoint | Room of Rough In Installation
checkpoint | Setout as per the following documentation
button | RLS Drawings | Yes, No, N/A
button | FFE Drawings | Yes, No, N/A
button | KOP Drawings | Yes, No, N/A
checkpoint | TMV Type Installed - Pass once confirmed
button | Type | Clinical, Non-Clinical
checkpoint | Waste Installed
checkpoint | Vent Installed
checkpoint | Penetration sealed
checkpoint | Pipe work Clipped
checkpoint | Setout as per RLS and FFE
checkpoint | Cross connection check / jointing
button | Hot Water Pipes | Yes, No, N/A
button | Cold Water Pipes | Yes, No, N/A
button | Temporary Water | Yes, No, N/A
checkpoint | Nogging installed as per set out
button | Extra nogging installed for basin | Yes, No, N/A
checkpoint | L / E Installed
checkpoint | Shower installed
checkpoint | Water Pressure Test completed
note | Attached below for reference - If Applicable
checkpoint | Rough-In works completed to specification/drawings - Area left clean & tidy
note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
checklist | QA 8D ITP Fire Inground Inspection Report V.090421 |  |  |  | QA 8D - ITP Fire Inground Inspection Report V.090421 | d264a846-0041-4e44-a4d6-031709ed8475
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of pits depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented - Attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure fire service pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are watertight up to 1,500KPA for 2hrs | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | Below Ground Pipework Checklist - Gas |  |  |  | QA 8 - Below Ground Pipework Checklist - Gas (July 2020) | de0174f1-d2a9-415a-aedf-17a9a13c07cb
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented/attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Records - Copper trace wire with tape
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Acceptance Criteria (As per below)
button | Haunching holding pipe straight & true | Yes, No, N/A
button | Ensure GAS pipe is laid out in accordance with the construction drawings & quality of work is up to standard | Yes, No, N/A
button | Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates | Yes, No, N/A
tickbox | Inspection by GPL Representative prior to backfill - Look up pipe to ensure installation completed to a satisfactory standard
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Check below ground pipework - pipe joints
note | Test - Fill in QA sheets for butt welds or electrofusion welds
note | Visual Inspection for copper brazed jointing
note | Fill in sheet for PE welds. Visual inspection on all welds
note | Records - Electro Fusion Welding Record QA16
note | Records - Butt welding Record QA 25
note | Australian Standards
note | Acceptance Criteria - Weld to have been completed via GPL QA Document & Bolt tightening to be completed using the correct sequence
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Connections to pits & existing services as per spec & Australian Standards
note | Inspected Upon Installation
note | Records - Installation Photographs (Attached below)
tickbox | GPL Site Representative to undertake Visual Inspection
checkpoint | Check below ground pipework - Hydrostatic pressure testing
note | Test - Standard Hydrostatic Pressure Test
note | Inspected Upon Installation
note | Records - Standard Pressure Test Certificate QA.6
note | Acceptance Criteria (As per below)
button | Pipeline & joints are air tight with the tested system tested with 1.5times the working pressure | Yes, No, N/A
button | Pipeline is flushed free of debris | Yes, No, N/A
button | Air Pressure test completed (Attached below if Applicable) | Yes, No, N/A
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checkpoint | Placement & compaction of backfill & material meets specification
note | Approval by GPL
note | Stage - This is not signed off based on duration, It will be signed off with the highlighted mark-up detailing what this ITP covers. This will be at the discretion of Site Foreman
note | Records - Compaction to meet specification requirements
note | Acceptance Criteria - Compaction in layers with mechanical compaction equipment, E.g. Wacker Packer (jumping jacks) & DPU vibrating plates
tickbox | GPL Site Representative to Document & Review (Attach below if Applicable)
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | As-Built information updated onto drawings
note | Approval by GPL
note | Stage - Upon Completion & then Ongoing
note | Records - ASBUILTS
tickbox | GPL Site Representative to Document & Review. NB- Works to use approved shop drawings only
checkpoint | Overall ITP Sign-Off
tickbox | GPL Sign-off Completed (Click to attach below)
tickbox | JH Sign-off Completed (Click to attach/request below)
tickbox | AECOM Sign-off Completed (Click to attach/request below)
signoff | Click to Add Signature or Request Sign-off
checklist | TMV Routine Service Log Sheet |  |  |  | TMV Routine Service Log Sheet V.040221 | df574e4c-282a-4a8a-adf1-0630d21e73be
checkpoint | TMV Routine Service Log Sheet:
textbox | Building name:
textbox | Contact Person:
textbox | Address:
textbox | Phone number:
textbox | Make of valve:
textbox | Model number:
textbox | Valve location:
textbox | Room name:
textbox | Date of service:
textbox | Outlet water temperature:
button | Outlets flushed for 15 seconds | Yes, No
button | Shower heads disinfected | Yes, No
textbox | Serviced By:
checkpoint | Recommended Service Periods
note | Outlet water temperature = Fortnightly
note | Flushing of outlets = Weekly
note | Disinfect shower heads = Monthly
checkpoint | Completed by:
textbox | Plumber Name:
signoff | Add Signature
checklist | Service Cross Connection Check List Report |  |  |  | QA 19 - Service Cross Connection Check List Report | dfbe2ce8-3cae-4315-a2b6-8387844a21cc
checkpoint | Service Cross Connection Check List Report Details:
textbox | Zone/Grid:
textbox | Drawing No.:
textbox | Rev:
checkpoint | Service to be tested
note | Isolation of potable supply in general.
checkpoint | Potable Water Supply
note | Confirmation of service isolation at all fixtures.
note | Keep potable water turned off.
checkpoint | Non Potable Supply
note | Confirmation of water flow for non potable water supply at each non potable fixture while potable is still isolated.
checkpoint | Turn potable back on
note | Potable back on
checkpoint | Non potable supply
note | Isolate non potable water flow and prove that each non potable fixture has no water flow.
checkpoint | Potable Supply
note | Check all fixtures that receive potable water are still getting potable water.
checkpoint | Pipe Identification
note | Confirm recycled water piping is identified by colour and noteling.
checkpoint | Other
checklist | TMV 12 Month Service Log (use a separate checklist for each valve) |  |  |  | zSYS - TMV 12 Month Service Log V.040221 (old version) | e25a3a62-1980-4c09-976e-9766e28e0ad8
checkpoint | TMV 12 Month Service Log
textbox | Building name:
textbox | Contact person:
textbox | Address:
textbox | Phone number:
textbox | Make of valve:
textbox | Model number:
textbox | Valve location:
textbox | Room name:
textbox | Date of service:
button | Element: | Ok, Faulty
button | O' rings: | Ok, U, S
button | Strainers: | Ok, Dirty
button | Non-return Valves | Ok, Faulty
button | Fail-safe test | Ok, Faulty
textbox | Serviced by:
note | Note: It is recommended that a new thermostatic element should be fitted at least every 5 years
checkpoint | Completion
textbox | Plumber Name:
signoff | Add Signature
checklist | QA-5A,/F/G/J/K Suspended Services Installation ITP V.250221 |  |  |  | QA-5A,/F/G/J/K Suspended Services Installation ITP V.250221 | e4f642ad-746b-49e7-b57c-4b9053ae9368
checkpoint | Installation Test Sheet
textbox | Drawing & Revision No
checkpoint | PIPE CLIP HANGERS
note | Attach comments/photos of install below
textbox | Details
checkpoint | MATERIAL AND SIZE
note | Attach comments/photos of install below
textbox | Details
checkpoint | ALIGNMENT
note | Attach comments/photos of install below
textbox | Details
checkpoint | noteLING AND IDENTIFICATION
note | Attach comments/photos of install below
textbox | Details
checkpoint | JOINTING
note | Attach comments/photos of install below
textbox | Details
checkpoint | PENETRATION SEALING
note | Attach comments/photos of install below
textbox | Details
checkpoint | FIRE STOP COLLARS
note | Attach comments/photos of install below
textbox | Details
checkpoint | Seismic Bracing Installed - If Applicable
note | Reference design details below & take photos
textbox | Details
checkpoint | TESTING
note | Passing above indicates that Testing ITP's have been completed in Testing folder
note | Attach comments/photos below
textbox | Details
textbox | Tester Information
textbox | Date of Test
checkpoint | Installers Details - Pass once entered
textbox | Name
textbox | Date(s) of Install
checkpoint | AUTHORITY INSPECTION (if applicable)
note | Attach comments/photos below
textbox | Details
textbox | Inspector
textbox | Date
button | Report attached or referenced below | Yes, No, N/A
signoff | Click to Add Inspectors Signature - If Required
checkpoint | AS BUILT INFORMATION UPDATED ONTO DRAWINGS
textbox | Details
button | Asbuilts attached or referenced below | Yes, No, N/A
checklist | QA 8A ITP Gas Inground Inspection Report V.090421 |  |  |  | QA 8A - ITP Gas Inground Inspection Report V.090421 | e91c65cd-acfc-4e71-a622-fb6e662be50f
checkpoint | Approved Drawing Number/Area of Works
textbox | Drawing & Revision Number
textbox | Area of Work
checkpoint | Check set out of depths & trench runs
note | Approval by GPL
note | Checked Prior to Commencement
note | Acceptance - Set-out marked with pegs & alignment matches approved drawings
tickbox | Visual inspection undertaken by GPL Representative & Documented/attached below
button | GPL Witness Point | Yes, No, N/A
button | JH Witness Point | Yes, No, N/A
checkpoint | Pipes & fittings comply with relevant Authority & Specification
note | Records - Specification/Approvals
button | Approved by GPL Site Representative | Yes, No, N/A
checkpoint | Bedding Placement & Backfill
note | Approval by GPL
note | Records - Copper trace wire with tape
checklist | Project Photos |  |  |  | Add Project Photos | f4ec78ba-78c6-46a9-8205-f960d935c472
checkpoint | Attach Photos and Comments
checklist | Fire Hose Reel (FHR) Test Report |  |  |  | QA 20 - Fire Hose Reel (FHR) Test Report | f5bb1f9d-5da2-4b46-972e-c708ca7874ff
checkpoint | Fire Hose Reel (FHR) Test Report:
textbox | Location of FHR:
textbox | ID Number of FHR (If applicable):
textbox | Manufacturer:
textbox | Model:
textbox | Size:
note | Aust. Standard Flow Rate: 0.33 LPS @ 210-230 KPA
radio | Measurement Apparatus: | Bucket
textbox | Bucket Size:
note | Measurement Method:
note | 1. Connect pressure gauge and outlet to end of hose
note | 2. Note static pressure reading on gauge
note | 3. Place bucket at outlet of FHR and fill
checkpoint | Reading
note | 3.3L
textbox | TIME (sec)
textbox | Flow Pressure:
note | 6.6L
textbox | TIME (sec)
textbox | Flow Pressure:
note | 9.9L
textbox | TIME (sec)
textbox | Flow Pressure:
checkpoint | Completion
textbox | Geschke Pty Ltd. Representative:
textbox | Others Present:
textbox | Date of Completion of Satisfactory Test: