## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | Seacliff Wastewater Treatment and Disposal Upgrade |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561469 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | CM | Construction Manager
Contract Number: | 9776 |  |  |  |  | C | Check | CR | Cust. Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 3 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Chambers etc |  |  |  |  | I | Inspection | PM | Project Manager
Discipline: | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | Seacliff Watewater Treatment Plant Upgrade |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | 310103025-01-001-C101 to C112 and C120 to C125 |  |  |  |  | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Calisa Mcleary |  | Date: | 2023-11-03 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
3.1 | Review all Drawings and Documents | Review all drawings and documentation provided to the Contractor. | Prior to the commencement of Works it must be ensure that all necessary documentation has been provided. | ITP | Prior to the commencement of Works | Visual | R | PM/QE
3.2 | Setting Out Levels and position | All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4 | Levels and position Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer | Compliance surveys or spot checks | Prior to the commencement of Works | Visual, Instrumental | H | SP/QE/SV
3.10 | Concrete Manhole, Catchpits and Access Chambers | Precast concrete estructures shall comply with NZS 3106. Specs 1131: 14.5 | Manhole charasteritics Match NZS 3106 | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
4.5 | Trench Excavation | Excavate to achieve required depth as per drawings C250, C106 Floor of trench to be even across width and length | Trench width and chamber clearance to walls comply with requirements | Photo | During trench excavation | Visual, Measurement Check | C | QE/SP
4.6 | Bedding | Bedding should be minimum 150mm compacted material | Bedding to comply with requirements Scala test to achieve 2 blows per 50mm | Photo | During installation | Visual, Measurement Check | C | QE/SP
4.7 | Chamber installation | Chambers shall be installed true to the design level | levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer | Photo | During pipe installation | Visual, Instrumental | C | SP/QE/SV
4.14 | Benching | Benching concrete shall have a crushing strength of 20MPa at 28 days. All benching and sloping surfaces on manhole floor shall be rendered in 20mm thick 1:3 mortar | Benching built up to the specifications | Photos | During benching contruction | Visual | C | QE/SP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
5.1 | As-built Drawings | Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2 | Engineer Approval | QA records | At completion | - | H | QE/CR
5.3 | Leak testing | Manholes should be tested seperately to pipeline for water tightness up to lower rim of manhole cover frame. Specs 1131: 16.2.2.5 | A maximum drop in water level over 30 min should not exceed 2mL/hr/mm of diameter/meter height of the manhole. | Photos, Test Records | For every manhole installed | Test, visual | H | QE/CR
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: