## Project Structure
Folder Structure |  |  |  | Checklists | #NAME?
Site QA
DB
Switchboards
Cable Tray
|  | Server Room |  | Cable Tray
|  | Open Office |  | Cable Tray
|  | Resource Area |  | Cable Tray
First Fix
|  |  | Kitchen | First Fix Electrical Common
|  |  | Social | First Fix Electrical Common
|  |  | Corridor to Boardroom | First Fix Electrical Common
|  |  | Resource Area | First Fix Electrical Common
|  |  | Server Room | First Fix Electrical Common
|  |  | Outdoor Deck | First Fix Electrical Common
|  |  | Boardroom | First Fix Electrical Common
|  |  | Lounge | First Fix Electrical Common
|  |  | VC Room | First Fix Electrical Common
|  |  | Breakout | First Fix Electrical Common
|  |  | Meeting | First Fix Electrical Common
|  |  | Open Plan Office | First Fix Electrical Common
2nd Fix
|  |  | Kitchen | 2nd Fix Electrical
|  |  | Social | 2nd Fix Electrical
|  |  | Resource Area | 2nd Fix Electrical
|  |  | Server Room | 2nd Fix Electrical
|  |  | Outdoor Deck | 2nd Fix Electrical
|  |  | Boardroom | 2nd Fix Electrical
|  |  | Lounge | 2nd Fix Electrical
|  |  | VC Room | 2nd Fix Electrical
|  |  | Breakout | 2nd Fix Electrical
|  |  | Meeting | 2nd Fix Electrical
|  |  | Open Plan Office | 2nd Fix Electrical
Floorbox Conduits
|  |  | Floorbox Conduits | Inground Services
Completion
Completion
FEL SM Weekly Site Checklist
| 2022-11-14 |  |  | FEL SM Weekly Site Checklist
| 2022-11-21 |  |  | FEL SM Weekly Site Checklist
| 2022-11-28 |  |  | FEL SM Weekly Site Checklist
| 2022-12-05 |  |  | FEL SM Weekly Site Checklist
| 2022-12-12 |  |  | FEL SM Weekly Site Checklist
| 2022-12-19 |  |  | FEL SM Weekly Site Checklist
| 2022-12-26 |  |  | FEL SM Weekly Site Checklist
| 2023-01-02 |  |  | FEL SM Weekly Site Checklist
| 2023-01-09 |  |  | FEL SM Weekly Site Checklist
| 2023-01-16 |  |  | FEL SM Weekly Site Checklist
| 2023-01-23 |  |  | FEL SM Weekly Site Checklist
| 2023-01-30 |  |  | FEL SM Weekly Site Checklist
| 2023-02-06 |  |  | FEL SM Weekly Site Checklist
| 2023-02-13 |  |  | FEL SM Weekly Site Checklist
| 2023-02-20 |  |  | FEL SM Weekly Site Checklist
| 2023-02-27 |  |  | FEL SM Weekly Site Checklist
| 2023-03-06 |  |  | FEL SM Weekly Site Checklist
| 2023-03-13 |  |  | FEL SM Weekly Site Checklist
| 2023-03-20 |  |  | FEL SM Weekly Site Checklist
| 2023-03-27 |  |  | FEL SM Weekly Site Checklist
| 2023-04-03 |  |  | FEL SM Weekly Site Checklist

## Cable Tray
Section | Cable Tray
Checkpoint | Unistrutt Filed & Painted
Checkpoint | Hangers Spaced as Specified
Checkpoint | Correct Size Tray Installed
Checkpoint | Tray Joined Correctly
Checkpoint | Hangers Seismic Restrained as per Design
Checkpoint | Tray Fastened to Hangers
Checkpoint | Correct Anchors used fixing to Ceiling
Checkpoint | Cable Tray Bonded
Section | Photos

## Switchboards
section | Switchboard
checkpoint | Fixings installed in wall correctly if board is wall mounted
checkpoint | All clearances sighted to ensure location is compliant
checkpoint | All cables correctly installed in protection device and earth and neutral bars and fully secured
checkpoint | Cables neatly dressed
checkpoint | Phase tabs on chassy covered
checkpoint | All earths and neutrals labelled to match phase numbers
checkpoint | Switchboard is clean on the inside and outside
checkpoint | Masking blanks installed
checkpoint | Feisst label on the door installed
checkpoint | Switchboard Tested & Passed, results uploaded to drive via iPad
checkpoint | DB legend installed
section | Photos

## Floorbox Conduits
type | name
checklist | Inground Services
section | Ducts and Conduits
checkpoint | Correct size installed
checkpoint | Start and finish locations correct as per plan
checkpoint | separation from other services
checkpoint | Clean inside and in good condition
section | Photos

## First Fix Electrical Common
type | name
checklist | QA - First Fix Electrical Common
section | Flush Boxes
checkpoint | Height as per plan
checkpoint | Location as per plan
checkpoint | Fire rated boxes installed where necessary
checkpoint | Acoustic boxes installed where necessary
checkpoint | Flushboxes not back to back on Acoustic / Fire Walls
checkpoint | Intumescent Pad in Place
section | Cabling
checkpoint | Power cables installed correctly
checkpoint | Lighting cables installed correctly
checkpoint | Switching / Control cables installed correctly
checkpoint | Circuits clearly labelled
checkpoint | Separation between Data and Power at 300mm or as specified
section | Cat Wires
Checkpoint | 300mm Seperation Between Power & Data
Checkpoint | Supported every 6 Meters or Adequately to avoid Sagging
Checkpoint | Correctly Secured at Each End
Checkpoint | Turn Buckle Installed and Accessible
checkpoint | Number of cables per cat wire. 8 maximum or as per electrical spec
checkpoint | Separation between other services maintained
checkpoint | All cables secured via cable ties with ends cut
section | Cable Tray
checkpoint | Minimum 25% spare capacity left on cable tray
section | QA - Lights
checkpoint | Setout Correct
checkpoint | General Lighting Cabling installed and correct locations
checkpoint | PIR Sensor Cabling Installed and in correct locations
checkpoint | Emergency/ Exit Lighting Cabling Installed and in correct locations
checkpoint | Nogging installed for Electrical Services
section | Photos

## First First Electrical
type | name
checklist | QA - First Fix Electrical
section | Flush Boxes
checkpoint | Height as per plan
checkpoint | Location as per plan
checkpoint | Fire rated boxes installed where necessary
checkpoint | Acoustic boxes installed where necessary
checkpoint | Flushboxes not back to back on Acoustic / Fire Walls
checkpoint | Intumescent Pad in Place
section | Cabling
checkpoint | Power cables installed correctly
checkpoint | Lighting cables installed correctly
checkpoint | Switching / Control cables installed correctly
checkpoint | Circuits clearly labelled
checkpoint | Separation between Data and Power at 300mm or as specified
section | Cat Wires
Checkpoint | 300mm Seperation Between Power & Data
Checkpoint | Supported every 6 Meters or Adequately to avoid Sagging
Checkpoint | Correctly Secured at Each End
Checkpoint | Turn Buckle Installed and Accessible
checkpoint | Number of cables per cat wire. 8 maximum or as per electrical spec
checkpoint | Separation between other services maintained
checkpoint | All cables secured via cable ties with ends cut
section | QA - Lights
checkpoint | Setout Correct
checkpoint | Cabling in correct location
checkpoint | PIR Sensor Cabling Installed
checkpoint | Emergency/ Exit Lighting
checkpoint | Nogging installed for Electrical Services
section | Photos

## Second Fix Electrical
type | name
checklist | QA - Second Fix Electrical
section | Power Outlets
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Outlet Installed level
checkpoint | Circuit Tested and results recorded
checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
section | Light Switches
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Light switch Installed level
checkpoint | Circuit Tested and results recorded
checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
section | Light Fixtures & PIR Sensors
checkpoint | Correct type installed
checkpoint | Correctly installed with terminations all secured properly
checkpoint | Tested for operation
checkpoint | Seismic Braces Installed as per design
section | Photos

## Completion
type | name
checklist | QA - Completion
checkpoint | All Areas Defected by SM & Feisst Team prior to PC
checkpoint | All DBs Tested, results uploaded to Drive on iPad and sent to Project Admin
checkpoint | PS3 Completed & Signed for Emergency Lighting
checkpoint | PS3 Completed & Signed for Seismic Bracing of Electrical Fixtures
checkpoint | All COCs completed and Submitted to Julia
checkpoint | "Clean" As Built Set of Drawings Completed and Submitted to Julia
checkpoint | All excess material removed from site and returned to wholesalers
checkpoint | All assets accounted for and removed from site

## FEL SM Weekly Site Checklist
type | name | values
checklist | FEL SM Weekly Site Checklist
section | Monday
checkpoint | Prestart Meeting with Team
checkpoint | Health Check
checkpoint | Review Tasks for the week
checkpoint | Identify Targets Including Hours
checkpoint | Approve hours by 9AM for previous week
checkpoint | Sign off Subcontractor Hours & Submit
checkpoint | Review SWMS
checkpoint | Site Toolbox Meeting
checkpoint | SSSP in Order
section | Tuesday
checkpoint | Follow up outstanding RFI's with PM
section | Wednesday
checkpoint | Review Roadblocks & Follow Up if still unresolved
checkpoint | QAs up to date
section | Thursday
checkpoint | Weekly planner filled out for week ahead
checkpoint | Roadblocks identified and actioned
checkpoint | Materials organized for week ahead
checkpoint | Plans printed with any relevant notes added
section | Friday
checkpoint | Submit Toolbox minutes to main contractor and FEL office
checkpoint | Job Cards up to date and submitted
checkpoint | Team tasks for week ahead filled out on whiteboard