## General
SECTION 1 – GENERAL DETAILS
Project Name: | DCC11014 Water Pump Station Renewals - SILVERSTREAM | [5 empty] | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561482 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council | [5 empty] | B | Report by Breach | CM | Construction Manager | Stephen Vorgers
Contract Number: | DCC11014-WPS002 | [5 empty] | C | Check | CR | Cust. Representative | Joff Riley / Mark Todd
Area/ Sub-System: | Commissioning - Silverstream |  |  | Lot ID Number: | N/A |  | D | Dimension Inspection | IP | Inspection Personnel | Bruce Allan
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | 561482-ITP-010 |  |  | Version: | DRAFT |  | H | Hold Point | OP | Operations Manager
ITP Description: | Commissioning - Inspection Test Plan | [5 empty] | I | Inspection | PM | Project Manager | Matt Paterson
Discipline: | Commissioning & Testing | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | C11014 Water Pump Station Renewals Specification 12581908 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | Construction Issue Drawings as issued by GHD - Silverstream Pump Station Project Ref: 12581908-GHD-PS-SS-DRG-GN Drawings: G0001, M0001 through M0004, & P0001 | [5 empty] | S | Subcontractor | SP | Supervisor | Hamish Watrson
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Hamish Watson / Matt Paterson |  |  | Date: | 2024-12-10 |  | W | Witness Point | SV | Surveyor
Quality Specified: | None - As per Specification | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Hamish Watson |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Paterson/Stephen Vorgers |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: | Joff Riley / Mark Todd |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
3.1 | Ensure installation complies with Electrical regulations and GHD specification (whichever more stringent) | Prior to livening up Electrical board | Installation in compliance with Electrical Regulations | Electrical COC | Once | Visual Metering | I | IP
3.2 | Ensure the Mechanical Installation is installed in accordance with the Drawings & Specification | Prior to system testing & flushing | All items are as per specified and installed to best trade practice | Completed ITP's | Once per ITP | Visual Metering | I | IP

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
4.1 | commissioning of switchboard | Switchboard modifications carried out, livened, subcircuits isolated | switchboard mounted controls operate as expected | Switchboard ITR | Once | visual | I | IP
4.2 | commissioning of motors | motors installed and terminated | confirmation of correct wiring configuration. | Specific motor ITR's | once per motor | visual | I | IP
4.3 | commissioning of VSD's | VSD's not energised | Power supply to VSDs correct as per supply/design | electrical drawings for site. | once per VSD | visual | I | IP
4.4 |  | VSD's powered up, before test running. | VSD's set up correctly for motors connected. | VSD ITR's | once per VSD | visual | I | IP
4.5 | rotation test of motor | VSD's configured, set to run at low speed | Motor Rotates in correct direction | Specific motor ITR's | once per motor | visual | I | IP
4.6 | Verification of local motor controls | motor operation confirmed, water in system. | controls operate as expected, e-stops do not automatically reset upon release. | Specific motor ITR's | once | visual | I | IP
4.7 | Verification of PLC inputs | PLC Installed, outputs made to a safe state, | Verification of input and output operations. verification of analogue input operation | Automation ITR | once | visual | I | IP
4.8 | commissioning of swing check valve microswitch | Check valves installed | Signals verified to PLC | Automation ITR | once | visual | I | IP
4.9 | Re-commissioning of pressure transducers | Pressure transducers installed, no pressure on system | Pressure transducers read as expected, output to plc verified and range confirmed. Verified against external gauge. | Automation ITR | once per PIT | Visual | I | IP
4.10 | Re-fill pumps with water | Open Valves slowly on suction & discharge side of pump | Bleed pumps and any high points in pipework | This document | Once | Visual | I | IP
4.11 | Turn on pump 1 - Check for correct operation | Pressure transducers and flow meters installed, pressurised system | Correct operation of instrumentation (Flowmeter & pressure transducer) | Automation ITR | Once | Visual | I | IP
4.12 | Turn on pump 2 - Check for correct operation | Pressure transducers and flow meters installed, pressurised system | Correct operation of instrumentation (Flowmeter & pressure transducer) | Automation ITR | Once | Visual | I | IP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key)
5.1 | Water supply is un interrupted and purged of any air | Bleed of entrained air | Wet well is full | This document | Once | Visual | I | QE
5.2 | Controls systems are operational and functioning as intended as per the Functional Description | Automation functionality verification | As per GHD design | Commissioning plan | Once | Visual | I | QE
5.3 | Pumps are operating correctly and changeover as per the control strategy. | Automation functionality verification | As per GHD design | Commissioning plan | Once | Visual | I | QE
5.4 | Pump flow is achieving the expected flow rate. Flow rate recorded and provided to Engineer | Correct setup of VSD | Flow rate matches design data | Pump datasheet | Once | Visual | I | QE
5.5 | System successfully communicating with DCC network | RTU communicating | Connectivity to client network | Commissioning plan | Once | Verification form Client | I | QE Client
5.6 | DCC Water technicians attend for operation & handover. Client Instruction | Operator attendance | Acceptance by DCC Operations | Commissioning plan | Once | Verification form Client | A | QE Client
5.7 | Operation & Maintenance Manual | Commissioning complete, system in operation | Installation complete, all technical data obtained | Published Operation & Maintenance Manuals | Once | Review of Documents | A | QE
5.8 | Mark Up drawings for As-Builts | Commissioning complete, system in operation | Installation completed | Red-Line Mark up Drawings | Once | Review of Documents | A | QE
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: