## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Postfix
46bdb08a-53d8-4ff9-902b-b3f963080877 | checklist | 561482-DOW-ITR-EL-0001 |  | 561482-DOW-ITR-EL-0001
490e47a8-734a-4c19-b593-7514b7125d34 | section | GENERAL DETAILS
a6704faa-ac58-490e-982d-035d49db31d1 | checkpoint-no-value | GENERAL DETAILS
d174c019-cf3c-5048-9ea1-e6b93462993f | note | ITR Number: 561482-DOW-ITR-EL-0001
b4c7024f-7f62-562e-a479-9f8f66b22a2e | note | Project Name: Pump Station Renewals – Silverstream Pumps
c132b089-4a2e-57de-9617-0018b477f834 | note | Contract/ Project No: 561482
3b1faa24-1a9f-5953-baee-cd010a20877c | note | Area: Silverstream Pumps
7258a5a4-079e-50b9-8a1c-ba2debcabd3e | note | Sub-System: Pumps
c5eaebe5-3b01-54c7-92ce-b6939152a8b7 | textbox | Reference Drawing:
ef70203f-3621-508e-a3d6-edf5f2860f97 | note | Discipline: EICA
1efeb13e-d1ac-5892-b341-8efd467fb16f | note | Work Pack Number: N/A
9063e935-7d8b-5fd2-b30e-112c800e3f15 | note | Lot Number: N/A
45337309-3bfd-5d42-b603-f3bce2bcdccf | note | Cable Number: TBC
138e3898-044a-5c11-9c02-660b96bb0d6d | note | Cable Specification: 50mm 3c+e Circular
db1e1870-8965-5f33-a5df-cc03e31ec2c4 | note | Source: Site MCC
45541751-fafe-5748-b10b-eb943d6ca573 | note | Destination: Pump 2 VSD
33be0498-45b0-5a0a-99e2-d26e5b20f8d0 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
0d80d2ad-17e3-4052-a175-52226a13a576 | section | INSPECTION
96f9f267-ca39-491b-b13e-872f0bc8ed35 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
a704ad21-7d09-4dc5-8694-489a36b5d51b | checkpoint | Cable size and type correct
3ac467e0-263a-4dc8-9069-f50d6deee578 | checkpoint | Cores terminated as per drawing & terminals tight
97efb197-ea3d-42e9-99ea-120feae9ccdb | checkpoint | Cable numbered correctly and applied at both ends
2b8479b9-7b7d-46e4-8371-98bca1e74f1c | checkpoint | Permanent core markers attached both ends
c416472a-a947-4431-b0d7-5a533e8e5378 | checkpoint | Cable supported and protected as per specification
7da97c13-c8d6-424e-83b3-79cb36a347b1 | checkpoint | Continuity of earth conductor/ screen satisfactory
b399cd41-eb4d-4d48-a3bf-b35c75dab248 | checkpoint | Cable ties trimmed
957e18ac-ec2c-4c8f-abc2-98b3b0c0194b | checkpoint | Connection of shielding/ armour as per drawings
3d2a175d-b8d2-4bb7-a493-945512cebd4a | checkpoint | Cable ends made up satisfactorily
ca92a645-6de2-4d7b-882e-b4d2950c296e | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
4a8603c3-04f4-48ef-a811-9216bc0a8abe | section | Field Test
e81f6b65-da9f-4a0d-9493-07f29c5a90ed | checkpoint | Field Test
d48c07e9-5047-5998-beab-0e57d2e74f49 | textbox | Core Designation: R-E |  |  | Results - MΩ
35952a6a-1348-5f57-916f-16fbd7bee310 | textbox | Core Designation: W-E |  |  | Results - MΩ
7de30493-5c66-55e4-be61-e17da2cad72e | textbox | Core Designation: B-E |  |  | Results - MΩ
a494c3ae-7816-5e12-987f-b1b035f9e082 | textbox | Core Designation: R-W |  |  | Results - MΩ
f22a1267-60e0-5b90-9489-0903f8ba3a9a | textbox | Core Designation: R-B |  |  | Results - MΩ
147b0cdd-6a2f-55b9-bac2-1189021700f6 | textbox | Core Designation: W-B |  |  | Results - MΩ
f4175d84-54eb-5143-a057-291122bdf57c | textbox | Cable Size:
0c1ef975-7e01-55fc-aadc-ea087a15aaf5 | textbox | E Continuity: |  |  | Ω
f61072a0-b041-5c32-88de-156d6fbcb358 | textbox | Lead Resistance: |  |  | Ω
38c6e329-45f0-452a-96a1-78e65842c6e1 | section | Completion
e6b75810-52a8-48e5-bb90-2f0ffde75489 | checkpoint | All cores reconnected and secure
60e45e49-7453-41cb-b6b8-6430919331d9 | checkpoint | Source connection tension
0e1c2689-d28a-568a-a583-fcdf6d1d8702 | textbox | Nm:
353498d9-b1ce-4e41-922d-f88ef3c09b3b | checkpoint | Destination connection tension
20121ab2-655b-5bb0-8f1a-8cff288c41bb | textbox | Nm:
22a918ed-667c-4b73-b825-395a474d5eca | checkpoint | All connections visually and physically checked
a24d6cd9-e009-4060-b791-8bdb16ac0cde | checkpoint | All test leads and bridges removed
6f6caa3e-054e-4a53-954a-0dabb8603219 | checkpoint | Drawings & schedules marked up to 'As Built' status
8dc6bca9-64f5-49a3-84ef-6ad2b3201931 | section | VERIFICATION
b11504cc-15b3-4fb6-a7cf-c2626602dfe0 | checkpoint | VERIFICATION
43d73d6e-a392-518a-91a7-4f4eb45368b3 | textbox | Deficiencies Identified:
bfa53376-41a4-5d3b-a6d3-f9ab656f3f8d | tickbox | Rectified/ Closed-Out
e6a97379-c63b-5ccc-815f-43cf8181fb82 | tickbox | Punch Listed
38042e58-d4b9-43a1-9b4d-be355d19fb8b | section | TEST EQUIPMENT
bdc1da99-adc4-4f1d-acc8-2b7f4ba82bf0 | checkpoint | TEST EQUIPMENT
c601fdb6-24d1-5ada-ac21-b11ab08f01a4 | textbox | Type of Meter
afaa0148-d68d-571a-bf99-5d72e9bb2425 | textbox | Make/ Model
5141cf9d-002f-5f73-b614-65f3d50a1b28 | textbox | Serial No.
a4a4be3c-a093-5e3b-8694-6bcd3fb6a9ad | date | Calibration: Date
e1ab1b61-aa89-5d8e-aa00-4325eac50854 | date | Calibration: Due
5c3d8865-1a35-49fb-9a5c-2d0e285f0b85 | section | ACCEPTANCE
5894d218-bad4-4a00-b34a-cd66669708f2 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
9aed2938-694d-4ccb-95c9-a05e64863e7b | signoff | Add Signature
6c900653-98ae-4ef9-9b10-87d3ac0d0d0d | checklist | 561482-DOW-ITR-EL-0002 |  | 561482-DOW-ITR-EL-0002
1f9b3bdc-8775-4c0b-af7f-2d38143c456a | section | GENERAL DETAILS
af287929-8794-4fb3-9a5d-d28fccb61549 | checkpoint-no-value | GENERAL DETAILS
c93ea3b9-13fb-5cdd-bae5-8194a0500055 | note | ITR Number: 561482-DOW-ITR-EL-0002
6da3cf1f-e586-5a19-b1c0-29cec6b9c415 | note | Project Name: Pump Station Renewals – Silverstream Pumps
23f7e14d-0937-505e-908f-173c430f33dd | note | Contract/ Project No: 561482
c80c70a8-f15e-577c-a63f-81ed1669ea51 | note | Area: Silverstream Pumps
7f0603e0-762c-5034-b58c-4d8eaf8af6b3 | note | Sub-System: Pumps
6f329f51-2a59-5826-a7b8-70e01ac753c7 | textbox | Reference Drawing:
058546a7-f7d5-5941-ad47-0f909e2c35e9 | note | Discipline: EICA
2ac2f980-2315-5668-86fd-b4daaa30cfc8 | note | Work Pack Number: N/A
08bfc57e-5195-5df9-b925-a874c0545758 | note | Lot Number: N/A
559f9ce8-37e4-5c41-b2ce-29379488daf6 | note | Cable Number: TBC
7dfa6880-b236-5280-b5ca-d98ce22dbb1f | note | Cable Specification: 50mm 3c+e Circular
5ccb347a-3f81-5140-bb99-bab73c32c426 | note | Source: Site MCC
1cbf3b88-1cfc-5c5f-a54f-ee4999623334 | note | Destination: Pump 3 VSD
6d88023a-9716-59dd-ae26-f2e13e52ea91 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
9d57c6f5-4498-4f17-aa67-b49d1e8c7ac1 | section | INSPECTION
b20d2de0-eb59-4411-9c84-96a39a212648 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
b7cabe26-5bdd-49f0-9d66-49afd4c39a34 | checkpoint | Cable size and type correct
f574d123-ef10-477f-b025-f3a4e9e25500 | checkpoint | Cores terminated as per drawing & terminals tight
a6a908d0-7da6-4ee3-aa62-e4df4114e703 | checkpoint | Cable numbered correctly and applied at both ends
54bb24a1-8e7b-4ddd-9765-3e611de14be9 | checkpoint | Permanent core markers attached both ends
1bb29c34-51ea-4695-bda0-228c2565a1ea | checkpoint | Cable supported and protected as per specification
449b75c3-a44a-4567-85d8-398185a08eec | checkpoint | Continuity of earth conductor/ screen satisfactory
788a932d-f726-4007-94c2-080cce8bb8d8 | checkpoint | Cable ties trimmed
9f2a3234-e99b-4934-9e08-e67f8fcd8cbf | checkpoint | Connection of shielding/ armour as per drawings
c5ab981f-28f9-43a6-a05d-e270b2f2b227 | checkpoint | Cable ends made up satisfactorily
8d5f0383-5300-4152-a68f-a19f9c9af8c9 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
60e4faf3-ed41-4555-b8a4-339cf628a87e | section | Field Test
978dd1bc-107c-4c6f-ab54-d41a9a2b8fbd | checkpoint | Field Test
c7a9e128-a622-563a-9b43-019efe6b77af | textbox | Core Designation: R-E |  |  | Results - MΩ
cd8fd7eb-0c26-5ec6-a4ee-4ffb63684136 | textbox | Core Designation: W-E |  |  | Results - MΩ
72610264-1c31-52bd-bc5f-122af12e43e6 | textbox | Core Designation: B-E |  |  | Results - MΩ
84447103-2ade-5d6d-b2a8-05505b788658 | textbox | Core Designation: R-W |  |  | Results - MΩ
477c0cff-e25b-5186-87e5-9881fa3ff4af | textbox | Core Designation: R-B |  |  | Results - MΩ
b2e0980a-b0e5-5aa6-a698-927b41c413c9 | textbox | Core Designation: W-B |  |  | Results - MΩ
af140be6-1839-50ef-a1b5-5830c288d76e | textbox | Cable Size:
d58f7ba1-3dad-5b14-b82b-c28d21a85498 | textbox | E Continuity: |  |  | Ω
fa571d5a-926f-5f54-8e00-1c1407d28c82 | textbox | Lead Resistance: |  |  | Ω
811e5c4c-4415-4114-95ab-dc004852c281 | section | Completion
87986a0c-ea71-42ab-99cc-ba2cc803b680 | checkpoint | All cores reconnected and secure
5ab177b1-a9eb-4ce8-98d1-d9a7e0187a22 | checkpoint | Source connection tension
85610c26-c3f0-5f9e-aa6e-f47b1488b526 | textbox | Nm:
32d8ce17-2d1d-4e90-b0ee-6c2e3a881f2f | checkpoint | Destination connection tension
3fabca7e-e48f-5460-a689-328d79630715 | textbox | Nm:
e755bb28-ecba-4681-9397-4605be3e13c6 | checkpoint | All connections visually and physically checked
6ab3ca67-690a-4d4f-87a2-fef15ef4af08 | checkpoint | All test leads and bridges removed
ad32a0d4-50e3-4ecc-8277-e0d38bcab4ec | checkpoint | Drawings & schedules marked up to 'As Built' status
a4b9bcbb-a66a-4974-b075-72de1d37fbe2 | section | VERIFICATION
f7940a87-8507-4003-abfe-bd43e15aa7ff | checkpoint | VERIFICATION
2201b93e-2ec1-5d3d-af49-27a4d3324aa7 | textbox | Deficiencies Identified:
dab4dbc0-9047-50be-82d8-189f050cd04e | tickbox | Rectified/ Closed-Out
bea5b8df-e262-5395-b1a8-a0f8bd12554b | tickbox | Punch Listed
c76fe494-3fa6-462c-aa9d-bc459eae16f0 | section | TEST EQUIPMENT
ff589755-0a21-4122-ab80-d2d1ff11cdb7 | checkpoint | TEST EQUIPMENT
6a61cc04-2add-5ae9-90cc-c8ae00b689ca | textbox | Type of Meter
4c7e7c3d-3c57-56a3-8009-76af42d4c553 | textbox | Make/ Model
659159d5-9c61-5acc-9332-7aba6f725014 | textbox | Serial No.
ffd0ff85-3ac4-59bc-b3ba-d524328e22a5 | date | Calibration: Date
3752226c-42e7-5e59-80a7-e15f9e07a624 | date | Calibration: Due
84a729b4-b3fb-43dd-a615-0ad661a6570a | section | ACCEPTANCE
d8cf7280-43ad-4771-bb9e-e6e44953d2e0 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
4f0d3fde-286f-4934-956f-fc7796e43033 | signoff | Add Signature
ec2f402e-1e25-4655-b653-1adc0ca25020 | checklist | 561482-DOW-ITR-EL-0003 |  | 561482-DOW-ITR-EL-0003
ba5946fb-b82d-4499-b2fd-30f5c2c031fc | section | GENERAL DETAILS
adc27e2e-8e9b-476f-85d4-bb242bb8aa73 | checkpoint-no-value | GENERAL DETAILS
03cd2f7c-a4a8-59e5-8c82-ce66818f893f | note | ITR Number: 561482-DOW-ITR-EL-0003
b7675fed-4b00-56cd-83e6-01000de3cb53 | note | Project Name: Pump Station Renewals – Silverstream Pumps
5a51a2af-6dc4-5164-b96a-d045e859c641 | note | Contract/ Project No: 561482
8cee4735-d4da-54ea-ac5d-e8c32d04f9f0 | note | Area: Silverstream Pumps
4a7572c9-f422-5273-b6ec-2a61e870d85b | note | Sub-System: Pumps
d1333993-fe99-5308-985c-90f54e36ffb1 | textbox | Reference Drawing:
543c219b-0cfc-5c32-86ab-6f98555b806c | note | Discipline: EICA
cb67388f-f7cb-5852-a2d7-030ac63c5e71 | note | Work Pack Number: N/A
eeb43d26-7eb9-5bf6-bf20-4994e7d43f0e | note | Lot Number: N/A
2cf926d9-9cef-5b2c-90c3-e7e5d4c811e4 | note | Cable Number: TBC
e5cbae24-ea93-5eb3-8fe1-f6efeba421e5 | note | Cable Specification: 50mm 3c VSD Cable
5a792e2a-46e8-57dd-9793-2f578d17fbfd | note | Source: Pump 2 VSD
afbb7a15-5207-5335-95d2-4d865417d5ed | note | Destination: Pump 2
e05c02f0-e462-55ad-917c-a14892b1af5f | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
161bd6ae-26cd-4c50-808e-caef9539163a | section | INSPECTION
8b611b77-412c-46e0-addd-929ac1d880e9 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
0fad52fc-50c3-4be7-a085-d4f0b80c0318 | checkpoint | Cable size and type correct
25577734-1c3d-4845-8c0c-80e21cdd581d | checkpoint | Cores terminated as per drawing & terminals tight
89559e93-0fba-4e06-9529-3a6cc6c4d6f0 | checkpoint | Cable numbered correctly and applied at both ends
183dd2a4-b794-4821-a5e3-414ad37ebd2d | checkpoint | Permanent core markers attached both ends
d8701437-e122-41c3-a2b3-e1a302723739 | checkpoint | Cable supported and protected as per specification
7c7f742a-15ee-486a-9d9f-30bd9898035d | checkpoint | Continuity of earth conductor/ screen satisfactory
8b70f95d-3c69-45fa-94ab-5717a5eb228b | checkpoint | Cable ties trimmed
409811be-5184-4fef-ab63-aa06684b0bb4 | checkpoint | Connection of shielding/ armour as per drawings
ea97db80-bcb8-4952-8f73-fffc1e2c40ed | checkpoint | Cable ends made up satisfactorily
b2a73903-95d7-4352-a181-ff3002faf25f | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
7334480d-48fd-4070-a883-272834bb215e | section | Field Test
77cd65e5-e8bf-4945-a41a-e90a99809ee0 | checkpoint | Field Test
01ae9f67-f590-58ac-b4bd-98dcb815823a | textbox | Core Designation: R-E |  |  | Results - MΩ
02409ecf-4c98-582a-8806-733294360b3d | textbox | Core Designation: W-E |  |  | Results - MΩ
2d25d28e-d914-50c1-8e57-7eb9571fb182 | textbox | Core Designation: B-E |  |  | Results - MΩ
acc9f1b0-0365-5251-a192-04adbd515d27 | textbox | Core Designation: R-W |  |  | Results - MΩ
84fdc135-de2f-5123-b1aa-9bea96c8e2b3 | textbox | Core Designation: R-B |  |  | Results - MΩ
168d9e38-82ea-5f9c-84fd-1d386bac3cb2 | textbox | Core Designation: W-B |  |  | Results - MΩ
280622a1-a8a9-5f31-9a82-5c6565fa2d07 | textbox | Cable Size:
0fdaa3ef-1119-537f-b65b-e301055302a4 | textbox | E Continuity: |  |  | Ω
2f7defbb-446f-5cc3-92f1-252a38f66689 | textbox | Lead Resistance: |  |  | Ω
6c36d970-d6d3-4f54-93b3-c23684914790 | section | Completion
066cd038-3b18-4b49-93dd-0a4085732c81 | checkpoint | All cores reconnected and secure
d5fc194a-3902-464c-9070-2b175b3f5e15 | checkpoint | Source connection tension
c22fc877-b5e2-5809-a659-2be483cc53bf | textbox | Nm:
1e7d4487-640f-4519-8e57-4bc3d8870789 | checkpoint | Destination connection tension
fa0e4da3-78fa-5dd7-9223-0f228b442660 | textbox | Nm:
5af70599-4936-43f7-b4f5-cf9b5d55f238 | checkpoint | All connections visually and physically checked
3e4346e6-23a6-4a02-9f0e-fb5debc51865 | checkpoint | All test leads and bridges removed
2ca1c1f7-8416-4245-9c34-cd05b038c7e2 | checkpoint | Drawings & schedules marked up to 'As Built' status
aeed48a8-33a0-46f2-9a83-f9cb75ab9b38 | section | VERIFICATION
775f93e4-f50c-48ed-be60-d69e2fa737d8 | checkpoint | VERIFICATION
e373cd59-4aa4-5977-b1f2-5d8ac7c08918 | textbox | Deficiencies Identified:
38d809e4-4e3e-5edf-a4b9-234bf15e0d69 | tickbox | Rectified/ Closed-Out
8d3c63f2-beed-52b7-a403-b9696039c806 | tickbox | Punch Listed
68a3ec33-d0f2-47b5-918b-37474205e8b7 | section | TEST EQUIPMENT
5210e94d-15da-43f1-90b5-3c29de2b509f | checkpoint | TEST EQUIPMENT
f865b527-5bbd-5795-bc29-f6978097329c | textbox | Type of Meter
825b793a-a17d-5a2e-a916-3cf8be6af0e2 | textbox | Make/ Model
a06a7733-a1b0-58a6-8517-0c28669fd725 | textbox | Serial No.
87e084fa-e851-53d7-8f6b-f979e1dd2679 | date | Calibration: Date
ba6a8b4d-771a-5465-bf6f-a21e255768cd | date | Calibration: Due
47ce6aae-76b2-4b26-833f-502bba9b29e5 | section | ACCEPTANCE
508a3df9-9206-4d47-b22a-9208d9071863 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
560c591d-36c1-4862-93a8-0dcff3fa4a04 | signoff | Add Signature
440b806a-bbda-4fed-be73-c833f5619995 | checklist | 561482-DOW-ITR-EL-0004 |  | 561482-DOW-ITR-EL-0004
46a03baf-b3b5-43ed-b74c-dfe286ffbdba | section | GENERAL DETAILS
f0eae58b-35e8-4a7f-b67f-56b8f4beba48 | checkpoint-no-value | GENERAL DETAILS
7d8ab75f-e5e5-59b9-ad3d-05192ec6d04f | note | ITR Number: 561482-DOW-ITR-EL-0004
93b64e97-52e9-5d46-a3bf-16f2eee12963 | note | Project Name: Pump Station Renewals – Silverstream Pumps
29243730-3c45-5135-a836-12651d16a546 | note | Contract/ Project No: 561482
86bea32c-0334-58c8-9e58-d19229319c3b | note | Area: Silverstream Pumps
f47ad404-846a-51f1-a978-fa560853bbc2 | note | Sub-System: Pumps
6064b594-310d-53f2-95ce-969f0e345514 | textbox | Reference Drawing:
47d4f204-b6f0-56d7-ad03-ea5ace6372fa | note | Discipline: EICA
3dbdea96-6e3b-591d-b02d-7feda8acce38 | note | Work Pack Number: N/A
7da01af5-24ac-5893-afbc-ebee290a1099 | note | Lot Number: N/A
669160d2-a193-5cd7-9df0-305639d39ee9 | note | Cable Number: TBC
f6c9801b-26dc-5a5e-a87a-82f1ce12d4cb | note | Cable Specification: 50mm 3c VSD Cable
70b0dd8f-47a5-5bdb-937b-6fb463ee0e9c | note | Source: Pump 3 VSD
7752875c-fba2-5142-9b56-0a121887c9d9 | note | Destination: Pump 3
d99caac5-df6f-5a65-9e19-57afabaeb101 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
c88e28f9-8397-4884-a1a9-07cacf82bbfd | section | INSPECTION
ffe90d9a-3ae2-4685-95bc-49a6b0862a7d | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
ccc490f8-1cfc-42e4-b0b5-5fc6b5ee40f9 | checkpoint | Cable size and type correct
8bfd40e9-fea7-43e2-bf86-60ec07adb845 | checkpoint | Cores terminated as per drawing & terminals tight
7d1d4822-181f-427d-a488-c746fceb4f0b | checkpoint | Cable numbered correctly and applied at both ends
fa38cde5-029c-4348-ae59-a5f30bf753bc | checkpoint | Permanent core markers attached both ends
80088b49-0f24-45a3-8fd2-a5fb1eed78f8 | checkpoint | Cable supported and protected as per specification
417d5900-0b33-4664-a60a-044a73552bdc | checkpoint | Continuity of earth conductor/ screen satisfactory
76218563-16ee-47be-8dfa-bdd46c9b502f | checkpoint | Cable ties trimmed
94fa5af4-fd9d-4cf3-8064-9183fea17a10 | checkpoint | Connection of shielding/ armour as per drawings
62959cb9-d4ca-423f-b9bd-6cacf3f94bff | checkpoint | Cable ends made up satisfactorily
6bcfe4d6-af59-4d5a-99d1-aabae6e0a503 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
9f697ea2-9b25-41ba-a57e-4659cb790551 | section | Field Test
641d1deb-297e-4f5d-a46c-629186bc089b | checkpoint | Field Test
8ce8373b-b765-536e-a72c-4e68e3be2555 | textbox | Core Designation: R-E |  |  | Results - MΩ
fcaf7924-4070-532b-8c02-59ebfd4eb27a | textbox | Core Designation: W-E |  |  | Results - MΩ
160e2244-e466-5d1b-b115-8a780f7be02e | textbox | Core Designation: B-E |  |  | Results - MΩ
5b011060-05d7-5cd1-ad35-5597d9e60c2c | textbox | Core Designation: R-W |  |  | Results - MΩ
75b9061e-8f6b-5660-96f5-f9ab27ed7de4 | textbox | Core Designation: R-B |  |  | Results - MΩ
01ffdc2e-ac8e-5cae-8847-8f5e7d929f24 | textbox | Core Designation: W-B |  |  | Results - MΩ
1dac07ea-2810-57c4-838d-7b3af9557236 | textbox | Cable Size:
b6d3c93a-6126-57ea-89c5-1d8f5569e0eb | textbox | E Continuity: |  |  | Ω
c3f9eef0-4abb-50de-94ee-e5a24ea28ec8 | textbox | Lead Resistance: |  |  | Ω
6f4164bd-d599-4f75-b03f-75cab8d439bd | section | Completion
621187cb-67cb-477f-82bd-3db19c155097 | checkpoint | All cores reconnected and secure
c465cad5-aeb8-48bf-b66a-a30720f55bf2 | checkpoint | Source connection tension
51c0a2e0-b530-572c-ba61-d72e6153a112 | textbox | Nm:
e8c516ef-783d-4f39-8e45-80e43cab7381 | checkpoint | Destination connection tension
04225934-fa54-5a49-ab9e-138dd941ac3c | textbox | Nm:
16f1f76b-ab63-4d13-8e92-d598c539ed62 | checkpoint | All connections visually and physically checked
ff724ff6-93e3-48ef-b42f-a3169bb72f10 | checkpoint | All test leads and bridges removed
f2b88e8a-647c-4bec-94f0-ab7a57c46d46 | checkpoint | Drawings & schedules marked up to 'As Built' status
1418aeef-07b0-46af-960e-ccf140f72f1b | section | VERIFICATION
485114e5-51fe-4a86-9ec1-072c60c5da86 | checkpoint | VERIFICATION
8c415108-f143-5052-85f3-9f0ea3c1ece7 | textbox | Deficiencies Identified:
479c3497-a139-5942-82c1-da610c6354bc | tickbox | Rectified/ Closed-Out
49877e3b-3657-5a46-be4d-ad33ef5f34f6 | tickbox | Punch Listed
6f3c7b50-bad5-4899-b057-fafdd4e067c0 | section | TEST EQUIPMENT
8ffd54ca-2eda-4366-a052-cec81d45396a | checkpoint | TEST EQUIPMENT
fe5422a0-2da4-52ce-bf17-26d06b072668 | textbox | Type of Meter
6386c218-dcf6-57f9-bdbb-dda3af088ccc | textbox | Make/ Model
f416aa70-924f-5066-a711-08898bcc166c | textbox | Serial No.
0e1738ef-8f50-5be5-9f1f-b4edf44860e3 | date | Calibration: Date
59629aae-222d-5d00-997e-34421ad3e7f5 | date | Calibration: Due
808fec8a-7439-400d-84f9-3378c2212b0a | section | ACCEPTANCE
07613046-5628-459e-b116-6b9ebb78d3d7 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
8da706c3-7254-4a3b-bf6e-d870accda146 | signoff | Add Signature
3f6a1974-bd0f-4c01-8081-27d1a832a581 | checklist | 561482-DOW-ITR-EL-0005 |  | 561482-DOW-ITR-EL-0005
8fe743e9-0ae4-40f3-a4a3-00eacb90fe75 | section | GENERAL DETAILS
5c299dd6-9a4f-4270-a701-27aa66c4fa39 | checkpoint-no-value | GENERAL DETAILS
20011d62-b627-5c20-9e1f-ae7704d77231 | note | ITR Number: 561482-DOW-ITR-EL-0005
1c074fdf-cc0e-5348-9103-445a88ed84f8 | note | Project Name: Pump Station Renewals – Silverstream Pumps
f4126fc3-0417-551a-a9e9-aab685958e77 | note | Contract/ Project No: 561482
9dcc51b1-717e-59c0-afeb-cf7a26cd4f2e | note | Area: Silverstream Pumps
2ffde549-a982-56f9-bc33-37685ab9a266 | note | Sub-System: Pumps
8b919373-7e8e-5e05-b43e-f951b9582d02 | textbox | Reference Drawing:
e99592e2-0f30-526f-8990-031e3225e022 | note | Discipline: EICA
f4463b00-44b5-5eb9-8808-699f7e8dc103 | note | Work Pack Number: N/A
6eb2b6cd-184d-5da2-a661-2b13bb42ac56 | note | Lot Number: N/A
37fdd1dd-38f0-50e1-8a2a-e89633540cdf | note | Cable Number: TBC
74ca06de-ae0a-56d1-8b8e-9891ce388a38 | note | Cable Specification: 95mm -final details tbc
c167de46-50d0-524b-ab43-dfdcc393c573 | note | Source: Site MCC
52659969-641e-5ab3-9a78-d2a033dda0f8 | note | Destination: Generator Connection box
8f1bf232-b5dc-5844-9379-ad9beec2f692 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
21cf6eca-a7bb-4639-b50a-9c314eea9baf | section | INSPECTION
029312d0-109e-48fb-aa29-4c54374ffe5b | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
23c550f7-fcb3-405f-8464-f128d4c6d8c7 | checkpoint | Cable size and type correct
edc72eda-27d5-4dae-acdd-49d827c30e8e | checkpoint | Cores terminated as per drawing & terminals tight
7badb281-40f8-4ffa-b6b2-0f435584c929 | checkpoint | Cable numbered correctly and applied at both ends
fec5d106-a2a2-41c3-8413-bfbe12720831 | checkpoint | Permanent core markers attached both ends
4a042daf-f344-4d0f-b633-48ee8d37f7d7 | checkpoint | Cable supported and protected as per specification
0ac66a2e-faba-45a9-bc38-c98999f7f835 | checkpoint | Continuity of earth conductor/ screen satisfactory
069b62c9-f7be-40e0-852a-09bdd9b24ed1 | checkpoint | Cable ties trimmed
10cb7efc-fade-4dc0-8593-5383ff3c6e62 | checkpoint | Connection of shielding/ armour as per drawings
b3af0030-235d-40e8-82b2-e02934652e09 | checkpoint | Cable ends made up satisfactorily
88e5719f-4608-4957-9a85-44c1131bcdc4 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
1256a927-fddb-4811-8ce3-c9c67948db49 | section | Field Test
9fb8c176-fcb8-47a8-9bc7-5ef49826cd2d | checkpoint | Field Test
f9a8dd8b-11ce-5029-ba6e-d4dfef506bb3 | textbox | Core Designation: R-E |  |  | Results - MΩ
b45741da-061c-5dd1-86f2-4d28689bd250 | textbox | Core Designation: W-E |  |  | Results - MΩ
fe41b123-c6cd-576f-9ece-84299ca53f0f | textbox | Core Designation: B-E |  |  | Results - MΩ
2b452d34-44dc-56fc-aa65-c3081d399425 | textbox | Core Designation: R-W |  |  | Results - MΩ
b2bb93df-08b5-57e0-a572-e01f1ec3324c | textbox | Core Designation: R-B |  |  | Results - MΩ
56c7be3d-059a-5e84-9b81-bb030fd51ce7 | textbox | Core Designation: W-B |  |  | Results - MΩ
74d8dcca-f3f4-5481-9f7b-102c9e58ae62 | textbox | Cable Size:
fe00bbc6-a05d-5610-8a95-63aaa4ac0fb9 | textbox | E Continuity: |  |  | Ω
23a9177a-7057-5c6c-bac7-f7b08dc0714e | textbox | Lead Resistance: |  |  | Ω
15bc07c4-7ac3-46d4-aefd-4178ce772c0d | section | Completion
13df2665-f3e2-452a-93d1-6f324d76eccc | checkpoint | All cores reconnected and secure
9fbc27ee-efa6-42db-a43a-268b932269bb | checkpoint | Source connection tension
d55eef1b-4f85-5732-ad28-3f9bf8df590d | textbox | Nm:
a9928ea8-50cc-4e5c-962f-9b8a1c420e0f | checkpoint | Destination connection tension
845e50fe-3556-58f5-aa14-340ffb91a1f4 | textbox | Nm:
97052b28-58c5-47fc-bfd3-23644a9ccc03 | checkpoint | All connections visually and physically checked
ff6318b3-d958-490c-85b8-fd4b73ad3b2a | checkpoint | All test leads and bridges removed
b664be0a-97f8-421d-a7af-6b48f73f778e | checkpoint | Drawings & schedules marked up to 'As Built' status
8bf9d15d-2f6e-4c59-a36f-74a2118637b1 | section | VERIFICATION
885535cb-c087-4835-ae38-70645c07c76b | checkpoint | VERIFICATION
77e3dc7c-efd5-56be-9fca-c1060c723cdd | textbox | Deficiencies Identified:
6f30f6c1-731f-5bb6-b74b-21d6de59afcc | tickbox | Rectified/ Closed-Out
0a4ff8e5-3208-5809-9b68-654f8e7a844e | tickbox | Punch Listed
c08ff26a-ce42-48d4-a9f0-5cad3bbe2b94 | section | TEST EQUIPMENT
a8f7c5c7-e6e4-454d-ab40-0f84454a22d9 | checkpoint | TEST EQUIPMENT
c86e78ae-34fd-57bf-b724-cb0312c262da | textbox | Type of Meter
9441d8ed-27bb-5acd-935d-50491b8f12e7 | textbox | Make/ Model
94f87772-3a8f-5b8d-b3d2-eb8844c15a29 | textbox | Serial No.
066a67a1-e104-5f9b-828c-1ee4750abf0a | date | Calibration: Date
d48d04f7-ce8c-5ba7-beff-3f3fa90e5dc3 | date | Calibration: Due
e72c85b9-0cff-4c9c-8896-657675ad5403 | section | ACCEPTANCE
8279dae5-f8f3-4a42-af25-6280502d512a | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
2269548e-b0a1-428e-b0b8-8b0c1f953c01 | signoff | Add Signature
20b5f2b5-d776-4bef-9960-75731bdb086f | checklist | 561482-DOW-ITR-EL-0006 |  | 561482-DOW-ITR-EL-0006
17095faf-da69-4aba-9ff8-3bd5a68c90b5 | section | GENERAL DETAILS
b05dc321-19a9-4c77-a822-2e63e540891d | checkpoint-no-value | GENERAL DETAILS
08ed8eaa-7707-5101-8c5c-98b999d973e9 | note | ITR Number: 561482-DOW-ITR-EL-0006
c49a5f8a-75af-5642-af0b-7e2777e0e4b7 | note | Project Name: Pump Station Renewals – Silverstream Pumps
7e138d2a-efbc-5d08-a1a8-d85bb803bb1d | note | Contract/ Project No: 561483
762e0fba-831e-5453-a864-f91dbb120ce0 | note | Area: Pumps
a60ff908-67c4-5722-9d6a-20a7b2c2fb31 | note | Discipline: EICA
6047a85b-f602-54fd-8174-12d2826aa412 | textbox | Reference Drawing:
8bdb0cf0-9ae6-5477-9bf3-3a1a5bb81a5a | note | System Reference: Pump 2
e88fff8e-d4da-52f1-8e6c-54c1417dfe11 | textbox | System Description:
d040a5ff-a69c-5d81-9d9a-760f822e69c0 | textbox | Motor Size:
5304770f-7a67-5191-b545-aeddc6f6cbd0 | textbox | Motor Brand:
b773772b-7dc3-5f4f-8240-3aef3aa31a31 | textbox | Motor Serial:
e8dc7008-d306-5af6-bcf3-6a875112e59a | button | Motor Connection: | Δ,Υ
ab2089e3-8433-5d77-83d5-c7bce219108b | textbox | Tag Number:
c9021ced-43a4-5cba-bb49-45db082d40e1 | note | PAU/ Skid Number: N/a
83407e8e-ad42-423e-85ad-645d7b3cca58 | section | INSPECTION - Completion Verification
7d77025c-b51a-4e06-8588-a6707fd26074 | checkpoint-no-value | Equipment, sub-system or system to be function tested during pre-commissioning must be subject to safety measures including, but not necessarily limited to: SWMS, Notice of Energisation, erection of safety barriers with warning signs and an open communication channel between testing personnel. Energisation and site acceptance test procedures are to be conducted with subcontractor/ supplier representative(s) as required.
733790fa-59e5-4176-9e57-d7c8e4a1f0a8 | checkpoint | Cable test and inspection completed
fca9ec59-c11d-4ded-89a1-6b90da1f7e93 | checkpoint | Motor switchgear ITR completed
301aa988-bb0f-432b-804e-7a116a822cae | checkpoint | Punch list "A" items completed from cable test sheet
02da00bc-b637-446c-8091-014e86d05318 | checkpoint | Hazardous area check sheets completed and accepted
633ccaa7-5f14-415e-b0fe-9a4a8232c602 | section | INSPECTION - Equipment Specific Pre Commissioning
c9cc745f-f825-474d-a032-e5dff5cb467a | checkpoint-no-value | Ensure interlocks are healthy (force status/ link out). Apply control voltage to motor starter circuit. Verify control/ trip functions. Ensure motor is safe to start – close MCC breaker.
70b37a8b-1fee-430c-96b4-7f6dda46cf2b | checkpoint | Prove electrical isolation
74bda93f-4e14-48a1-a22a-c4372ea270ee | checkpoint | Verify operation of local control station
6e25ddd8-8fa0-4da8-9911-519f418f9a86 | checkpoint | Rotating parts guarded
935a37b0-d96a-4b37-a386-d8a912ed9537 | checkpoint | Confirm motor frame earth
75952ee2-a29e-4e53-b94f-fdfb43d666f6 | checkpoint | Confirm motor alignment checks completed
6888251b-44a7-4c74-af1a-83dace4ea3d7 | checkpoint | Confirm motor is safely uncoupled
06a6718c-7ab5-4ac1-a596-1cdeb6b2e6f2 | checkpoint | Record frame earth continuity
31d5ba12-cc8c-504a-b2b9-5850212c1d31 | textbox | Ω
6debdb43-2532-4c99-933c-f81fee797e34 | checkpoint | Confirm motor lubrication
2adadc95-0d19-460e-90d3-56a403bbea62 | checkpoint | Feeder protection settings match motor (record in Tests section below)
5dd73770-e552-422d-9f57-0916aced9c23 | checkpoint | Emergency stop
61ac86c7-660f-4b22-b000-f41d48a1574a | checkpoint | Circuit earth fault
2e6b409b-c583-4e6c-a82d-8089eed58624 | checkpoint | Motor oil temperature trip/ alarm
00a0d15e-bc16-4775-a3c7-5947018b6040 | checkpoint | Motor winding temperature trip/ alarm
cd058f56-0d87-4602-a469-dfb2e1eff13e | checkpoint | Local stop
6a9e9538-ac33-4697-a4ff-8ea39d6372d8 | checkpoint | Remote stop
4b9ec02b-0421-4fa4-a283-709369563cd8 | checkpoint | Phase differential trip
2a8a18de-9eb4-42a4-83e4-8ecdadf86b74 | checkpoint | Duty/ standby
c261a343-672c-4217-a690-534ae52d8da5 | checkpoint | Other:
c989ece1-1efe-5dd8-8069-b8c0ba0dd061 | textbox | (specify)
86fa497f-566a-47b1-beef-1e8272a7aa59 | checkpoint | Verify motor rotating in correct direction
5a36e476-aac4-45c6-860d-b6177714d644 | checkpoint | Verify motor local stop
90137c19-d378-4b54-a966-b5dcd1c497c5 | checkpoint | Confirm run up time
72efc392-889a-4e3a-a270-c90c27edc2d1 | checkpoint | Verify DCS/ remote stop
b7141386-3a93-47ae-9f2d-5c7e75f65e73 | checkpoint | Confirm starting current (as required for larger motor KW)
0501702d-1e3c-4029-a4ea-4401ae10fdce | checkpoint | Verify trips and interlocks as per above control circuit function tests
8bb71990-771f-4e48-bdbe-1f6fd1adc8ff | checkpoint | Ensure all temporary links/ forces are removed and isolations re-instated/ locked out
b7b503e0-b7dd-41d6-a61e-a7879f2df100 | section | Tests
264bbe8e-f076-4853-8b4e-53a18cd5ba2c | checkpoint-no-value | As required carry out no load run until winding temperatures stabilise and confirm vibration levels. Enter "N/A" for non-applicable fields.
f83879be-ca9d-4a46-9111-b4ee701c8286 | checkpoint | Record Bearing Temperatures:
e1d57482-6708-5e94-85b9-0da3a3c10ed9 | textbox | DE: |  |  | °C
bbb27d96-8c49-5d48-9797-84e96def48de | textbox | NDE: |  |  | °C
f3a45497-9d13-4132-b2e6-8f5d20e1c7db | checkpoint | Record Winding Temperatures:
d35d09af-b35d-5aea-8a35-2f5f35eb7229 | textbox | W1: |  |  | °C
d80a14e6-1a58-5de6-b23f-5dabcf100dc9 | textbox | W2: |  |  | °C
4e893de9-4cd4-59ab-869f-10e09167b29a | textbox | W3: |  |  | °C
43a6a86a-42e2-43ca-81ac-6792918d5f78 | checkpoint | DE(X)
90fa1811-7948-541f-986a-e9871bb80cfb | textbox | DE(X): |  |  | m/s2
b95a2666-41d7-4efd-b781-7c8f28b8b09a | checkpoint | DE(Y)
73d54826-8e71-5d20-a2c2-d06cecf40853 | textbox | DE(Y): |  |  | m/s2
de218620-4751-4859-9492-8c6bf74ec33a | checkpoint | NDE (X)
6edf5667-bdd8-5db1-b0d9-64904669927b | textbox | NDE (X): |  |  | m/s2
347fa9c8-8b96-4ed1-9cc2-e5cba00389d8 | checkpoint | NDE (Y)
baceecbd-b9e0-5017-83e8-1c7fdeb233e0 | textbox | NDE (Y): |  |  | m/s2
6ab93c4a-3419-4637-b82a-6c5d97733925 | section | VERIFICATION
9d71c770-77d5-4a47-bc97-4995172fef77 | checkpoint | VERIFICATION
652423d6-ff37-5982-b0fc-df7c2fdf3f5f | textbox | Deficiencies Identified:
b6987634-15d6-558e-b9be-461d3cf6b393 | tickbox | Rectified/ Closed-Out
77e9b2e1-b351-5251-9a1e-932829a2cf5a | tickbox | Punch Listed
455dd97b-b51b-40e1-9c6b-d0db479b10b2 | section | ACCEPTANCE
72a907de-6f4a-4913-9773-b5e6e1673c46 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications and standards.
1306ae2d-3bf2-4378-98f8-d29b8f88de31 | signoff | Add Signature
d912b578-ca67-486f-8c08-9edfad494912 | checklist | 561482-DOW-ITR-EL-0007 |  | 561482-DOW-ITR-EL-0007
cac754be-7e65-43b4-85f9-7128a8bb3997 | section | GENERAL DETAILS
eb9148fd-533d-4aa0-9d52-6289e4d08366 | checkpoint-no-value | GENERAL DETAILS
701bff04-a190-5d99-956f-ffdf0e2144f6 | note | ITR Number: 561482-DOW-ITR-EL-0007
53e78519-a205-5c5b-816b-37b2410c56ae | note | Project Name: Pump Station Renewals – Silverstream Pumps
944b671a-f3fd-57d2-b3c6-82d99b102332 | note | Contract/ Project No: 561483
b9a3d1ee-f47e-5a53-b2d1-1ff5bf7dc684 | note | Area: Pumps
d80d7634-4f85-5aa1-ad97-f79a842ebf2b | note | Discipline: EICA
58903ed0-cb82-5b19-b0e2-84dcd54b3f97 | textbox | Reference Drawing:
2a15ef8e-9a87-5701-9031-d7e59cdf912e | note | System Reference: Pump 2
e1797feb-bac2-531f-82a1-0a8dcd865de0 | textbox | System Description:
e0001b21-4541-52c2-98db-30379e0d68ce | textbox | Motor Size:
1b1dbe68-a9da-59d9-b081-eece4049b4d9 | textbox | Motor Brand:
9cf7619f-920e-594e-9276-3b947279ff96 | textbox | Motor Serial:
9eab5500-a5e4-5110-969b-5ee77b62766a | button | Motor Connection: | Δ,Υ
57236e2a-fc46-5bf3-a215-cee7e76b482b | textbox | Tag Number:
61063a8c-6d32-5c0f-81b4-087f49758867 | note | PAU/ Skid Number: N/a
177bb7ba-684e-4c4b-892e-45d54053602e | section | INSPECTION - Completion Verification
6a246d22-e8de-4e0b-9b9e-0d6751d44924 | checkpoint-no-value | Equipment, sub-system or system to be function tested during pre-commissioning must be subject to safety measures including, but not necessarily limited to: SWMS, Notice of Energisation, erection of safety barriers with warning signs and an open communication channel between testing personnel. Energisation and site acceptance test procedures are to be conducted with subcontractor/ supplier representative(s) as required.
70dc5dd2-c61d-4316-9266-276021c6e3bd | checkpoint | Cable test and inspection completed
968f0e35-58a1-480d-af7c-49525ea87426 | checkpoint | Motor switchgear ITR completed
6675c79e-bec4-4fba-b31e-78421b1eb320 | checkpoint | Punch list "A" items completed from cable test sheet
8d59fb9e-fd2f-4609-ae21-ad5e02d7f0a5 | checkpoint | Hazardous area check sheets completed and accepted
e29b1754-4a06-4a18-81b2-4af21c601541 | section | INSPECTION - Equipment Specific Pre Commissioning
041b85a0-1a54-4f41-8363-2528ead5c738 | checkpoint-no-value | Ensure interlocks are healthy (force status/ link out). Apply control voltage to motor starter circuit. Verify control/ trip functions. Ensure motor is safe to start – close MCC breaker.
80f4b3ed-52ed-4afb-90f8-860b9260292b | checkpoint | Prove electrical isolation
f4dbbf7b-75e4-4742-bf2b-29f6266d1c59 | checkpoint | Verify operation of local control station
ad5e0c0f-c13f-491f-98c0-e103813125e0 | checkpoint | Rotating parts guarded
31041332-75ca-44d6-bace-207e9d350611 | checkpoint | Confirm motor frame earth
b9b355b0-ec33-49f0-9b58-156767cb9332 | checkpoint | Confirm motor alignment checks completed
ea974410-3247-4c3a-b827-9d748bee622a | checkpoint | Confirm motor is safely uncoupled
c2dfa169-6064-4482-977d-2037b9d31092 | checkpoint | Record frame earth continuity
cded1638-a89f-5ac0-a0f7-554f099e04fb | textbox | Ω
4ed90b62-b5b3-4069-91e1-7197547da5bc | checkpoint | Confirm motor lubrication
12efd11b-0f62-43a1-8268-cbce6ba97d2a | checkpoint | Feeder protection settings match motor (record in Tests section below)
1a1a817a-3666-41bb-bf91-fa25bf93a606 | checkpoint | Emergency stop
fa9f281e-b4c6-4f14-9a47-387d26254eb6 | checkpoint | Circuit earth fault
e59f399a-b9af-40b8-bdf9-305ae7ff25ee | checkpoint | Motor oil temperature trip/ alarm
a389dfe8-1f40-4ac3-a6a5-ea345625edf5 | checkpoint | Motor winding temperature trip/ alarm
f7391516-8feb-4876-8753-ebc92f84b7da | checkpoint | Local stop
7c1a56fe-0e6e-48c0-b5b1-a4ba6cf43d68 | checkpoint | Remote stop
70680a5e-cf59-4292-ab31-5718e8c95eab | checkpoint | Phase differential trip
de08297c-eefb-4fa7-a4e6-8f612451c2b6 | checkpoint | Duty/ standby
7c2aee38-cf98-485f-a099-c438e8ea5613 | checkpoint | Other:
bc18d56d-f2c9-5086-94a1-c719f245f8db | textbox | (specify)
6d08dab8-bf18-418a-9d96-12ed27c8c460 | checkpoint | Verify motor rotating in correct direction
39f9ab96-f3b6-4cf9-9d09-2269789bd687 | checkpoint | Verify motor local stop
398b103c-3301-4c7a-ac55-e0a345cc3095 | checkpoint | Confirm run up time
83a72e07-c97d-43a3-8e1d-1c3b9d9ffe58 | checkpoint | Verify DCS/ remote stop
ffdc2160-b037-4d78-a0d0-f19f53780739 | checkpoint | Confirm starting current (as required for larger motor KW)
a98502f6-e39f-4d09-8de2-2dd12adf8941 | checkpoint | Verify trips and interlocks as per above control circuit function tests
e1e0ab94-bbb2-42ba-ae69-63c14f0cdddb | checkpoint | Ensure all temporary links/ forces are removed and isolations re-instated/ locked out
689a928f-5665-4d2c-a36c-168cb9c2e2e8 | section | Tests
81db4e7e-6e50-4af1-872c-8e3af40e03a0 | checkpoint-no-value | As required carry out no load run until winding temperatures stabilise and confirm vibration levels. Enter "N/A" for non-applicable fields.
7ab39cf5-f24b-4fcf-93d7-bf7efa75c48e | checkpoint | Record Bearing Temperatures:
5c766991-6aa7-5165-b24d-6dc78668249b | textbox | DE: |  |  | °C
2332986d-3579-55d2-960a-b92a0b76b58c | textbox | NDE: |  |  | °C
a183b037-30ee-4655-9f67-8a75a1748eb7 | checkpoint | Record Winding Temperatures:
806efdf1-4750-5707-abea-6759df9700a6 | textbox | W1: |  |  | °C
df660a57-6edc-5ed9-9f5b-c4150f0c191c | textbox | W2: |  |  | °C
cc840543-5cb6-5ffd-96eb-a17553638774 | textbox | W3: |  |  | °C
c1359a0d-16c9-4299-88ed-bdd63f323e99 | checkpoint | DE(X)
d3b7c29e-78f2-5457-a9d6-a4af442188cd | textbox | DE(X): |  |  | m/s2
1681815b-4b15-4919-b026-88e93aad5c94 | checkpoint | DE(Y)
3a7caed7-d851-5cf8-87b7-6e11af6fe18b | textbox | DE(Y): |  |  | m/s2
7011fb01-8e84-4a5f-994b-080fd0c3282b | checkpoint | NDE (X)
26135479-0910-54c4-b9a5-88ad8db5c2a7 | textbox | NDE (X): |  |  | m/s2
04d0e307-1ae4-468c-94d0-952789d129ed | checkpoint | NDE (Y)
2a2d7cb2-37fa-5aae-85fb-b225e83a29a0 | textbox | NDE (Y): |  |  | m/s2
7082f193-7f56-4405-bfbd-404a6fec7f8e | section | VERIFICATION
2f79f263-1b2d-4a55-8968-eef53dcb31dc | checkpoint | VERIFICATION
9f349ab1-936b-57f9-ae41-e1ab1f4a6fae | textbox | Deficiencies Identified:
9b5bd0cc-5c32-57d6-8fd7-29de1bd4c693 | tickbox | Rectified/ Closed-Out
7dce7432-5e1d-5fe7-94b3-23452a3a5e89 | tickbox | Punch Listed
282b09c2-9840-42a0-8b67-af131277d4a6 | section | ACCEPTANCE
29492c7a-05f1-49c7-8680-d02fc02457a0 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications and standards.
e50d8934-35e5-454e-abfb-fc0a40acfbe2 | signoff | Add Signature
ad261d07-6d8b-4543-8cb4-32f684eb4b66 | checklist | 561482-DOW-ITR-EL-0008 |  | 561482-DOW-ITR-EL-0008
3870ca2f-b1df-4045-9e4b-c59e59195deb | section | Details
e1dd6d65-8877-4ada-bae3-ff9f11718076 | checkpoint-no-value | Details
8d9e3082-41cc-59ca-9216-e5f159aeeba9 | textbox | Area (L0):
a341fb38-cd94-5607-b693-265ac9de3ff9 | textbox | System (L2)
072d79e9-3e24-5b73-8a3b-38ff79f802c2 | textbox | SubArea (L1)
f1b68282-ec38-53d0-b7a4-d3aa9a570591 | textbox | Element (L3)
e7c1da0a-b227-4fde-b3a8-1cc428b636fd | section | 1. GENERAL DATA
cbc0320f-4f3e-461f-ada4-b233a739ac4f | checkpoint | Details
f0f2247b-3f56-5b8b-b4ec-b30b4367a810 | textbox | Schematic Drawing
25aa37b0-2faa-59ad-99c4-7baa6c16346c | textbox | kW rating
2b1efcaf-fa5e-57e2-ab15-fbdc7a35b611 | textbox | Manufacturer
3399beaf-fff4-5751-bf95-06f427beca36 | textbox | Model Number
bc5c587e-59ae-5ac0-ad8a-0ee1125083b9 | textbox | Serial Number
89afee9d-1a0c-5193-a5e4-15f8affa3eed | textbox | Supply Voltage
dfa5234b-f2b5-58c1-9b8c-d01267f1113b | textbox | Supply Label
a01dfa51-90ed-5804-b3b3-a82ceae7f4fd | textbox | Control Label
e43715da-9395-47df-bf3f-735c9d8a770c | section | 2. TEST PROCEDURE - 2.1 Readiness for test
60a2cdf3-ee9c-4203-ade6-5f4f30ee5a0d | checkpoint | Drive power isolated
8d4e11b3-ff2f-410e-b34c-a2ca3f9136b0 | checkpoint | Control power connected
c4ed4e0d-3675-492e-85f6-9b4df53f08ca | checkpoint | ITR completed and signed
a43afd6e-a11f-461f-9faa-ed3fe033c1c6 | checkpoint | Area signposted & controlled
a318e9bb-9728-4041-b612-1b9d8fabf1a9 | checkpoint | All field IO Correct
ee73e466-2008-490d-95fe-c024fd972ec3 | checkpoint | 24V DC supply energised
2bcc4876-8022-46ec-b02c-701c0d631182 | checkpoint | Confirm potentiometer rating
837a311f-696f-448b-a70f-5781e63859b1 | checkpoint | Mechanical Installation as per Fig 1
fd4f9568-bdc7-4346-8201-8d28f550caea | section | 3. COMMISSIONING PROCEDURE - 3.1 Configuring the VFD
4db0c60a-d3c6-44c1-96d8-c23c2c878a7b | checkpoint | Verify DI1 is not active
6ee9597a-9200-4429-87ef-5543c3a36adb | checkpoint | Energize VFD
90d73cd4-c95d-43bf-970a-17c590ab361f | checkpoint | Set Date/Time/Language
22298cc8-b6b9-4595-9aba-232fd4f87118 | checkpoint | Select Simply Start (1)
effff162-d24d-406c-98db-8253f3cd43f5 | checkpoint | Motor Standard Freq
07096810-1127-5360-a863-02389eaa43cb | textbox | Hz:
afc42dde-4909-4a53-8320-f23fce67b2d3 | checkpoint | Nominal Motor Power
2155429f-26fb-5edd-ad06-415a32b9a731 | textbox | kW:
3aef6d35-782c-4860-a2dc-007b2218f73f | checkpoint | Nominal Motor Voltage
c6eff14e-c9ed-5333-8c81-cb98f3fd0908 | textbox | Vac:
a2776927-ae3f-4d6b-aa39-326e2f3a3652 | checkpoint | Nominal Motor Current
51d99b3b-23e8-5d73-bdd2-b3dc4cc7b5ce | textbox | A:
86b29121-90f1-487f-aabd-11c90a536f93 | checkpoint | Nominal Motor Freq
ad810abc-a264-59ec-9fee-1678f1f09f8d | textbox | Hz:
e21da687-708a-4ba0-9667-4f2a6d36aca1 | checkpoint | Nominal Motor Speed
ec7b09d0-424b-52e2-bcba-f4d56aeb71ca | textbox | RPM:
41f9ce42-de23-4ba0-bdbb-d94d64315604 | checkpoint | 2/3 - Wire Control (2C)
3f2a15ed-e1c3-4ffc-b67b-67be532beeab | checkpoint | Maximum Frequency
1cd87fb8-821e-5c10-a274-51425c950a6f | textbox | Hz
f8de33a5-59f5-4930-b1e9-f66a00176142 | checkpoint | Motor Thermal Current
d42e76f2-c745-541e-b2d2-18dc728dc75e | textbox | A
20e37049-2b4e-426d-ac5a-8753fe46a135 | checkpoint | Clear Area of Personnel
6a07690f-7f1e-43da-b9d1-64ad9f49e8b6 | checkpoint | Select Simply Start (1)
63867f9a-1a44-43f3-b40f-212f13ff58a8 | checkpoint | Select Autotuning
319d8e8a-5fa3-4695-b429-6a1339453f12 | checkpoint | Set Apply Autotuning (Yes)
d9ff57c8-1316-440f-b908-179e8a687b3d | checkpoint | Select Simply Start (1)
c593c0e5-f671-43c2-956e-04cdcabb90c0 | checkpoint | Set Acceleration
be27c3ba-e1e1-5fad-8277-bca04dc7d8eb | textbox | s:
6ea66ab0-d621-4a77-8a8a-a52a495ab5a2 | checkpoint | Set Deceleration
30635265-3f8a-572d-90b5-4fe07acf8604 | textbox | s:
0dd379c1-339e-4980-ac24-c9faf1fcf417 | checkpoint | Set Low Speed Freq
1c9ef998-c12f-5b64-af4b-e508ef236d35 | textbox | Hz:
93c7b644-39e7-4b5d-8877-a8e4b235905b | checkpoint | Set High Speed Freq
f3e69f4f-ae12-577f-b54a-1045acd7a9c3 | textbox | Hz:
68c53d88-c023-4fb4-ab74-9ad8b2357b00 | section | 3. COMMISSIONING PROCEDURE - 3.2 VFD Module Tests
4085babf-361e-4e56-a9bd-d51764dfcbb7 | checkpoint | Confirm VFD starts/stops
5283d796-90ca-43fe-8c67-c246deb29041 | checkpoint | Simulate Overload Fault
b277497e-206f-43f3-b3c9-587ad766dc8c | checkpoint | Reset VFD
87f9dff0-e8c1-4768-ba4b-bfb12eec8dca | checkpoint | Confirm comms VFD-PLC
93ef8252-7291-426c-8a26-fb2f142b74de | checkpoint | Inputs verified into PLC
301a5027-048a-42c7-b51b-f9d94c81d34e | checkpoint | Outputs operate as per design
cee59dc4-e1d9-4165-85e9-19d67b6f586e | section | 3. COMMISSIONING PROCEDURE - 3.3 Other Tests Conducted
bea7d49a-0807-443c-bb97-f63882220e13 | checkpoint | Other Tests Conducted
8f85c4b5-bd99-5d7c-9fec-2df8f213ff89 | textbox | Details:
4ff38fcc-a373-4e07-9acc-11296a075b45 | section | 4. COMPLETION
a3aa7906-0997-4536-a12c-111c84d61338 | checkpoint | Temporary supplies disconnected
453b4aa5-ca2f-4142-8a57-b777d8d36602 | checkpoint | Temporary bridges removed
690bc41d-9be9-469b-9635-206093e087db | checkpoint | All covers reinstated
3a706951-dc94-4b5f-b566-a17698f8dd47 | checkpoint | All equipment left in fit state for energisation
db1dbebc-2f6c-4987-803c-8297ba31252c | checkpoint | As built drawings marked up
36442067-c2e1-448b-9b52-04788067601e | section | 5. REMARKS OR REMEDIAL ACTIONS REQUIRED
ecdf8955-0af9-4e4c-a749-11e545caae68 | checkpoint | Remarks / Remedial Actions Required
0e516f12-c7c2-574d-9737-a7e220c478c2 | textbox | Punch List ID
07f11961-ea38-5c28-b974-f0b7feb467d1 | dropdown | Priority (A/B/C) | A,B,C
c855e389-4fb4-509b-b608-d1cafa7b64b1 | textbox | Description
de694f35-c556-5d10-aa1a-68b98b513839 | date | Date Due
7427c2a0-8c27-54e1-a44d-50315215ba1b | dropdown | Responsible Team (M/E/C/P) | M,E,C,P
bb853d1f-d53d-40c9-90b1-5471409627b2 | checkpoint | Remedial Actions Completed
a52f501e-7809-5544-aa60-8939348f52cf | textbox | Commissioning Eng/Tech:
0bc2e917-6058-5bb2-a2c1-54b6ca3e6fe0 | textbox | Commissioning Manager:
2421c67b-cdc5-5f89-ae06-1b7f43223661 | textbox | Client:
5cba6d8b-3830-45a1-8b64-4f836cc99bf6 | signoff | Add Signature
0bbfb344-a72e-44be-8481-7ac4e8a51d93 | checklist | 561482-DOW-ITR-EL-0009 |  | 561482-DOW-ITR-EL-0009
50d7a6d4-faf2-43eb-93b1-b7651a37ed4e | section | Details
43b48396-3b1c-4f9b-b6d7-c53bc7d55405 | checkpoint-no-value | Details
2139a0cb-f61d-530f-9787-da73e093447a | textbox | Area (L0):
1fef3661-1bf3-539d-aca9-00f575ac8810 | textbox | System (L2)
bc4e5499-0503-5db1-b030-64d3165a12f0 | textbox | SubArea (L1)
1ffe3d0b-22f1-5710-bcd7-65abf288da9c | textbox | Element (L3)
6c1fb1aa-2bf3-4325-88e8-1d0fb53cc3fd | section | 1. GENERAL DATA
76a87abe-c278-4e6e-9826-cc1ffba7c8b6 | checkpoint | Details
2ab7eac1-b7b4-588d-9ca8-4b8122ff1c64 | textbox | Schematic Drawing
a66e3672-7ace-5e7a-881a-6f729c44b5ee | textbox | kW rating
a2760915-434d-549d-9e6f-2185ac6c39b7 | textbox | Manufacturer
9eac25da-24c2-58ba-8fbd-a98fe6e7ee2a | textbox | Model Number
ff4bc051-a8ab-5e13-a8fd-3bcf492f92c6 | textbox | Serial Number
a820276a-e87f-5ce4-baa8-3a53425b6745 | textbox | Supply Voltage
f48d91b7-feff-5fb9-8229-4c24aca3c3e0 | textbox | Supply Label
6a44e370-a97f-58c9-8074-6132fa4ff775 | textbox | Control Label
d4126cd1-8c87-4954-a0ab-53547378c533 | section | 2. TEST PROCEDURE - 2.1 Readiness for test
2b44e95e-af83-406b-8210-58cbfab0b9ae | checkpoint | Drive power isolated
cbec878b-f4c1-40d0-9e97-6ceeba14ad79 | checkpoint | Control power connected
d41c6253-b939-413a-8dd1-854d1f5ebdc5 | checkpoint | ITR completed and signed
3c8873fc-e631-4f3d-81db-1728faaf40fc | checkpoint | Area signposted & controlled
25370002-35f9-4ec5-a035-786a942441e1 | checkpoint | All field IO Correct
5e83c2d6-e714-4d7e-88ad-92f94a8a3c31 | checkpoint | 24V DC supply energised
7c1f39d6-a6ba-4f80-b423-1e57b12140ec | checkpoint | Confirm potentiometer rating
63bce948-b757-4329-ab71-49561573eeca | checkpoint | Mechanical Installation as per Fig 1
b49e7e5f-cd06-4925-8fff-955b319e5402 | section | 3. COMMISSIONING PROCEDURE - 3.1 Configuring the VFD
3e1ae047-3a17-4bf8-97e8-a4e61ff97ad8 | checkpoint | Verify DI1 is not active
1e57cfb3-8aa7-4106-84b9-8cb1d6dbdd88 | checkpoint | Energize VFD
90f29ba8-ef1e-4dfd-bf7e-5ba96fb2069b | checkpoint | Set Date/Time/Language
ac97e6bd-95df-4515-a0c4-7b869f62afd9 | checkpoint | Select Simply Start (1)
d4430946-cf59-4587-8980-e8bc8f8154a4 | checkpoint | Motor Standard Freq
73b37ce8-5a00-5a98-8f3e-6aeff7ee10ac | textbox | Hz:
ee868f6f-9a6f-487e-a315-b62315504769 | checkpoint | Nominal Motor Power
8bf6d220-7a0c-55ad-8458-16073f5d5c7d | textbox | kW:
d2725c49-2517-45d3-91f3-cbed9a28f151 | checkpoint | Nominal Motor Voltage
1a8616a1-b1dc-52ed-a398-50009d58924e | textbox | Vac:
399e5338-d626-4def-a99a-2b3db796a838 | checkpoint | Nominal Motor Current
f1cf777c-46c1-5773-94cb-63d157ad5d6a | textbox | A:
21abd509-66f9-42ae-a293-4be83bfa64e7 | checkpoint | Nominal Motor Freq
170fb2ea-da54-5e20-87fe-93f9d20e7981 | textbox | Hz:
4ca0e874-1d28-4788-bf61-a603b7daf44f | checkpoint | Nominal Motor Speed
4a9428b6-3314-522f-a746-c0da41769167 | textbox | RPM:
bade61db-a501-479c-bfd2-67770e472b61 | checkpoint | 2/3 - Wire Control (2C)
bb51c4f2-e909-4987-a26a-08c2bac6d50f | checkpoint | Maximum Frequency
77b80ed3-a4eb-5989-98ca-a3576df1ba57 | textbox | Hz
4cd77968-eeb8-4e12-ad7f-2107519c0c79 | checkpoint | Motor Thermal Current
59e0183e-7ee2-5edd-8092-fb34677cb1c0 | textbox | A
638e2f21-5cca-420a-833c-e96295d55171 | checkpoint | Clear Area of Personnel
b93e6da3-80cd-47df-88ec-d48c3edd98f8 | checkpoint | Select Simply Start (1)
5854fe90-ef21-4ad9-8f32-d6de813737d5 | checkpoint | Select Autotuning
9cf31dc3-b54d-4581-9790-a51b37c64d08 | checkpoint | Set Apply Autotuning (Yes)
528d2b78-41b1-4087-8be6-46af24566a21 | checkpoint | Select Simply Start (1)
df571b15-d169-4b7e-a753-351d0152a901 | checkpoint | Set Acceleration
f0307097-9636-5c4c-9a97-d3c1b8713fd2 | textbox | s:
d2fc871e-463c-4817-b4c6-68e34babee30 | checkpoint | Set Deceleration
8314ff91-f0f9-522d-9897-61719d60cd32 | textbox | s:
5541c355-487f-40df-a732-483c3d892725 | checkpoint | Set Low Speed Freq
4f931db6-e097-56ec-897d-df2fd1e6acb0 | textbox | Hz:
e0d03578-1c21-4b90-b4b5-7989f8406372 | checkpoint | Set High Speed Freq
09e73285-cc93-55e6-a2fb-da01dc92722b | textbox | Hz:
8e7f5e67-9dbf-4aad-8cc9-65b8dc918c87 | section | 3. COMMISSIONING PROCEDURE - 3.2 VFD Module Tests
cca4f358-edb8-441a-8d2a-da665a4ff67a | checkpoint | Confirm VFD starts/stops
36683af4-6bc7-42ce-80dc-8f504b4e1592 | checkpoint | Simulate Overload Fault
c7baec75-dea8-4793-bceb-89baba6a8f83 | checkpoint | Reset VFD
7f7cee46-33c0-4e0b-a703-d200124238cc | checkpoint | Confirm comms VFD-PLC
ee60ec27-83f1-4fa8-a161-4d8e417f6871 | checkpoint | Inputs verified into PLC
cbfe810b-f7d3-405f-83b7-c74a07e3827c | checkpoint | Outputs operate as per design
9e2b65af-f211-4c97-b927-23a43dbd2fff | section | 3. COMMISSIONING PROCEDURE - 3.3 Other Tests Conducted
45cbbfa2-41a0-40c8-8dc9-59a663bb3707 | checkpoint | Other Tests Conducted
88d804a5-355a-5351-9a75-945ff3456bb3 | textbox | Details:
b32d7b87-5703-45c7-9675-13832379db0c | section | 4. COMPLETION
ab02d63f-c3a1-4b55-897f-d17a529d2288 | checkpoint | Temporary supplies disconnected
20d8a938-d68c-45de-91be-ff6f1ad07e25 | checkpoint | Temporary bridges removed
8fb8c2dd-5054-4e0a-b99f-359969ea3797 | checkpoint | All covers reinstated
f74c4417-c308-4418-925b-705318619587 | checkpoint | All equipment left in fit state for energisation
fcd85849-cc56-40d0-b7e5-68feed82a99a | checkpoint | As built drawings marked up
8c162b81-feab-4b3f-8018-095de6b66bc5 | section | 5. REMARKS OR REMEDIAL ACTIONS REQUIRED
813b815c-05ee-45d3-9f02-239f1d2f9d80 | checkpoint | Remarks / Remedial Actions Required
5cfd1b9b-5791-5e27-8e0e-32d60ae0c3b4 | textbox | Punch List ID
c51629d7-d63e-53d3-afa2-7f06efa34a11 | dropdown | Priority (A/B/C) | A,B,C
c76922de-0059-59cc-b715-4d61218897cb | textbox | Description
bd7210b2-c1d0-5461-a098-379358fe0e39 | date | Date Due
473ee54e-3fe0-543f-b84f-1393e9d89811 | dropdown | Responsible Team (M/E/C/P) | M,E,C,P
43b0a5a2-624a-4648-9830-94dabd486bd8 | checkpoint | Remedial Actions Completed
9e4c36b3-4005-5cd7-9b9c-b08a08908201 | textbox | Commissioning Eng/Tech:
5e3a67c5-7a3c-5da7-bf93-19991945c045 | textbox | Commissioning Manager:
483aa056-fb0a-5660-adbb-eacf70b8773f | textbox | Client:
de0b5e83-9163-4a36-9332-d05583779d6a | signoff | Add Signature
4d5bb36a-786a-4248-8b37-e5641ad3db54 | checklist | 561482-DOW-ITR-IN-0001 |  | 561482-DOW-ITR-IN-0001
6a7a1693-db9d-4b03-8bc6-b686a8b8bf8f | section | GENERAL DETAILS
561cd45a-993c-426c-9f84-1ba23b507a2d | checkpoint-no-value | GENERAL DETAILS
d9159949-8531-5e52-80cf-1f17a1dd1b87 | note | ITR Number: 561482-DOW-ITR-IN-0001
659aae97-3366-5589-b14c-8f7303a00c58 | note | Project Name: Pump Station Renewals – Silverstream Pumps
4564da58-e07d-568b-a375-c39e67def544 | note | Contract/ Project No: 561482
24e08815-f061-5c3b-9a54-a2faed4a64df | note | Area: Silverstream Pumps
a559bb91-6c98-50c0-990f-7d3c57b8a010 | note | Sub-System: Pumps
8e007d20-ef7c-55c6-bb44-2200903445fd | textbox | Reference Drawing:
e70ea651-7077-573e-b074-13630e6fd995 | note | Discipline: EICA
20e29fbb-6485-5f68-9eb4-4a2173984446 | note | Work Pack Number: N/A
216a58c1-f192-522d-a054-09d6385f6045 | note | Lot Number: N/A
c1b85383-e89e-5749-8db3-afebc0c5c88b | note | Cable Number: TBC
2ec85410-1880-5da6-9b6c-29bf620a0dd5 | note | Cable Specification: 1.5mm 4 pr CS
29afad37-fce9-5b50-93df-64c54a98eebd | note | Source: MCC
6feb263a-5405-58ff-91a7-61d411312d59 | note | Destination: Pump 2 VSD
4a832a9c-05d6-558c-9008-72fd7246c46f | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
7d0d5458-b8e4-44ba-a39d-ca015f9164da | section | INSPECTION
1fa7e4d0-2a14-4152-af1b-15b0d2cbf019 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
bd2f5c5a-a660-414b-8bc9-be64fc502a48 | checkpoint | Cable size and type correct
d717def2-f748-438e-9ccf-cef8b044461a | checkpoint | Cores terminated as per drawing & terminals tight
8d5dcb7b-412e-43a6-b962-dab896db4ba5 | checkpoint | Cable numbered correctly and applied at both ends
a3c4a50c-0448-4f21-8df3-05cbf4564385 | checkpoint | Permanent core markers attached both ends
406c7c5d-0926-47d4-a88a-7b8c216e4894 | checkpoint | Cable supported and protected as per specification
0ff3ca8f-1750-4a5f-a599-5c27cd0b5128 | checkpoint | Continuity of earth conductor/ screen satisfactory
a10cdd38-3aee-45c5-ad9a-84a4856c7cc8 | checkpoint | Cable ties trimmed
a424a2b4-6a3f-437c-b718-139270139fef | checkpoint | Connection of shielding/ armour as per drawings
6984c27d-1b58-4769-b813-8856307dfe98 | checkpoint | Cable ends made up satisfactorily
bd839e4b-00ca-43ce-b677-d5b87de40585 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
27d07bc4-4519-432e-8cef-92d362930efd | section | Field Test
83f5f31a-7666-4079-a580-fac73c09571f | checkpoint | Field Test
2b943409-38fb-5133-8a58-52861b966026 | textbox | Core Designation: W1 |  |  | Results - MΩ
a94a7e41-b522-51e6-ab56-2b7fa22e6771 | textbox | Core Designation: B1 |  |  | Results - MΩ
e871d816-a801-5f95-9734-a451d87aa42d | textbox | Core Designation: W2 |  |  | Results - MΩ
99eb9c0b-1425-5d70-96c2-b034edfb5f1b | textbox | Core Designation: B2 |  |  | Results - MΩ
76892278-24e8-5901-a44e-8adf9f302dbf | textbox | Core Designation: W3 |  |  | Results - MΩ
897c7891-aefb-56c5-b62e-471057179c9c | textbox | Core Designation: B3 |  |  | Results - MΩ
08497411-9ff3-577d-b66f-8a062060e877 | textbox | Core Designation: W4
7fff2ad7-e73d-58e6-be7e-d533cebbb8e6 | textbox | Core Designation: B4
d8c04478-b10b-56d2-aad4-535887aedf1e | textbox | Cable Size:
8b564774-420d-5ece-ae88-f9012a5429a8 | textbox | E Continuity: |  |  | Ω
afa4d93e-0c3b-5fb0-a421-f45e00fe1c13 | textbox | Lead Resistance: |  |  | Ω
ac0a952d-4cab-4f4f-9d63-6e322633810a | section | Completion
9f07a819-05d5-4724-ba96-77e36042ab4e | checkpoint | All cores reconnected and secure
e305813c-51ae-412d-a710-2e2670cbe79f | checkpoint | Source connection tension
72305437-b219-5aae-8ab8-64c644a5d495 | textbox | Nm:
04b3996c-96a3-4b2e-87a4-01f67c38650a | checkpoint | Destination connection tension
2795410b-489f-5aea-bd6b-d2ab87a66689 | textbox | Nm:
66fc5e7d-b134-405a-a42f-9e938e25aaca | checkpoint | All connections visually and physically checked
3a1c5c4c-0328-40c9-8780-25039ab52865 | checkpoint | All test leads and bridges removed
c9a08f6a-e40f-48d0-873c-03483c1ea021 | checkpoint | Drawings & schedules marked up to 'As Built' status
2a9073d4-c9d0-49f3-a5ea-239bfed88d52 | section | VERIFICATION
2ae970a1-3203-4924-bc0f-b73cf33898c1 | checkpoint | VERIFICATION
60f7f3d1-bd2e-5e28-81ca-65d2ad6fbf5f | textbox | Deficiencies Identified:
8ffc9c20-bada-5084-8ddc-67b4799d99c5 | tickbox | Rectified/ Closed-Out
183e2ac8-73d8-59b3-b020-3d9a82022f51 | tickbox | Punch Listed
e06a0399-2b3f-454e-89c4-00629444cf0d | section | TEST EQUIPMENT
07b68738-2068-4459-8604-03a10ab3b40e | checkpoint | TEST EQUIPMENT
2fb1320f-148d-5a97-8203-1bab7bece5f1 | textbox | Type of Meter
7b68c7cf-d4ab-5f00-8026-d3cccd1d373f | textbox | Make/ Model
525a3d10-97d8-5ba9-84e3-366e335a059f | textbox | Serial No.
63a3c4c3-f0f2-5ca2-8676-1a881e7e568a | date | Calibration: Date
de27b52a-3c95-5d94-9df3-f90893d50661 | date | Calibration: Due
f832d243-4b84-4d2a-af8d-508c625e428d | section | ACCEPTANCE
2b1e7d8b-d632-4159-9779-efdcf36a9403 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
45b8f4bb-298a-4244-8eed-58ea04e87488 | signoff | Add Signature
01b1f57a-dee8-437b-9a8d-21837ea264b4 | checklist | 561482-DOW-ITR-IN-0002 |  | 561482-DOW-ITR-IN-0002
ede15603-11b1-4351-99f5-9bce01e94bb6 | section | GENERAL DETAILS
b4c89283-a57a-451a-b0af-bd90d195057d | checkpoint-no-value | GENERAL DETAILS
1fe6ab64-6aaf-5522-842b-6f6d75856b28 | note | ITR Number: 561482-DOW-ITR-IN-0002
5c2935e0-5260-5508-b98d-727438a7d2aa | note | Project Name: Pump Station Renewals – Silverstream Pumps
5754bda8-d6cd-5a27-a8a2-c8fc9cb34259 | note | Contract/ Project No: 561482
dc77c30a-e062-5f18-bbf9-7fa4ea3e35c0 | note | Area: Silverstream Pumps
bf3a38a5-b0c0-5e1e-b0a9-c3ba1d32de9c | note | Sub-System: Pumps
4d4d03d6-45e2-528b-ad25-109cf741bcbd | textbox | Reference Drawing:
6f77f06f-8bd4-58db-80eb-7a08e64fa8a4 | note | Discipline: EICA
d9e33b0d-f596-5444-97fa-e831901914b9 | note | Work Pack Number: N/A
e167bf2e-c1d3-55c6-8e01-8ab9a58f268f | note | Lot Number: N/A
b406f184-a032-5309-bf2a-21549dd6e9ba | note | Cable Number: TBC
7d97fd22-9608-582b-a6fe-e1263a3d46fc | note | Cable Specification: 1.5mm 2 pr CS
df2e3a48-fe58-590a-b09b-5f18a2522e2f | note | Source: Site MCC
b7c3ca81-11c3-588a-ae7f-fb8100e4abe8 | note | Destination: Pump 2 VSD
307ca369-c0d5-5f37-95ef-93b9f13205ca | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
d80451c7-d103-465a-b920-d0c1f55b7098 | section | INSPECTION
ec3e3fa8-7771-4b2a-aa56-291b72ef924f | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
c3bdb05e-ab98-4221-ad4d-d0c1a72d20df | checkpoint | Cable size and type correct
056259fd-b5aa-4e15-a37a-692e1a31fc78 | checkpoint | Cores terminated as per drawing & terminals tight
c93f154b-05b7-4c75-abd0-891d46f0828e | checkpoint | Cable numbered correctly and applied at both ends
da521f7c-c816-4cdc-8863-84e7eb745cf5 | checkpoint | Permanent core markers attached both ends
1e9bb338-691c-4ac6-976b-baacd6344726 | checkpoint | Cable supported and protected as per specification
a143f3a9-b6ce-48de-bfe7-7d7aa8d7490b | checkpoint | Continuity of earth conductor/ screen satisfactory
94b8909a-a436-4e6d-b654-57a38a0a208f | checkpoint | Cable ties trimmed
129736ed-e08d-49f8-a55b-ccfea8a61308 | checkpoint | Connection of shielding/ armour as per drawings
a58199ec-824a-47c6-bd90-8555ef1e9606 | checkpoint | Cable ends made up satisfactorily
65584a61-8c48-437e-b096-8cbb565544ad | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
1f1e66b5-563c-43f7-9983-270f3a1b8918 | section | Field Test
8c351ee2-ca0d-4569-a7c6-eea0d58fb390 | checkpoint | Field Test
41f173ce-4c4a-5cb3-9195-d3b3f0ae147e | textbox | Core Designation: W1 |  |  | Results - Ω
d181258f-bc12-5371-af3a-26ef9781a8c8 | textbox | Core Designation: B1 |  |  | Results - Ω
77e08c45-123c-5d2a-a40d-e4088eec7633 | textbox | Core Designation: W2 |  |  | Results - Ω
f415db8f-16da-5e7d-b4da-9ee0ed242572 | textbox | Core Designation: B2 |  |  | Results - Ω
5217c536-d83a-5a5b-af39-60a41cb3174f | textbox | Core Designation: W3 |  |  | Results - Ω
2cf0a0cd-64ef-5bb3-b5d5-6a71ac8ad3ff | textbox | Core Designation: B3 |  |  | Results - Ω
dd5aca1f-ebbf-5fc7-9d75-4059bce09b5d | textbox | Core Designation: W4
2dfcf83d-8914-5cad-999e-2f92e81f36d1 | textbox | Core Designation: B4
3ede36c8-0c5e-53d7-8c89-68bdb34a91d3 | textbox | Cable Size:
8bb852ea-534c-5729-8c2b-d0815243333d | textbox | E Continuity: |  |  | Ω
44b56d95-c15d-575c-bb53-f8339a0da38a | textbox | Lead Resistance: |  |  | Ω
65840138-2e2c-439d-9fb7-5b523bd0138b | section | Completion
20163f34-cd33-4f39-84db-fcacb3a0651e | checkpoint | All cores reconnected and secure
0b924551-5d14-4fed-a71b-59c058f304b2 | checkpoint | Source connection tension
3fefa81c-e8a5-51c6-8795-d797f847eb8d | textbox | Nm:
aff46f23-6b96-4cef-970a-0c49682ea0f3 | checkpoint | Destination connection tension
174a358f-8cfa-5138-a9a4-9afcd396511f | textbox | Nm:
ec71d410-0dac-4c36-9f96-9b7f1752535a | checkpoint | All connections visually and physically checked
07f25f73-5654-4d69-b70f-3122f586f1ef | checkpoint | All test leads and bridges removed
50304dbe-0bdf-49e9-b874-6dcfa0840638 | checkpoint | Drawings & schedules marked up to 'As Built' status
468c768c-a3a1-44ea-86a7-3fbc6bca3ee8 | section | VERIFICATION
534bfd14-b1ec-48d6-a04d-38a61958337b | checkpoint | VERIFICATION
3e7f3c77-90b3-50b8-8b8f-8436221f5861 | textbox | Deficiencies Identified:
26c20011-a431-53a8-98c4-e5b3a8c28dd7 | tickbox | Rectified/ Closed-Out
1da43e70-0d4d-565a-849a-02bf34e2e2b3 | tickbox | Punch Listed
ecd3154b-0fc3-4785-a892-628de2740c7d | section | TEST EQUIPMENT
bc301692-7eea-4b87-8ed8-e40a70d9274c | checkpoint | TEST EQUIPMENT
91389571-09c9-5061-be64-1e17c63bb61c | textbox | Type of Meter
a09460f5-0678-59d2-80de-d5d66c3c49af | textbox | Make/ Model
d3167935-26e3-5db4-b3ad-a45427b891a1 | textbox | Serial No.
3c1f1247-6039-5d7b-a4d5-4009c7a0f7a2 | date | Calibration: Date
2130dd1a-461c-53d6-b8d1-b58c57dd776e | date | Calibration: Due
4e51cd90-93fa-4d04-882f-af4bbf259930 | section | ACCEPTANCE
1e155ac0-69c2-43c7-9ddc-54273f223038 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
37d486c2-808a-4746-8db4-e1dd70442857 | signoff | Add Signature
9fb641ae-440f-435f-b080-0cb4393b65b1 | checklist | 561482-DOW-ITR-IN-0003 |  | 561482-DOW-ITR-IN-0003
442c5059-65bb-4e7d-89d3-cc710ba172c9 | section | GENERAL DETAILS
bfa8cce0-0aab-42d9-9573-f492bc014274 | checkpoint-no-value | GENERAL DETAILS
7dd2f127-ff92-5167-ad4f-60a86a4ad878 | note | ITR Number: 561482-DOW-ITR-IN-0003
dc149894-2a79-50d9-87ae-770e3d8c2311 | note | Project Name: Pump Station Renewals – Silverstream Pumps
4f5b08da-e1a8-5108-a4fe-4d2474730fae | note | Contract/ Project No: 561482
703243ba-74ee-57b0-87e4-c5d5ba22c9f9 | note | Area: Silverstream Pumps
19228eab-d9ac-55c8-bac9-80cf2cd04fc9 | note | Sub-System: Pumps
365460f1-bc8e-5e84-b6a8-7afb8761b80b | textbox | Reference Drawing:
b8d3cac9-c907-5d4e-99cf-a93f10172839 | note | Discipline: EICA
10199b16-1234-5065-bb10-6fbde2604be0 | note | Work Pack Number: N/A
55cd6836-f9bc-555d-900b-662c19db88ce | note | Lot Number: N/A
a3912e8f-1563-5f75-8752-adb39be5f5af | note | Cable Number: TBC
f4fbb155-d80c-5077-8524-f681d0650db1 | note | Cable Specification: 1.5mm 1 pr ES
fc0425c8-d0fb-592f-a0a5-4fcdcfde3d19 | note | Source: Pump 2 VSD
a83b9965-f214-593f-83e1-32b9e2f434f9 | note | Destination: Pump 2
f9c36d80-97d2-5c49-97de-de655598217a | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
e55784bc-1580-42fb-b45f-82d9bafe629c | section | INSPECTION
547143c7-7678-4837-b59d-b1b2d7217010 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
cfd7dc1c-ff9c-483e-b191-02d29cda88e7 | checkpoint | Cable size and type correct
3c16cfa7-c427-4e08-9ae5-4fc6cd9696a0 | checkpoint | Cores terminated as per drawing & terminals tight
381bde16-e922-45b6-8734-ee71764603f1 | checkpoint | Cable numbered correctly and applied at both ends
8162c6f0-3077-4843-b18e-a9ab1d14d825 | checkpoint | Permanent core markers attached both ends
32d3c321-5c63-490a-9b56-4736c8ab0ef1 | checkpoint | Cable supported and protected as per specification
c2a2ce41-eb5b-41b0-891e-448acf8f6c83 | checkpoint | Continuity of earth conductor/ screen satisfactory
8e17ee63-5ab2-4316-8ef9-bc3dfbc0bb45 | checkpoint | Cable ties trimmed
8ec6e08c-e7a9-4319-b491-ab9c2233c720 | checkpoint | Connection of shielding/ armour as per drawings
73ab9ba4-02eb-4004-9810-6ada7bb4fc36 | checkpoint | Cable ends made up satisfactorily
e17efcb4-23b0-442d-aebd-3c0371a337b2 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
91cef6d4-14c2-4af6-81ad-75ee01b0d22c | section | Field Test
b7034660-719b-46e5-912b-a03676041c68 | checkpoint | Field Test
ab3d592e-6622-5495-b4ec-ea5e11b102a8 | textbox | Core Designation: W1 |  |  | Results - Ω
ceb43563-3fdc-5f67-8291-1538b1aebc0a | textbox | Core Designation: B1 |  |  | Results - Ω
630eb96e-94c4-581f-b3e2-12a81d20f203 | textbox | Core Designation: W2 |  |  | Results - Ω
a5fa630b-7c4f-5104-b3c9-b46f9419137f | textbox | Core Designation: B2 |  |  | Results - Ω
eda7de41-8253-59b7-a92b-a7ff5e82488d | textbox | Core Designation: W3 |  |  | Results - Ω
e48f7f5e-a746-5c4b-bd69-8a45401d2749 | textbox | Core Designation: B3 |  |  | Results - Ω
6be5ead4-051d-555c-b4c8-83d9f9983785 | textbox | Core Designation: W4
a5bcf6bb-187b-5a6b-8f2d-a89a41ae9c90 | textbox | Core Designation: B4
5ef5905a-f27a-554e-81fc-0a0e3ea2dd78 | textbox | Cable Size:
c492b2b1-dfe6-57ce-955e-52e374d80baa | textbox | E Continuity: |  |  | Ω
3d3073e2-3df9-57dd-88b5-a4412c47c406 | textbox | Lead Resistance: |  |  | Ω
0300f460-8b34-4fac-9a97-148961c46b54 | section | Completion
e027cba6-e65a-4392-8bbe-340b30140e8c | checkpoint | All cores reconnected and secure
2da906d8-a805-4e4e-86cd-80d44eef9303 | checkpoint | Source connection tension
8992f1f9-cd03-5b7f-83b6-0267be2ba8f9 | textbox | Nm:
fa07a9df-799c-4b24-9bd9-9b07a532b6ee | checkpoint | Destination connection tension
fb9214d9-fc79-5973-8540-ceda93f12ad6 | textbox | Nm:
e0f39231-409f-4f5f-91c7-e62a674d0efe | checkpoint | All connections visually and physically checked
d3ec2f7f-d9b5-43a5-9bee-fe2dbf5fbf65 | checkpoint | All test leads and bridges removed
cb569ca4-1b1a-4cf4-8f4b-67004ff2bcff | checkpoint | Drawings & schedules marked up to 'As Built' status
6ce61939-8427-4776-b2cc-e731579e7e9b | section | VERIFICATION
09d368ee-6a2d-4325-a212-2c157b7ca1bc | checkpoint | VERIFICATION
4d275c40-198b-5ac8-a9e0-b1a3a266aee9 | textbox | Deficiencies Identified:
e91677ea-045f-5d11-a14e-987476ec6944 | tickbox | Rectified/ Closed-Out
7be27298-dddb-5bca-aed3-7398ba5df446 | tickbox | Punch Listed
0bd627e8-1bb6-4385-a798-d07bfe1f68b1 | section | TEST EQUIPMENT
4a30e5fa-2a96-4152-b3cd-0d317c011ec9 | checkpoint | TEST EQUIPMENT
64c63eeb-f9e1-5368-80d1-53486f0b1b37 | textbox | Type of Meter
d537ea18-7e17-505b-b772-fd568f7c70b1 | textbox | Make/ Model
5b2612fe-d683-5b0b-b179-741cabede706 | textbox | Serial No.
6e15f40c-4430-5507-a7d5-7b15660081f8 | date | Calibration: Date
5306484e-0c63-53c7-8aa4-07853b672040 | date | Calibration: Due
eddd824b-a614-4cd2-b48b-f18890ef2f12 | section | ACCEPTANCE
32d7b97d-edbc-4ca7-8390-65da43a1cea0 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
b0a63d5c-05e9-4b0f-a34e-ac934f7cb2b3 | signoff | Add Signature
56e5be5c-9cfe-4c84-b3c1-f329998e5b24 | checklist | 561482-DOW-ITR-IN-0004 |  | 561482-DOW-ITR-IN-0004
fc1a1f0f-6f3c-46ab-8fbc-e54bc9273dbc | section | GENERAL DETAILS
cab15121-18ed-43b3-9fed-06b98f3db2a6 | checkpoint-no-value | GENERAL DETAILS
04b10be0-d039-58ee-8d38-42ff59153c80 | note | ITR Number: 561482-DOW-ITR-IN-0004
65fa4191-7ad5-5ff9-8435-4c132b9ad618 | note | Project Name: Pump Station Renewals – Silverstream Pumps
f06656a4-1baf-59df-a244-f70d83e962fc | note | Contract/ Project No: 561482
ecca8ce4-4360-5e9e-96d0-dc5f5bf075b4 | note | Area: Silverstream Pumps
4585e656-ffc2-5f64-b266-2c7d3e4276da | note | Sub-System: Pumps
f93817e1-c70c-56b6-9d0c-4f6f15a653d6 | textbox | Reference Drawing:
9689493e-0307-59dc-ab62-4e15d6ce1381 | note | Discipline: EICA
8ae45314-b4d6-575a-a7d5-5d14b152b5ad | note | Work Pack Number: N/A
5c68215e-f209-50c9-9d93-4b7098fb4d85 | note | Lot Number: N/A
f94891a9-d423-575a-b986-e7b9c6741136 | note | Cable Number: TBC
1518ea3f-28b5-5ad6-aa1c-aeb7ea294769 | note | Cable Specification: 1.5mm 4 pr CS
c1e83650-7a9d-5bf9-be4d-b152dbbb9556 | note | Source: Site MCC
dab1c3f2-c8ce-5fb0-a84c-35f4ec50540a | note | Destination: Pump 3 VSD
722dd91b-748a-57a8-b68d-a0bad8176ff1 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
f00a22ae-f9fc-4e29-929c-9fa5241c8152 | section | INSPECTION
f6f72fde-5977-446e-8a0b-1ba5d53978df | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
c7de909e-f8d4-49f0-9041-d6ec65e77459 | checkpoint | Cable size and type correct
384b1aba-eb25-471c-aa20-7b50bf586deb | checkpoint | Cores terminated as per drawing & terminals tight
09eca55c-eb9f-4e18-b5a3-5b1556df1fcb | checkpoint | Cable numbered correctly and applied at both ends
fba89705-f915-4799-b83f-e83a3a4e026f | checkpoint | Permanent core markers attached both ends
ce0c24bb-32cd-499e-862d-b621cadf03d8 | checkpoint | Cable supported and protected as per specification
a3645286-f8d3-4e43-8df8-7fb3fca4f181 | checkpoint | Continuity of earth conductor/ screen satisfactory
2c462c3a-bedf-481a-860e-094cfcbd77e4 | checkpoint | Cable ties trimmed
e13a5c9d-56ea-4a66-8eba-bef1d2a13d35 | checkpoint | Connection of shielding/ armour as per drawings
5c7986b4-b33e-4e5a-8de5-5572f4d50359 | checkpoint | Cable ends made up satisfactorily
6f941992-81d0-4725-91cd-26bcefac3dd6 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
951bc0b2-41b8-49fa-a89a-46a259b2a5c1 | section | Field Test
93378ad2-9d0e-444d-80fe-2ffb79627f93 | checkpoint | Field Test
91a0ad51-b5f8-51ad-b7d2-87a1ed9cd9fe | textbox | Core Designation: W1 |  |  | Results - Ω
3c8131b4-3809-5c29-8981-9d2a00bbb44d | textbox | Core Designation: B1 |  |  | Results - Ω
08cd4ee4-6180-5a08-b83a-2143e44bdfb2 | textbox | Core Designation: W2 |  |  | Results - Ω
cace6edd-f891-5058-9784-e0abd1503249 | textbox | Core Designation: B2 |  |  | Results - Ω
b649bee0-4b67-5fa3-bbb5-067a85b7c686 | textbox | Core Designation: W3 |  |  | Results - Ω
7c9c4024-3e15-5ec9-b181-9128544a4151 | textbox | Core Designation: B3 |  |  | Results - Ω
9f234afa-2304-5d93-8d38-12c2684d4830 | textbox | Core Designation: W4
65b51847-18cf-50e7-9123-336600077028 | textbox | Core Designation: B4
c524a55c-edd9-5a57-b9f1-cd92e2ffc8ca | textbox | Cable Size:
203bf846-adce-57e4-b7a4-c0dd471096b1 | textbox | E Continuity: |  |  | Ω
63420514-ffde-52a9-b15d-7498deedbadd | textbox | Lead Resistance: |  |  | Ω
0967b4f2-947c-4988-a806-26a7b056b38e | section | Completion
bcaf1627-7041-4452-a765-cd528da19153 | checkpoint | All cores reconnected and secure
36d85e5e-b500-45b8-a49e-e781eb9c5e47 | checkpoint | Source connection tension
de145dc0-0a93-57d3-9f6d-4bbb5bf48a42 | textbox | Nm:
1ed85108-8683-4fa6-9b61-7ecd3a7ac2c7 | checkpoint | Destination connection tension
8fd44dc7-625d-5ea1-b7ae-96b4ca311158 | textbox | Nm:
89fb5a23-f3f4-4b1f-81d6-a1bca65c10c6 | checkpoint | All connections visually and physically checked
05c89fd6-5011-4e71-bc5a-65863e4e09b1 | checkpoint | All test leads and bridges removed
aab7aca0-1b52-45ec-ad9b-34294e3c4596 | checkpoint | Drawings & schedules marked up to 'As Built' status
15e0690c-9f27-4c8c-bfa0-04599fe01572 | section | VERIFICATION
7971571c-a81e-4a2c-ba81-45f11cf3f45a | checkpoint | VERIFICATION
66b145a6-6060-5bee-9f82-93efc61d95ae | textbox | Deficiencies Identified:
ba2d8213-acca-568b-940a-aafd8f478f64 | tickbox | Rectified/ Closed-Out
6c8e0b35-73ed-571e-aa08-986f9253ef3e | tickbox | Punch Listed
0b601401-bc80-4899-8d92-3a362cbd417f | section | TEST EQUIPMENT
fe1d4c2c-fc4d-4ae4-b5bb-8ec45af3104f | checkpoint | TEST EQUIPMENT
2d6f2078-4200-585b-9194-d7114f5d8389 | textbox | Type of Meter
91943543-a85e-5e13-a1ca-2cd36cdad3b7 | textbox | Make/ Model
a8a25d9f-1297-56b7-a550-3e864bc87e2b | textbox | Serial No.
97762567-70d8-5c7f-a228-048b7b92e9d4 | date | Calibration: Date
9f446e77-6e43-5dad-80a2-cf75c4d9abc3 | date | Calibration: Due
4f0b55ae-82a4-4f37-9942-b49345f2e143 | section | ACCEPTANCE
1a9a38b7-ebfc-4829-9fb8-3cac4cc31cce | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
6d5bb978-cd86-4ea8-9169-cccd0c37c489 | signoff | Add Signature
528b7ba5-39b6-4944-8d60-6545675dcc8a | checklist | 561482-DOW-ITR-IN-0005 |  | 561482-DOW-ITR-IN-0005
8acca605-e791-41fe-9124-7367f6e577ed | section | GENERAL DETAILS
628a3be0-e6e6-4eee-bc32-b8a66d8f3b19 | checkpoint-no-value | GENERAL DETAILS
a60f1ff6-8d47-57ba-8aba-7b8445ce12d9 | note | ITR Number: 561482-DOW-ITR-IN-0005
63b8e2c0-e487-5d03-b69d-9395a73a9434 | note | Project Name: Pump Station Renewals – Silverstream Pumps
f5b2c722-b5a8-54fa-9ee9-310d89b5fb53 | note | Contract/ Project No: 561482
ad9feead-260a-5ff9-8fd0-833a4ed3d5d6 | note | Area: Silverstream Pumps
c3ac6cdb-f30d-5095-8202-3a3e92df6f27 | note | Sub-System: Pumps
9f34cda2-5e12-5770-9ef6-eeaefb08d773 | textbox | Reference Drawing:
4ea62ef8-e4a5-5bb4-b100-5636b5069298 | note | Discipline: EICA
acdacc55-dec7-59f9-80cc-a99968070a27 | note | Work Pack Number: N/A
5166cbcc-be95-50bf-b2b4-db0d8276d283 | note | Lot Number: N/A
2d124245-8d96-56c1-982f-1f8e9019d878 | note | Cable Number: TBC
8fa301e2-ff7f-5bd2-a218-8e745e330401 | note | Cable Specification: 1.5mm 2 pr CS
85051af1-8cbe-59b7-b48f-cd356cbc5f9a | note | Source: Site MCC
6a826d9c-3c46-57e3-8f3c-8d2184f2642a | note | Destination: Pump 3 VSD
0291d877-0d9f-511d-a6f0-2140bfd36a7d | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
3667e62e-840b-4479-9dc5-cf56081aee11 | section | INSPECTION
383f92f5-b396-4adf-9499-98463ac35fcf | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
38f423f7-d853-45cd-91f9-b71fe38ea924 | checkpoint | Cable size and type correct
130e9135-e1e4-4fe2-92b7-780826dbec96 | checkpoint | Cores terminated as per drawing & terminals tight
d260b9d3-34bf-483f-b8c1-e440b810a40d | checkpoint | Cable numbered correctly and applied at both ends
55cf2694-1e50-4e97-b33c-18b032463cca | checkpoint | Permanent core markers attached both ends
b762400d-92bf-42ff-bed0-4f799a3eb121 | checkpoint | Cable supported and protected as per specification
d3a8b874-2fee-4c48-b105-3969b9227e15 | checkpoint | Continuity of earth conductor/ screen satisfactory
ed576ef0-2b69-462a-8df0-7960a1bb6652 | checkpoint | Cable ties trimmed
e0b78b18-c76f-41ab-ad32-2b99df8fbaff | checkpoint | Connection of shielding/ armour as per drawings
e8d9f22e-7331-4163-963f-0cc455eb51bf | checkpoint | Cable ends made up satisfactorily
47556ef7-b870-48cb-b2a1-bf4c98cd5546 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
0be7b9d8-95d5-4a75-8d97-bef9e60dfda3 | section | Field Test
f57f44d7-f30f-4d4e-abf6-f63811b81342 | checkpoint | Field Test
f0ce9242-2629-5972-b56e-001e18f8649a | textbox | Core Designation: W1 |  |  | Results - Ω
ee1cabfd-b5ad-5cb2-a953-303500ac4892 | textbox | Core Designation: B1 |  |  | Results - Ω
fa61f390-d425-53b8-a3a5-0e9683916955 | textbox | Core Designation: W2 |  |  | Results - Ω
addd9e82-61c8-5869-b15a-33fdf1c86acf | textbox | Core Designation: B2 |  |  | Results - Ω
ff2b3667-6f8f-5086-bb02-c20a2e90264c | textbox | Core Designation: W3 |  |  | Results - Ω
e5a2e172-a7de-549e-912d-b946e11456d5 | textbox | Core Designation: B3 |  |  | Results - Ω
89313399-e0cd-59d9-9224-8f3d227f1cc1 | textbox | Core Designation: W4
9561448c-3328-576f-8e3e-b444e4c394d1 | textbox | Core Designation: B4
d6fb3cdd-2f8d-5ee3-9ceb-a0375f1eed11 | textbox | Cable Size:
1b307ce2-4dd0-529a-a621-7ef7d4425e72 | textbox | E Continuity: |  |  | Ω
2d2bc4f2-f569-589a-bb35-17541601c303 | textbox | Lead Resistance: |  |  | Ω
69097a01-1842-4b99-a9fd-a7b07bb3315f | section | Completion
ac3d22bf-a406-4bef-bf84-be4e38ed74b4 | checkpoint | All cores reconnected and secure
195de689-b8a8-42e8-8709-33867b0cde54 | checkpoint | Source connection tension
133e09b0-80e1-56cd-b9ba-06394c77b032 | textbox | Nm:
28eae370-1fa1-4e71-a6e5-1cf720c3529f | checkpoint | Destination connection tension
89494b09-6022-5b44-b167-9b3b78c1f0fd | textbox | Nm:
a93fe505-d57a-45c0-a2bd-f57bfac1c500 | checkpoint | All connections visually and physically checked
dda93627-5997-4064-8e4f-3de376fa6306 | checkpoint | All test leads and bridges removed
3925d44d-bc99-467e-8f9d-34af91273d21 | checkpoint | Drawings & schedules marked up to 'As Built' status
31b36542-452d-4c94-9529-b00417335914 | section | VERIFICATION
60596189-5865-471c-9284-7bd11300be7d | checkpoint | VERIFICATION
bea6b3e0-5b3c-5488-9198-9ae4961d3b48 | textbox | Deficiencies Identified:
a64a1a9a-70ed-534a-8daf-e598003e30a1 | tickbox | Rectified/ Closed-Out
f2be302c-30ed-5d1c-a607-c2e1f4cbe19b | tickbox | Punch Listed
8caf405d-3ceb-4d5a-938d-3b1afb979d32 | section | TEST EQUIPMENT
45071450-b4fc-4205-bd64-bd84ddabce4d | checkpoint | TEST EQUIPMENT
c01370a7-7df1-55b6-b072-61235d40dbe8 | textbox | Type of Meter
1a796073-0d4e-5357-ac9a-2c76ae912a41 | textbox | Make/ Model
cd0a6900-0aa4-58d9-a22a-c81b071bdb32 | textbox | Serial No.
8a4bf856-9e8f-5219-b421-0556322896b7 | date | Calibration: Date
8f23eceb-61f4-5369-a033-45b5b6087edb | date | Calibration: Due
59fbc05e-7e2b-462c-98ea-bcb2252ac7c2 | section | ACCEPTANCE
d5eac35c-5e54-43a4-a9b1-d9ab5b25e526 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
935b1f27-7d09-4eeb-97a7-dd37f8dd42b1 | signoff | Add Signature
f84d9b98-0a54-4474-b5f7-6c2b1e0f6b21 | checklist | 561482-DOW-ITR-IN-0006 |  | 561482-DOW-ITR-IN-0006
9e3140cf-618d-44ea-b01e-c8b290ab87f1 | section | GENERAL DETAILS
2c0929af-522c-427e-a32a-4987cfc51f27 | checkpoint-no-value | GENERAL DETAILS
43425d65-5293-5450-9947-15fa486b1b48 | note | ITR Number: 561482-DOW-ITR-IN-0006
08f64c43-6159-5a67-954d-48635ce4f4de | note | Project Name: Pump Station Renewals – Silverstream Pumps
f8efab10-7031-57a3-8f9f-2716bdfbe9bd | note | Contract/ Project No: 561482
5dbee2d9-5cc3-58ac-819d-b971bc97dbf2 | note | Area: Silverstream Pumps
584c23a0-4bcb-5c5b-b285-fce2c9fb2d51 | note | Sub-System: Pumps
6df6c058-c879-57a2-9014-cb65bbf56103 | textbox | Reference Drawing:
9b946ea1-f6fc-5b64-8d89-9b090514e226 | note | Discipline: EICA
9d2e3be8-f6e9-54a5-aeb3-56bf1bf67971 | note | Work Pack Number: N/A
f1d4f7e9-9c98-54cf-85e5-e75f7e5ca8c5 | note | Lot Number: N/A
a52c060a-3566-512f-aed4-27d27ee940c7 | note | Cable Number: TBC
a73715bb-7a58-55f7-b0fc-113a2584c6b4 | note | Cable Specification: 1.5mm 1 pr ES
66283e27-29fb-5ee6-977e-15be1f6e447e | note | Source: Pump 3 VSD
1b9aa65f-a39e-5e44-bc9a-73923310f02e | note | Destination: Pump 3
577c0675-7d07-578b-a479-818ac1dcaa3d | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
e78e7225-6367-4927-81ca-68925f12e57d | section | INSPECTION
48382292-4cee-4e4c-ad8d-9139d9135c79 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
2b39a946-edbb-4be3-b77b-01b6c335500a | checkpoint | Cable size and type correct
9a783f7d-8a82-48b6-b0f6-f205fa67fa2e | checkpoint | Cores terminated as per drawing & terminals tight
1c6557b1-90d8-4417-b323-21ce09980b48 | checkpoint | Cable numbered correctly and applied at both ends
1cd67c05-e5c7-4b78-8f57-80b62c67d1e0 | checkpoint | Permanent core markers attached both ends
5804b606-7bb6-47ea-a5ad-c4fc4d488d57 | checkpoint | Cable supported and protected as per specification
968ce9ae-7f87-431d-b1be-ef0043cb4586 | checkpoint | Continuity of earth conductor/ screen satisfactory
3b8155fb-3850-4907-a1a9-292061873f36 | checkpoint | Cable ties trimmed
7349ae06-4047-4a1f-b56a-ffb692aac8a4 | checkpoint | Connection of shielding/ armour as per drawings
6b38fdd5-7929-4bd7-bf28-d10b57fbf6fd | checkpoint | Cable ends made up satisfactorily
99482457-4118-4f34-a23d-c5cf990faf20 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
63a79b6b-7021-4514-a9d3-3e764f1647fd | section | Field Test
4e8852c7-86e8-4360-93d1-9eeeee18337c | checkpoint | Field Test
1f9bec3d-ac11-5e67-b830-3ae510a6aa7b | textbox | Core Designation: W1 |  |  | Results - Ω
a85b6c27-a062-5663-8190-a20f4f812dd5 | textbox | Core Designation: B1 |  |  | Results - Ω
6a4d4067-884f-5a9d-88be-207541826f4f | textbox | Core Designation: W2 |  |  | Results - Ω
4bd6e44d-4708-5850-ae17-905e4d8e385a | textbox | Core Designation: B2 |  |  | Results - Ω
f42acc59-4c9f-5c69-802b-df6eacdeded0 | textbox | Core Designation: W3 |  |  | Results - Ω
676e0e2b-e5eb-5ace-afea-84f0016c0f95 | textbox | Core Designation: B3 |  |  | Results - Ω
2ff16326-006f-566c-89cc-1bb5709539be | textbox | Core Designation: W4
18de2dd6-096c-5056-9d5e-2f45075815d2 | textbox | Core Designation: B4
0fa90ca4-92bc-5d7c-8071-f89eb6082040 | textbox | Cable Size:
a2614c15-21dd-5bcc-8b9f-fcf3ef049673 | textbox | E Continuity: |  |  | Ω
9e6b916a-dc6c-5ce2-86eb-100201a65692 | textbox | Lead Resistance: |  |  | Ω
de2becd8-3cf8-4e5a-a663-e431a3efe1b6 | section | Completion
1a75cd75-a15a-445f-aba0-3b1cc9006000 | checkpoint | All cores reconnected and secure
599080e7-a627-4ac1-b43e-beed8ff0e281 | checkpoint | Source connection tension
bc213135-d6cb-5424-ae59-27aec46bed85 | textbox | Nm:
29579276-cf46-4101-b18f-354b52da10ea | checkpoint | Destination connection tension
b58dc5d3-1c98-5569-a686-6874d4b12240 | textbox | Nm:
f05214e0-8447-41af-a79c-82ac6cf5d548 | checkpoint | All connections visually and physically checked
9abe1eaf-e336-4b2b-aa05-939a68ee08de | checkpoint | All test leads and bridges removed
d2aa0bcc-5f68-4e41-8564-62619db9cec0 | checkpoint | Drawings & schedules marked up to 'As Built' status
28ada8aa-34f3-49dc-8492-1a190cdac89d | section | VERIFICATION
2877eef5-5d34-4466-8b19-eae2c0fb75b3 | checkpoint | VERIFICATION
c652967e-8e95-573d-b367-7bd5301872ef | textbox | Deficiencies Identified:
de157eae-8cb5-536f-8af9-9c04b1556e6a | tickbox | Rectified/ Closed-Out
2569aa52-9d1a-53d9-89ad-fd5da24e3e37 | tickbox | Punch Listed
eb3e46e8-7c58-4e36-8fce-29bda35f3c7f | section | TEST EQUIPMENT
4b5d2a46-d7dc-4fde-89fb-ec7132d7834d | checkpoint | TEST EQUIPMENT
2ade420f-8430-5940-b4c4-f073cd943ac8 | textbox | Type of Meter
bf42fe10-5acf-5245-864a-35f707aec0c5 | textbox | Make/ Model
7e1f6967-848b-5eec-9206-a106645db439 | textbox | Serial No.
8a8ddab7-a9dd-5ef2-8240-e66aa7e5908a | date | Calibration: Date
9596c698-42ae-5d3f-9b9f-4f40e60f29b0 | date | Calibration: Due
4391539f-b2d3-42cd-9ee5-16cd451f5918 | section | ACCEPTANCE
65a6d527-0b91-4949-b772-58ec5a8071c2 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
43da6f7e-f3c6-45af-a582-ecb6cb2511bb | signoff | Add Signature
71910980-0f34-4387-8cef-ff2c1bb88d3f | checklist | 561482-DOW-ITR-IN-0007 |  | 561482-DOW-ITR-IN-0007
b04f1347-7237-4e18-a688-093feff120a3 | section | GENERAL DETAILS
4e61411d-d9ef-4c23-8c2b-dd42086efab9 | checkpoint-no-value | GENERAL DETAILS
5a9d73f9-695b-5d82-9ae7-413ccc6fead7 | note | ITR Number: 561482-DOW-ITR-IN-0007
eeaaffbd-0278-5f4c-ad9b-37216ae60d2a | note | Project Name: Pump Station Renewals – Silverstream Pumps
c67a4485-5be4-581f-ae04-d5f59cab085a | note | Contract/ Project No: 561482
8dd3574d-ec65-5ad6-b587-415e086e8a52 | note | Area: Silverstream Pumps
e4acacc8-7ad3-5605-b198-408eb7390267 | note | Sub-System: Pumps
c5a76a09-b95c-5a35-997c-fc9fc6eb8c92 | textbox | Reference Drawing:
91a0e02f-4fd0-534b-abc7-58dddf2e3d9b | note | Discipline: EICA
25f20f89-a614-5a98-9cc9-b418af573d02 | note | Work Pack Number: N/A
8827cdc4-2fea-5cd3-964a-28eb2641ee30 | note | Lot Number: N/A
f05cf91a-7757-5815-99d8-22f2705620e2 | note | Cable Number: TBC
f48da932-f97b-5536-82df-30e43e0637aa | note | Cable Specification: 1.5mm 2 pr CS
fe9e87ef-0a7b-5d3e-8ec7-8f630eda0963 | note | Source: Site MCC
aa49a642-285d-5f33-b0cf-97247dd6e418 | note | Destination: E-Stop Button 1
41cd100e-e9af-5b6f-a38d-07c70c8f72ee | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
3a5993a2-c0c4-4237-a383-551770e2662d | section | INSPECTION
c2dc7c1f-09ee-4542-ac2f-8289e0ecc66b | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
f83b7138-5c42-4306-ae25-88c1d1b3e213 | checkpoint | Cable size and type correct
2ff6d87b-1bf9-4bf4-b13b-c8dc2f88f775 | checkpoint | Cores terminated as per drawing & terminals tight
13676527-5502-4331-85f2-5430fcd1d9af | checkpoint | Cable numbered correctly and applied at both ends
8f3ff7bf-96fa-4f69-89a1-8b094969e43f | checkpoint | Permanent core markers attached both ends
39bad966-33c6-4aa5-a579-c78e340cb137 | checkpoint | Cable supported and protected as per specification
6aff6a82-c130-465a-9f1d-b916c8458b80 | checkpoint | Continuity of earth conductor/ screen satisfactory
ff766ea5-ed5f-44a1-b67f-ace30125eec1 | checkpoint | Cable ties trimmed
323a079f-6af7-46eb-bc0b-a67858bee8ad | checkpoint | Connection of shielding/ armour as per drawings
50dbd044-2469-44a6-a7ae-81162d620b56 | checkpoint | Cable ends made up satisfactorily
7fef32ac-77f0-4fa3-8777-459e12ecc18c | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
feeb372e-1d9a-42fa-8155-352115d17c29 | section | Field Test
31b14cd7-e7a8-4610-9518-bcb6cf7dc4ba | checkpoint | Field Test
d56355db-fe6d-5b28-86f4-300693d4d746 | textbox | Core Designation: W1 |  |  | Results - Ω
4cbddcd9-45c5-53e9-991d-30accb355775 | textbox | Core Designation: B1 |  |  | Results - Ω
9e088317-9ead-509f-99a3-d3d40c49b34f | textbox | Core Designation: W2 |  |  | Results - Ω
f26cb6f1-31b7-59bc-a99e-a9ae5b155ffd | textbox | Core Designation: B2 |  |  | Results - Ω
dd01188e-89e8-5735-ba25-67c3a32f02eb | textbox | Core Designation: W3 |  |  | Results - Ω
87614d37-053d-582a-b76d-e80949cce0d5 | textbox | Core Designation: B3 |  |  | Results - Ω
612dcf7d-7b4a-5c43-8522-f04150464bea | textbox | Core Designation: W4
1c073655-1c7e-50b5-8ce6-f5707c9de0db | textbox | Core Designation: B4
a8763a31-d34a-54c7-84c6-cb8760dec5bf | textbox | Cable Size:
b06c8e37-5387-5eac-b9a6-99f485f3342f | textbox | E Continuity: |  |  | Ω
e9430fab-27de-516b-ade3-12821c60bd28 | textbox | Lead Resistance: |  |  | Ω
02d9405a-4243-4ce8-9933-a06dc256c128 | section | Completion
71955df9-c865-46d1-8e06-e7bffdb08019 | checkpoint | All cores reconnected and secure
fba2c7db-d327-4049-9e5b-ce9ff242066a | checkpoint | Source connection tension
45bfe187-4c5d-5bb6-a43e-d15fdab45ff0 | textbox | Nm:
07c133d4-a6f7-4330-a67d-866542c32779 | checkpoint | Destination connection tension
59e02bbe-1caf-5317-a705-740bea25707e | textbox | Nm:
679c0a05-ce55-40bf-87e7-93cba2629f3b | checkpoint | All connections visually and physically checked
a2f06589-bcbd-43fb-bb85-a3da7f623028 | checkpoint | All test leads and bridges removed
77a228c1-d282-4910-b3dc-f98d3e3a23cd | checkpoint | Drawings & schedules marked up to 'As Built' status
42cf83b0-3adf-497d-8238-14457b7eb281 | section | VERIFICATION
c874a08d-c6b1-47a6-aa12-15a13a9943bc | checkpoint | VERIFICATION
d32b39dd-b01a-5867-b377-a5638f119454 | textbox | Deficiencies Identified:
8e1f3f89-cb1d-5e1b-a650-d2e272698725 | tickbox | Rectified/ Closed-Out
d48e079a-d364-56b6-a571-3699cafbf913 | tickbox | Punch Listed
f7c753a7-ab23-43b5-ad44-bd3103583fdf | section | TEST EQUIPMENT
c28eba6e-5d12-4575-942d-6c7cdac164e2 | checkpoint | TEST EQUIPMENT
df2d0187-595c-58a3-af98-7a62b64697c8 | textbox | Type of Meter
bfc9e65d-d1da-5767-b17c-9b40d0e8af24 | textbox | Make/ Model
43ecdde8-cf06-539d-8042-99da44690e4b | textbox | Serial No.
70c3f42e-2806-558a-bb71-67c380c5e392 | date | Calibration: Date
591d77b8-4f0a-5da5-808b-56d3bb6ffad6 | date | Calibration: Due
2e16e689-e45f-41bc-a1ad-cdb430ffb9d6 | section | ACCEPTANCE
673fafca-3609-49e3-a7d4-2141f5aa3feb | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
bf7fb3a7-983b-4bce-a674-075cbbd111d2 | signoff | Add Signature
7e19bc6c-6475-4291-8c1f-c7589662394f | checklist | 561482-DOW-ITR-IN-0008 |  | 561482-DOW-ITR-IN-0008
d7ca327b-356d-418e-92c8-83adb3540542 | section | GENERAL DETAILS
6b476faa-f727-46a5-a15f-1a3a3653f0af | checkpoint-no-value | GENERAL DETAILS
cdb79f4a-f38e-57d0-bd84-c547c17f4c02 | note | ITR Number: 561482-DOW-ITR-IN-0008
2090eea7-1e42-5727-870f-97b2ca591e02 | note | Project Name: Pump Station Renewals – Silverstream Pumps
192180d9-0bb6-51c7-8aec-ddd5b938d318 | note | Contract/ Project No: 561482
58dca363-5fea-55f4-b3bf-0a45ecfc1524 | note | Area: Silverstream Pumps
12c4282c-deba-578e-8956-f408a4729e5b | note | Sub-System: Pumps
c3c086a0-11d7-5b2d-a212-dca32d6efb92 | textbox | Reference Drawing:
db505fd5-b265-59ed-aaa6-9999e0298e53 | note | Discipline: EICA
fbd60287-9490-5aef-93a7-3d10ddb8a060 | note | Work Pack Number: N/A
ce75540a-ca4e-5a45-9528-24883ae46010 | note | Lot Number: N/A
f0fbcf6d-b6a3-5ca4-9154-8a1baafac08f | note | Cable Number: TBC
be0e09de-bcbf-5076-8911-7bf5bfb057b1 | note | Cable Specification: 1.5mm 2 pr CS
a7615fb6-6de0-5aa3-99e8-8b5fea235568 | note | Source: Site MCC
eda89716-584e-5fba-8f47-226ec392347b | note | Destination: E-Stop Button 2
ede99cda-698d-532a-b04c-0781e49a4293 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
8b36557e-ef01-44ef-800e-6f7368dff5f5 | section | INSPECTION
97d2a722-77b8-4cb1-ba08-afe453aac2a4 | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
10d9fa5d-29cb-4362-a3ef-7650a5e4064b | checkpoint | Cable size and type correct
e8824070-8466-433b-ad90-297f840e41b3 | checkpoint | Cores terminated as per drawing & terminals tight
301a3941-9417-4111-9a3e-93e655562f16 | checkpoint | Cable numbered correctly and applied at both ends
24b4551b-86a3-45a8-8707-e6c4841a7165 | checkpoint | Permanent core markers attached both ends
b5c37f7b-a196-466a-bd37-955c70c930c3 | checkpoint | Cable supported and protected as per specification
f469589f-56b1-403c-bd51-19fbca4f8f2e | checkpoint | Continuity of earth conductor/ screen satisfactory
af83f958-0e12-4537-8bdf-e513fcb3ed2b | checkpoint | Cable ties trimmed
250261eb-532e-4436-9dcd-f711fffec043 | checkpoint | Connection of shielding/ armour as per drawings
4807042f-4671-4ab5-881d-af85cd469262 | checkpoint | Cable ends made up satisfactorily
d58cd845-144d-4527-8581-bb493fd3b289 | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
f208da01-0955-4de3-b514-7686559232a2 | section | Field Test
656a5cee-e875-4067-91b0-be13976ed22d | checkpoint | Field Test
6fcb37a4-71b8-5d81-b41e-75fb54e37dfd | textbox | Core Designation: W1 |  |  | Results - Ω
8afd2a61-a799-5604-8753-3057d1d641fe | textbox | Core Designation: B1 |  |  | Results - Ω
bd6227e8-f5a2-5969-907b-b3456808b197 | textbox | Core Designation: W2 |  |  | Results - Ω
ca446eb6-7c42-5c5c-89d4-5ce7e9b900a6 | textbox | Core Designation: B2 |  |  | Results - Ω
1e9a7e67-659b-5b3c-a049-324bbb80d94a | textbox | Core Designation: W3 |  |  | Results - Ω
a1c76554-57c7-5b63-8ca9-b09bcbd96497 | textbox | Core Designation: B3 |  |  | Results - Ω
032629f9-bed9-562f-bc2d-8320add26225 | textbox | Core Designation: W4
a9b517ec-4b33-587c-a033-3edb6644c11f | textbox | Core Designation: B4
4e57b89b-e9b5-535e-903b-fa7a56b48f84 | textbox | Cable Size:
9e70bc55-5613-552f-b7fd-7bae31498882 | textbox | E Continuity: |  |  | Ω
f5cd6375-b81c-51f5-96b9-975e8a806a2e | textbox | Lead Resistance: |  |  | Ω
b548c68b-b18c-4571-a6c0-a965c4645193 | section | Completion
6fe79094-2f1d-4dd6-8c31-0b7011325778 | checkpoint | All cores reconnected and secure
d32c8bf4-5f16-42e4-a996-a9268a520b61 | checkpoint | Source connection tension
fe7bc03d-bd5a-55e1-9d8e-9b22da0f72fb | textbox | Nm:
9085cbaa-c25a-441b-a1cb-3684a00d18ba | checkpoint | Destination connection tension
074820e7-8f3e-580b-8003-cd4761bfa53d | textbox | Nm:
d0339a9e-a5bc-433d-a881-ef2babbe4032 | checkpoint | All connections visually and physically checked
02ea27e6-9cee-4d1b-9684-d664fa14f280 | checkpoint | All test leads and bridges removed
0ad3e806-13f3-4707-8249-62d7c2bd20c9 | checkpoint | Drawings & schedules marked up to 'As Built' status
d57c70e5-c43d-40b2-8e55-df5ad000ce90 | section | VERIFICATION
15fc9032-97df-4c8b-981c-11491718cae2 | checkpoint | VERIFICATION
9ed1af64-0f16-57ac-bff5-cb8329eb416e | textbox | Deficiencies Identified:
7338d6e3-c626-57c1-8ada-05aef260fbbc | tickbox | Rectified/ Closed-Out
c1665978-28e0-5510-a61f-88c7cb619865 | tickbox | Punch Listed
fe3645d5-867c-42a1-aade-4f6982017a3f | section | TEST EQUIPMENT
eba37ce3-8144-42bf-91cb-a43dd4a3c98a | checkpoint | TEST EQUIPMENT
c7406e70-a8b7-5b1c-a3d9-daa218a7f975 | textbox | Type of Meter
bdf1a8e6-0c2d-5add-a329-bc02ba6ef4a5 | textbox | Make/ Model
38175653-65ab-526f-b54b-6467e3fd26c1 | textbox | Serial No.
9e666e2f-f2f5-57f4-9461-9ce6b6afed68 | date | Calibration: Date
74eb00cf-bd47-5c91-b0d2-f84e179e7c98 | date | Calibration: Due
d96a2b17-fb66-44b0-854d-4563f7e5103e | section | ACCEPTANCE
a45c119b-6a7f-4b4f-91ac-6604369ffd20 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
f09c07b3-c581-4a2d-921e-9073f42f4461 | signoff | Add Signature
af02662a-3180-4e1f-ae4d-b7a48e89aa0c | checklist | 561482-DOW-ITR-IN-0009 |  | 561482-DOW-ITR-IN-0009
09977631-4c59-407c-a594-84bcfe53c023 | section | GENERAL DETAILS
a4e78bff-aae5-4324-b9c3-02fba7e645a8 | checkpoint-no-value | GENERAL DETAILS
05fba1c3-a615-539b-b439-b8b01215ecc9 | note | ITR Number: 561482-DOW-ITR-IN-0009
fce264be-10ef-55b3-9228-9ce9501a8161 | note | Project Name: Pump Station Renewals – Silverstream Pumps
e719aa5a-aa6f-5c21-a0a6-078d9f2c85c6 | note | Contract/ Project No: 561482
aee24022-866d-54f3-9a5f-714110ea3e32 | note | Area: Silverstream Pumps
9e7360af-1cb7-55d6-a998-1bba87f33af7 | note | Sub-System: Pumps
f1870d98-4a27-5fbf-bc45-c40479e9c8cd | textbox | Reference Drawing:
ea9a299d-5267-56b7-bd0b-e07edfa6e7a0 | note | Discipline: EICA
e6fc6f0e-7c8c-59a9-857a-e430e005dd0e | note | Work Pack Number: N/A
2268a44e-a92e-5ae0-ba12-c0ce684d8f8e | note | Lot Number: N/A
5cf7d1b1-997e-5872-9362-cdefc7b3adca | note | Cable Number: TBC
7e8a680a-e34d-5ac2-895a-8b20bfdcc8ef | note | Cable Specification: 1.5mm 2 pr ESCS
95ef1eb5-fa77-56f0-aa51-dcbb9553b0a3 | note | Source: Site MCC
eaab9167-180d-57f6-aa81-bac57560a40c | note | Destination: Generator Connection Panel
59f0b05c-09b0-5524-b169-448f750066e2 | note | Standards: AS/NZS 3000, AS/NSZ 3008.1.1:2017, AS/NZS 4836 and AS/NZS 3017
0bfff24c-90f0-4055-9279-7b2629d5685b | section | INSPECTION
259d2f21-1a74-4f60-bf52-19c25550edcb | checkpoint-no-value | Ensure circuits are de-energised before connecting test equipment. ELV and comms cables must not be insulation resistance tested.
1988ac1b-95ca-4f5f-b926-7372fd7620b1 | checkpoint | Cable size and type correct
704ce0b5-07e2-432a-8e4a-139146b17a9b | checkpoint | Cores terminated as per drawing & terminals tight
dd724644-b491-4d8d-8ae2-e82826b5f9ef | checkpoint | Cable numbered correctly and applied at both ends
7c985d35-ca24-452d-aad4-2628a8a5b1dc | checkpoint | Permanent core markers attached both ends
bcc049e0-975f-4e07-8944-1374f20fa733 | checkpoint | Cable supported and protected as per specification
1d98b532-58a5-4452-acb5-01cd50c54777 | checkpoint | Continuity of earth conductor/ screen satisfactory
8b3e4d0d-dd0c-49f0-90d0-b7c4db0c7cae | checkpoint | Cable ties trimmed
45118513-4e71-48ea-aecb-048b873ec3db | checkpoint | Connection of shielding/ armour as per drawings
ee959e35-b3e1-4f82-a87f-20505aadb85e | checkpoint | Cable ends made up satisfactorily
ca3e045f-87ab-4274-b391-10d9b3c7f9ca | checkpoint | Protective earth complies with Table 3.2 AS/NZS 3017
a317a65c-38b6-4cfe-9acb-2789587fc839 | section | Field Test
fd4a554e-ca89-4ea1-8d4a-bef2bd56029e | checkpoint | Field Test
ff8aa0d3-3ee8-5b69-86c2-aea4db54b028 | textbox | Core Designation: W1 |  |  | Results - Ω
cbf6a974-e8bb-53db-8556-4a450bbfb8c1 | textbox | Core Designation: B1 |  |  | Results - Ω
0674d7c5-9d26-5443-acc5-a45f81fa3d1a | textbox | Core Designation: W2 |  |  | Results - Ω
cb943fcb-a931-5380-8a79-ae4ef0a2cc77 | textbox | Core Designation: B2 |  |  | Results - Ω
d4bb3b88-e7e5-5fba-9fda-2986a0fb9c64 | textbox | Core Designation: W3 |  |  | Results - Ω
d0e1281e-bd04-5b5a-99c1-3d1dec8f33e6 | textbox | Core Designation: B3 |  |  | Results - Ω
6e3b457b-ae55-5953-af57-3baa50fbe805 | textbox | Core Designation: W4
b8170992-781c-530d-b345-39875f955913 | textbox | Core Designation: B4
f2798fb3-44f3-5486-982c-27640799e6f0 | textbox | Cable Size:
4006bf52-298b-51ac-9d9b-524a77100180 | textbox | E Continuity: |  |  | Ω
a65fc8ec-e965-5c22-a15d-df4492566c28 | textbox | Lead Resistance: |  |  | Ω
42dfca30-7d26-4197-aa28-aba9f1a5b70e | section | Completion
6954e8c3-dd7d-48dd-9f21-8561515559b1 | checkpoint | All cores reconnected and secure
49ccf4d0-0407-4ea4-94a7-f80532a0c821 | checkpoint | Source connection tension
2a0d6ade-bc32-50e2-82a5-47bbfb9798ea | textbox | Nm:
5d089484-793a-4a73-9009-b4af650323d3 | checkpoint | Destination connection tension
4fba6efc-03fa-5473-8002-9227dd9d6c51 | textbox | Nm:
aa41d4f7-8f01-4b68-9c8b-86891d733eb6 | checkpoint | All connections visually and physically checked
b043dfc9-1df1-474c-9a8d-5be3b43a6472 | checkpoint | All test leads and bridges removed
966a942b-25fc-4ac4-b7db-a4c7684f140d | checkpoint | Drawings & schedules marked up to 'As Built' status
43179624-5314-4e00-aa07-8597a7eeb842 | section | VERIFICATION
21bdea59-1ff8-4bc1-8e86-b1c6268eb61b | checkpoint | VERIFICATION
2902f8ef-b18d-53f5-a41e-3f7dd7970df4 | textbox | Deficiencies Identified:
77823555-175c-587b-9488-ceb8addb78ba | tickbox | Rectified/ Closed-Out
34fab554-1e0d-57ed-a029-0513b1ec303d | tickbox | Punch Listed
01d22fd6-32e3-46b7-8b19-ec63ed950e69 | section | TEST EQUIPMENT
d9b3dc04-b608-402d-98e3-958b6804765d | checkpoint | TEST EQUIPMENT
44080477-aa3f-5749-80f1-a9565e6fb337 | textbox | Type of Meter
cb1ad1fb-ec9a-55e3-a2f7-474ddaabeba3 | textbox | Make/ Model
aa895ad3-d03d-5e1e-9093-b3315325a85a | textbox | Serial No.
6ab38081-6d5a-5976-abcb-f6fa500cae21 | date | Calibration: Date
1f67db85-ab57-5ec9-ba7f-967de014411b | date | Calibration: Due
557b0325-bca2-45cf-97df-5bd57f40c5b7 | section | ACCEPTANCE
8a6199ee-4803-45aa-8cd5-118d664487b4 | checkpoint | I hereby confirm the work has been completed in accordance with contract specified/ referenced drawings, technical specifications, and standards.
7390a49e-995c-4970-a630-8751d9d2de3f | signoff | Add Signature
f0db95d4-873f-4b29-a738-5cfcf82cc2a8 | checklist | 561482-ITP-001 - Switchboard Delivery and Electrical Installation | itp | 561482-ITP-001 - Switchboard Delivery and Electrical Installation
03d96dad-b6d7-4370-b6c2-e93fe8881bfc | section | SECTION 3 – RECEIVING INSPECTIONS
2efffef1-0820-489a-a6a5-a8ef55310afc | checkpoint | 3.1 - Inspection of Switchboard Cabinet Pieces prior to delivery to site
66cf0f2b-c4f6-5712-8603-9995cffecabb | note | Inspection Point: Quality Control Activity - Check overall condition. check connections for internal electrical components
f5de3d8d-3fd4-5dd3-b21f-5d174bcadf98 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
1eb6bd9c-7eb9-52cc-a1e0-c8f886ed71a2 | note | Verifying Document - Email or NTE to report
40293768-b21d-5856-9a68-1db2e0561aa0 | note | Frequency - Once
46092adb-95d8-58bb-8945-e3af623f5e28 | note | Inspection Type (Visual, other) - Visual + Photograph
49ff573e-728b-515a-aab9-bb7e255b54b1 | note | Inspection: Key - C
60cdabeb-f92a-52f1-b54b-f0ccabf16018 | note | Inspection: By - IP/B
22693e5a-b5aa-489d-8715-95cc5cfa99b3 | checkpoint | 3.2 - Delivery of Switchboard materials to site
9475c1bb-facd-5bd7-8b17-7314d8a9ff0c | note | Inspection Point: Quality Control Activity - Check and verify that the switchboard materials have been delivered damage free
06932993-0987-5da5-b363-2973929cad60 | note | Acceptance Criteria - materials are damage free
02a8df15-dde5-5d9d-bd57-6bba8e2ed7c0 | note | Verifying Document - Material Delivery Docket
9b8c9801-5cfb-53ff-93ec-979fc764d56b | note | Frequency - Once
0a0a485e-0fb8-52ad-81b5-a04d059e86d7 | note | Inspection Type (Visual, other) - Visual + inspection
26797898-83e2-59b7-8727-af672ed37fb7 | note | Inspection: Key - C
4f306a28-36d9-5d94-ab2d-fc4516766fa2 | note | Inspection: By - IP
f7a26402-6f5f-472b-95ee-fc7d9079dc2e | section | SECTION 4 – IN-PROCESS INSPECTIONS
1f2080f5-1d90-4790-ac81-e4972c4e8419 | checkpoint | 4.1 - On-site assembly
67b391b3-ac14-5f31-8c1d-8cbee95df221 | note | Inspection Point: Quality Control Activity - Pre-Removal of required covers from Switchboard
701126a1-dd9d-5bda-a322-6a4215c4a696 | note | Acceptance Criteria - isolation of switchboard is proven
9abd8938-3952-52e2-ba3d-6d5e8726bc49 | note | Verifying Document - on site testing, isolation tags in place
ff96fd02-43d6-557d-8b84-6c14ec485f97 | note | Frequency - once
872b69f4-29ea-58d5-bcb5-90accf923cac | note | Inspection Type (Visual, other) - Visual
1f013e52-ec05-5e16-b3e1-37ded06fc6cf | note | Inspection: Key - I
d08ecc5b-3264-5416-9a2a-32c5a584b28c | note | Inspection: By - IP
e3d78801-3b21-4d4a-b872-c6a249e87ad4 | checkpoint | 4.2 - On-site assembly
b6b8ecec-8e2a-5fbc-9eb2-b6aba0b2f912 | note | Inspection Point: Quality Control Activity - Switchboard exterior panels removed as required
1cd50ba0-40b5-5b3e-99de-139bbb2b9af7 | note | Acceptance Criteria - work area secured, all voltage sources isolated. no signs of degradation on switchboard.
83982f87-e96d-57ec-a21f-1347a0155842 | note | Verifying Document - Testing, photos as required
76e7d5eb-2056-5178-b96a-269df23f2b63 | note | Frequency - once
da655707-1ef0-5ffb-bc62-3682c330c080 | note | Inspection Type (Visual, other) - Visual + Photograph
9482329f-fc59-5e4a-8578-ed030df91ce2 | note | Inspection: Key - I
7a5be0f8-08d8-5588-9e72-369b6462ca15 | note | Inspection: By - IP
8f070261-c725-4c63-97db-74d9b200b889 | checkpoint | 4.3 - Connection of new Generator Change-over cabinet.
99ef6b58-70eb-5d61-99b9-bfb209856466 | note | Inspection Point: Quality Control Activity - connections of electrical cabling/bus bars.
a796355a-6445-52c0-948f-68c719b7bb7c | note | Acceptance Criteria - Cabling/busbars connected correctly, insulation resistance between conductors acceptable.
9b2e8732-e108-5fc9-b59c-6e316c559310 | note | Verifying Document - Switchboard Acceptance Test. C.O.C from Switchboard Manufacturers.
33786f13-e2df-5d9d-b64f-495930bb8337 | note | Frequency - Once
014f67bb-b2bc-52e6-83f2-8999ebe8f114 | note | Inspection Type (Visual, other) - Visual + Photograph
d89f3fef-e7d2-527e-b249-b28b571d0495 | note | Inspection: Key - I
180afe3e-3065-569a-8f7a-5c30cca4c86e | note | Inspection: By - IP
bc9903e8-8ef2-45bc-82d3-ef25dffc347b | checkpoint | 4.4 - Re-Energizing of switchboard
96587c88-e25f-57c7-8629-fbda9608bc0a | note | Inspection Point: Quality Control Activity - Switchboard work completed.
c14e1f3c-fa3f-5fc1-a965-942685ee31d7 | note | Acceptance Criteria - Switchboard upgrades completed. testing completed, interlocks between main switch and generator switch tested and verified, phase rotation confirmed
4f23c6f5-24ec-53ce-b555-efe529b88908 | note | Verifying Document - Switchboard C.O.C, instrument test of supply mains.
31f675b5-f6de-526e-ba0c-4ea69c70f370 | note | Frequency - once
ce7b4382-2ac9-5cf0-9115-2b9a0ce223ca | note | Inspection Type (Visual, other) - Visual + Inspection
1b472704-4f0a-5f1d-b211-4b7136b2cb5e | note | Inspection: Key - I
e0c87eed-6474-55e1-a86d-9aaa77357573 | note | Inspection: By - IP
2cf05069-8ace-4579-bb29-5d50d0be125c | checkpoint | 4.5 - Submission/review/appr oval of the Level 2 FD
45546cc8-64fc-54ae-97da-14b18be19e31 | note | Inspection Point: Quality Control Activity - Software functionality meets expectations
8b7df376-1d2d-56d5-ab20-71d5c05ad662 | note | Acceptance Criteria - Approval from consultant
7241d513-2778-5351-ad63-194763a4638b | note | Verifying Document - NTC
891b2744-6cd5-55c1-b301-7baa67d521bd | note | Frequency - Once
6af9ef14-3237-58fd-a947-5ababa2b77fe | note | Inspection Type (Visual, other) - Visual
c8a4dacb-daa8-5891-a6e4-5cd4720d1957 | note | Inspection: Key - I
193ddabe-c026-5779-a445-666fca1212b2 | note | Inspection: By - IP
04e4ede5-9076-4eeb-ab18-105bff22ca76 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
8cea6a96-d312-4232-bef7-528edf10d115 | checkpoint | 5.1 - Switchboard
118d1e96-ff38-537f-b516-a61ddb46b57f | note | Inspection Point: Quality Control Activity - Assembled, inspection carried out and approved
c4c31e54-0234-5973-b1a3-c1476f7f5941 | note | Acceptance Criteria - Electrical Testing completed, all covers in place and secured.
960a08b5-1aa0-528a-bae2-a9847c35ec52 | note | ○ All bolts present.
a291fe3d-27cc-5f26-be43-b601f128ee19 | note | ○ R.O.I issued by electrical inspector.
96308669-9641-5e44-8054-7aaac5952947 | note | Verifying Document - Switchboard acceptance test sheet.
b064dc5c-1dce-5fe7-8b9d-50cc7f194439 | note | Frequency - once
af5d213c-b87f-525d-9915-e78d715997b3 | note | Inspection Type (Visual, other) - Visual + Document
7ead4aa6-528a-577e-bf03-880e8b536eed | note | Inspection: Key - I
a3c2cac1-7498-584a-a18d-fdfaaddfd9c8 | note | Inspection: By - IP
5694bb18-1ee9-4546-8f2e-7f5411470860 | checklist | 561482-ITP-002.2 - VSD2 Delivery and Installation | itp | 561482-ITP-002.2 - VSD2 Delivery and Installation
e8a29596-f907-47ed-a3ff-d56447e70a97 | section | SECTION 3 – RECEIVING INSPECTIONS
0a620231-31ea-4fc1-84ab-6bf05ae7c91b | checkpoint | 3.1 - Inspection of VSD prior to delivery to site
b711e90d-6a9d-5236-b488-f29469f05207 | note | Inspection Point: Quality Control Activity - Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct.
02c259ec-6d19-59f1-882c-00756d6433e8 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
31b328e5-7da7-55a3-a2b9-45f4d3690541 | note | Frequency - Once
2dd46d13-49ea-5aa2-965a-2cafdc117f89 | note | Inspection Type (Visual, other) - Visual + Photograph
d40e8e6b-7597-52b2-a5ba-394883a07183 | note | Inspection: Key - C
042a200f-d3fc-5163-bb83-d649db9607a1 | note | Inspection: By - IP/B
cc720413-a9a4-4318-adee-e3a6aca0763c | checkpoint | 3.2 - Delivery of VSD to Site
e926fcc3-1e48-5f5b-910d-f0d7dec1a0aa | note | Inspection Point: Quality Control Activity - Check and verify that correct VSD are delivered and that drives are undamaged
0a701dce-4779-5117-bb11-4bdd7637b32d | note | Acceptance Criteria - VSD are damage free
45123216-e665-523d-bb78-8c965ac2b79c | note | Verifying Document - VSD Delivery documents
927c450b-6da0-5c1a-9cdc-719efaee4d31 | note | Frequency - Once
a4cc56e3-d443-5dc3-8c12-ff505199ad2d | note | Inspection Type (Visual, other) - Visual
ba9fadfb-b4d5-5cab-8e26-384a4c824a43 | note | Inspection: Key - C
fc00601b-667b-5a99-aa53-6d6a11b9319d | note | Inspection: By - IP
bea26331-ec78-4063-b365-ba695662a850 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f205976b-ce14-4e06-af56-87887192ec61 | checkpoint | 4.1 - On-site assembly of mounting Frame
9e6ac5d6-01d5-56a6-afa1-d07750a9505a | note | Inspection Point: Quality Control Activity - materials for frame delivered to site
8a1d6bb1-f172-53b8-87a9-de6461b3d109 | note | Acceptance Criteria - Correct materials on site, protective coatings correct.
963bc178-819b-5a4e-9ec6-1ad00658b112 | note | Verifying Document - Delivery Docket for Materials
cca45854-eb98-5b78-ab6a-26da9eb8e526 | note | Frequency - Once
0e4d0793-b2f2-5310-a009-f9bfff14386c | note | Inspection Type (Visual, other) - Visual
0107fcc8-da26-52dc-9a40-a692cfdd3883 | note | Inspection: Key - I
6a14d11b-1688-5bac-9912-5bc0c11831b7 | note | Inspection: By - IP
9204f331-acd2-4094-8b87-4b7f87a2d091 | checkpoint | 4.2 - Assembly and mounting of Frame
b369c196-c6b3-516a-aaa6-3bbbe3b32442 | note | Inspection Point: Quality Control Activity - Frame Built and bolted to Ground.
54b69342-6b74-5cc3-b1ba-14311fa557f5 | note | Acceptance Criteria - Frame built and Securely attached to ground, minimal flex/ movement when force applied.
c7fe9ac8-f3e6-525c-9c8f-b3426d9b6238 | note | Verifying Document - N/a
045cfaa9-854e-50c0-a255-035130966748 | note | Frequency - Once
1b8549f9-5afb-5129-a784-3024459bc94a | note | Inspection Type (Visual, other) - Visual + Photograph
67ee5aba-98c9-5be6-b794-c23ce8bafb7b | note | Inspection: Key - I
c47c6f63-4d23-5231-be5d-360ffbf07e53 | note | Inspection: By - IP
29e6913e-ce98-4b6a-a993-5e65066dc34b | checkpoint | 4.3 - Mounting of VSD to Frame
21f90df7-b9d5-506a-a2d1-6d989977ef08 | note | Inspection Point: Quality Control Activity - VSD Mounted to frame
5e8062da-6c36-5337-b1fd-c84eb48c1048 | note | Acceptance Criteria - VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used.
b4e55954-9dbf-521b-927a-49a3d24038fd | note | Verifying Document - VSD Inspection Sheets.
544c1703-1944-5dec-a858-315fe9b71eaf | note | Frequency - Once
34b38009-d74b-5a01-a132-ba6b0774bf59 | note | Inspection Type (Visual, other) - Visual + Photograph
43531518-fe1d-5dca-b08d-32a016d059bf | note | Inspection: Key - I
7bb7a2bc-020e-5ec1-9242-234ec1c4889b | note | Inspection: By - IP
f10462aa-c656-45f9-9e5d-0acf00f303b2 | checkpoint | 4.4 - Installation of supply cables to VSD
1535154d-ff9e-53ec-b063-ee730876a191 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into VSDs or switchboard
a3db684f-8908-5fb3-94a4-473619c760cd | note | Acceptance Criteria - Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable
3138948c-61b0-5644-8600-e1f25aeac078 | note | Verifying Document - VSD Cable Test Sheets.
bcef6a0f-129b-58fc-acb2-839efce275e7 | note | Frequency - Once
dcb21b52-fd27-5cae-ae38-c954de75998f | note | Inspection Type (Visual, other) - Visual + Inspection
88657b4e-be97-521b-b5a0-3ca40519b06c | note | Inspection: Key - I
2ee048d6-a97a-54ef-a41b-a01e4f98e8ee | note | Inspection: By - IP
93a3b3cc-891c-43bf-8769-18b34b4ed940 | checkpoint | 4.5 - Installation of Output Cables From VSD to Motors
7c179e9b-3e5c-5e25-b9e8-20e5d923f21b | note | Inspection Point: Quality Control Activity - Cables installed, not terminated at motors or VSD
1d2f3cb5-df59-5d9f-929e-42fd43efad14 | note | Acceptance Criteria - Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable
87406536-8b5a-56f7-8b5e-eea0d8a03acd | note | Verifying Document - VSD Cable Test Sheets.
1ef91cec-2858-5498-90ff-05328fe28de8 | note | Frequency - Once
a971308f-5280-55f0-8203-1090d3b85a9c | note | Inspection Type (Visual, other) - Visual + Inspection
d9a40b50-ab69-567e-95fd-a56648fc48ca | note | Inspection: Key - I
32becccc-2120-525a-ad21-4302f639487f | note | Inspection: By - IP
6834322a-b86f-429a-98da-f4df8a909c4b | checkpoint | 4.6 - Termination of cabling to VSD
26a3b432-9d6a-5737-b5a7-c522ebb54082 | note | Inspection Point: Quality Control Activity - Cables terminated into VSD
5d656b39-29c4-59a9-8870-457de0c65db5 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
62df3caf-cad4-571c-b909-f06301772524 | note | Verifying Document - VSD Cable Test Sheets.
bfa2cf51-8c8b-5978-aa38-238f8d45da16 | note | Frequency - Once
22ce3704-402e-5179-896c-6c7e2e643482 | note | Inspection Type (Visual, other) - Visual + Inspection
398f1e97-c4ee-5e87-bfde-d1abf15e3b20 | note | Inspection: Key - I
46c2d451-8ada-5aac-aa38-f9e1664803d8 | note | Inspection: By - IP
1f50617e-7bec-4c3a-bfbe-c829c347580b | checkpoint | 4.7 - Termination of cabling to Switchboard
d4e50742-f7e8-5d3c-a869-0efee2101bb4 | note | Inspection Point: Quality Control Activity - Cables fit off at Switchboard.
a6cc7cfe-3668-5d8e-b230-46227e11ab09 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
48f8a4f7-1048-5a44-84d4-18fca3238ce6 | note | Verifying Document - VSD Cable Test Sheets.
252dd7fe-78bd-5889-9a36-704e9c88372c | note | Frequency - Once
baccd78e-cc27-5072-be57-ca0d99278868 | note | Inspection Type (Visual, other) - Visual + Inspection
a1045ebd-0251-529c-951a-5df52c876793 | note | Inspection: Key - I
3991e6b9-d724-50c9-8fd4-f24e894327ec | note | Inspection: By - IP
76b886d0-0907-42cf-b5d0-5ad396911d95 | checkpoint | 4.8 - Verification of motors electrically
245e2e0b-14b8-5113-99f7-7194c0a6d8f4 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into motor
ed25256b-35e8-51e6-9357-48ff7f3f1358 | note | Acceptance Criteria - Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate.
4cf608b0-6068-53e5-ada2-693ba7c6ef66 | note | Verifying Document - VSD Cable Test Sheets.
32b18451-a516-5189-abb3-6ee21b707ce9 | note | Frequency - Once
34e2290e-ecf2-5122-8b61-f3b8e65fcef2 | note | Inspection Type (Visual, other) - Visual + Inspection
41eea300-a2a7-5112-bcdc-98c9b57d2327 | note | Inspection: Key - I
09e9a904-09a4-5572-bbcb-122104f75108 | note | Inspection: By - IP
be9dc99c-23fe-448b-9e37-6b57af62aa8e | checkpoint | 4.9 - Termination of cabling to Motor
1d466e69-3466-5035-8b99-b88a610867b6 | note | Inspection Point: Quality Control Activity - Cables fit off at Motor
6cf886a8-10b1-5ade-9402-09c1bb8cebfe | note | Acceptance Criteria - Cables Lugged off correctly, terminals tightened to correct torque
ebe0d2ac-3887-5f19-b621-f24e8446c473 | note | Verifying Document - Motor Inspection Sheets
951e699e-3795-5857-b0a7-c56875b5538c | note | Frequency - Once
5e4a1f89-b885-5cc9-8601-6c97aa4e0aac | note | Inspection Type (Visual, other) - Visual + Photograph
675d23d1-71e0-5f0b-b8d2-56c7532a234f | note | Inspection: Key - I
eb1d5199-2c86-59d9-aad2-b5d98aeac4c4 | note | Inspection: By - IP
97679dd4-ad5c-44c8-9576-4d18e20ddb37 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1055a22c-979f-4231-bd9f-8ca2a1678a13 | checkpoint | 5.1 - VSD
8ef2c718-a6af-5000-851f-2549b9a7b8b8 | note | Inspection Point: Quality Control Activity - VSD Energised and set up, motor nameplate data entered, protections set, Labels attached
9420ca62-f273-5ac0-b52e-780bd4501906 | note | Acceptance Criteria - VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc
2ced564d-e6da-547c-8943-2f7ce7fdcdb1 | note | Verifying Document - VSD ITR Document
886d4fba-5bec-5b8d-8d2c-20b921559b9c | note | Frequency - Once
05f87880-7060-5e87-b8a7-c7d771bd6bb3 | note | Inspection Type (Visual, other) - Visual + Document
846488cd-1f81-5d7c-b284-c8a8809e53ee | note | Inspection: Key - I
52e42ff7-d3af-5902-9617-ca2c3f72fcc5 | note | Inspection: By - IP
c1cd517c-531e-4ce2-a647-93184ee752ac | checkpoint | 5.2 - Motors
ab7200cf-9c69-5c6c-9b01-f724b367cb98 | note | Inspection Point: Quality Control Activity - Assembled and in position, inspection carried out and approved
1d5de886-0223-51dc-ba4e-0cc8aec81f1a | note | Acceptance Criteria - Motors Tested, rotation direction confirmed, pumps operating as intended.
73c3ec5a-62ca-5ff7-986b-d043a7e4abf4 | note | Verifying Document - Motor inspection Sheet
49ce9f86-5dba-5bad-8f46-d729706e9907 | note | Frequency - Once
c57cdebc-e5d2-5d3b-b02f-c6c61e6f59ea | note | Inspection Type (Visual, other) - Visual + Document
3ff45640-1380-5d8e-add6-16a6222bce0c | note | Inspection: Key - I
6ff626d5-607a-5a38-a7cb-4e3d643d0cbb | note | Inspection: By - IP
b45d75dd-4d34-45f0-98ee-64636958e098 | checklist | 561482-ITP-002.3 - VSD Delivery and Installation | itp | 561482-ITP-002.3 - VSD Delivery and Installation
2393c0ea-dfcc-417b-80be-76492c5f4ae7 | section | SECTION 3 – RECEIVING INSPECTIONS
02301741-977c-4570-9026-ec4968bbc621 | checkpoint | 3.1 - Inspection of VSD prior to delivery to site
e638b967-be43-5a38-ab2f-dbe16a4f525e | note | Inspection Point: Quality Control Activity - Check overall condition of packaging, noting any obvious signs of damage, Check rating of drives is correct.
7014054f-75ed-587b-a7ac-598ecc501cbe | note | Acceptance Criteria - Visual check and report any defects or areas of concern
d9c9d92d-ea71-5879-8998-27af8cee43b7 | note | Frequency - Once
ad593165-5832-58d8-8591-810e1f29878a | note | Inspection Type (Visual, other) - Visual + Photograph
6314ffff-d3e0-578a-a460-1a8da9d5f399 | note | Inspection: Key - C
439e7077-358c-50d2-89cc-ba0645d453e1 | note | Inspection: By - IP/B
d9f1c287-66b4-449f-b4e6-da9e8531f985 | checkpoint | 3.2 - Delivery of VSD to Site
64beadac-c488-572e-a976-aab39d24e57a | note | Inspection Point: Quality Control Activity - Check and verify that correct VSD are delivered and that drives are undamaged
545419a7-4392-5834-94de-10f8849cf5e9 | note | Acceptance Criteria - VSD are damage free
fe10d294-beea-5df8-823b-1e65ad6c317c | note | Verifying Document - VSD Delivery documents
87e165a1-cab3-5270-a69c-4ca2958cd900 | note | Frequency - Once
6510bdfd-4d32-5c51-a90b-87d397f09306 | note | Inspection Type (Visual, other) - Visual
6f6a1a49-059d-556d-9bf0-96fe87167e60 | note | Inspection: Key - C
65383a29-6ea4-5ff4-ab4d-4ed24cd1a9a5 | note | Inspection: By - IP
2f564d66-eb7f-4589-8d3a-78006ef4cf80 | section | SECTION 4 – IN-PROCESS INSPECTIONS
e00cc8a3-f665-4563-8c32-97513f1aa4a7 | checkpoint | 4.1 - On-site assembly of mounting Frame
0fb44e38-7e46-5430-b5eb-f17df98ef34c | note | Inspection Point: Quality Control Activity - materials for frame delivered to site
42f1a079-321f-5de4-9271-6e357b02ae91 | note | Acceptance Criteria - Correct materials on site, protective coatings correct.
254aa36f-6ae9-5712-963f-ef9ae173b91e | note | Verifying Document - Delivery Docket for Materials
e9f60b3a-1bf1-5f95-8778-56c400aefc77 | note | Frequency - Once
619c9776-feb0-5f00-97ef-414148aca636 | note | Inspection Type (Visual, other) - Visual
36db81c9-cb50-570f-9997-16641910ba65 | note | Inspection: Key - I
17682ce3-557f-566d-bcda-cfb9356bd3c2 | note | Inspection: By - IP
a110b86c-a8fb-4247-a6d5-23c11aa9e903 | checkpoint | 4.2 - Assembly and mounting of Frame
90aab059-67d9-5a0d-86ca-32dd766aed31 | note | Inspection Point: Quality Control Activity - Frame Built and bolted to Ground.
6019cbfd-b08e-5e27-b39e-1b11938b77b6 | note | Acceptance Criteria - Frame built and Securely attached to ground, minimal flex/ movement when force applied.
a8eb00d2-3b03-55d0-aa0d-15bba2e4130a | note | Verifying Document - N/a
570a059a-9265-5adf-9018-0127d868235d | note | Frequency - Once
9ab30dc7-7f36-5013-8b4c-2562d72e57b9 | note | Inspection Type (Visual, other) - Visual + Photograph
6fff6911-0fae-5502-9986-7c2f85d49c0c | note | Inspection: Key - I
2e0011e5-8bff-5726-9b52-ae5d7296bc24 | note | Inspection: By - IP
7f25864b-cfc7-4106-ac16-1ea478271a3a | checkpoint | 4.3 - Mounting of VSD to Frame
e9f0c403-ba0e-59e4-ae98-aa3fb5309aeb | note | Inspection Point: Quality Control Activity - VSDs Mounted to frame
738a8ff6-8e25-5ef1-91d2-c84e897c09dc | note | Acceptance Criteria - VSD Mounted satisfactorily, bolts tight, washers and spring washers present, S/S bolts and fixings used.
df81cc09-cd70-5c72-b6c1-57dbd8e88eb9 | note | Verifying Document - VSD Inspection Sheets.
35153245-d380-5dd4-b5e7-4452d543183c | note | Frequency - Once
75f9c373-27e7-5798-9399-d87c4a7e6b49 | note | Inspection Type (Visual, other) - Visual + Photograph
acc4a448-3560-57cb-807e-fc8486e840c0 | note | Inspection: Key - I
6e390a68-2210-5a96-bbc5-fa45c5b996b6 | note | Inspection: By - IP
85a6bf5d-9b19-4899-bc8b-b03edafaea00 | checkpoint | 4.4 - Installation of supply cables to VSD
acbc88d1-faa8-5399-ac5a-2cb799b4e6c3 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into VSD or switchboard
ebffbd7f-f728-5ec4-89f3-e887934c0324 | note | Acceptance Criteria - Correct Cables installed, suitable for full load plus 20 percent of VSD, insulation resistance acceptable
0accc637-1d48-58b1-86a6-7d1c0cd34d6f | note | Verifying Document - VSD Cable Test Sheets.
13396456-6553-5c40-aac6-b6d5eae29bb4 | note | Frequency - Once
b196647e-0413-5efd-92d5-6e8be52688dc | note | Inspection Type (Visual, other) - Visual + Inspection
410070d9-b730-5ebe-a1ae-d826fd3b2809 | note | Inspection: Key - I
fd0bdc50-73e9-5cb5-ae6e-09d82d6c10b0 | note | Inspection: By - IP
59470769-4953-47e1-8289-c613cdaa7a17 | checkpoint | 4.5 - Installation of Output Cables From VSD to Motors
07d1e711-a0af-5b80-b10e-bc42da38374c | note | Inspection Point: Quality Control Activity - Cables installed, not terminated at motors or VSD
a0ccb903-93e9-501d-82e6-b08d114104ce | note | Acceptance Criteria - Correct Cables installed, suitable for full load of motor plus 20 percent, insulation resistance acceptable
d2368aa1-d892-5de8-9bb6-7abf419380c2 | note | Verifying Document - VSD Cable Test Sheets.
7b2701f4-05de-57ff-99ea-7a3679f67d13 | note | Frequency - Once
f52baad8-e62c-5f77-ab58-0970824f275b | note | Inspection Type (Visual, other) - Visual + Inspection
8a94a4f6-05e2-5c2e-9d09-6cdcaab92e5a | note | Inspection: Key - I
ceede671-448f-59db-9ca1-0d86bad5b02c | note | Inspection: By - IP
59850520-005d-4fed-896f-3729b6d7dffc | checkpoint | 4.6 - Termination of cabling to VSD
f17d8d90-f783-5d25-b66e-3be2f6862d5e | note | Inspection Point: Quality Control Activity - Cables terminated into VSD
925ad370-5c9e-51ec-881f-2bca7f6df065 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. cable earths and screens fit off correctly.
a6650d2d-90d5-5b9b-9e81-7ade985660d8 | note | Verifying Document - VSD Cable Test Sheets.
bacf4799-c741-513a-bfca-c42f987287e1 | note | Frequency - Once
67fc7851-baa4-5cd1-a89f-9e6c46db6e15 | note | Inspection Type (Visual, other) - Visual + Inspection
194f6f70-691f-54e2-a9cd-5485b6d436a1 | note | Inspection: Key - I
a527cc14-881a-5182-a073-e5514b23093d | note | Inspection: By - IP
2ceeb426-5c7d-499a-b151-110aa422135f | checkpoint | 4.7 - Termination of cabling to Switchboard
95fdd7db-4547-51cc-813e-2aff2ec6cbde | note | Inspection Point: Quality Control Activity - Cables fit off at Switchboard.
568e280e-e868-56c1-98ae-6f4237d90ac2 | note | Acceptance Criteria - Correct Cables installed, terminals tightened to correct torque, cables prepared correctly. Cable earths and screens fit off correctly.
96c74336-f0f8-518a-b748-bf5192fb231e | note | Verifying Document - VSD Cable Test Sheets.
d398e7b9-1653-5252-b979-84781a90dff8 | note | Frequency - Once
be9c959c-9a07-541d-80e1-829ff093f858 | note | Inspection Type (Visual, other) - Visual + Inspection
4997927f-3e18-512a-93f1-57e94ab7b21d | note | Inspection: Key - I
10bb3b16-ef05-5dcf-b6dd-e731f606dad6 | note | Inspection: By - IP
f57b317d-5672-4e55-ac06-d35bb9f208fd | checkpoint | 4.8 - Verification of motors electrically
c3cb97fd-358a-57d9-93ba-9aa42ee9dbb6 | note | Inspection Point: Quality Control Activity - Cables installed, not terminated into motor
10b5cbda-8f33-5b22-8fa4-38cbb7b5be2b | note | Acceptance Criteria - Correct motors installed. insulation resistance verified, winding configuration confirmed against nameplate.
741911a7-fb1e-5493-9ad9-bb57074a662c | note | Verifying Document - VSD Cable Test Sheets.
aad5d5bb-4923-595c-8559-f7bb99cd3267 | note | Frequency - Once
63dbc81d-e794-5736-85fb-a5706177f0ac | note | Inspection Type (Visual, other) - Visual + Inspection
2929316c-7df4-5011-97c1-5b5b90c000bf | note | Inspection: Key - I
11e5ebdb-8850-52f3-b2ac-3598774fec99 | note | Inspection: By - IP
317e4470-5aba-4e78-99c9-2d0cc15c8595 | checkpoint | 4.9 - Termination of cabling to Motor
3ca3b56b-5d6c-52b5-9229-46bb5d120b13 | note | Inspection Point: Quality Control Activity - Cables fit off at Motor
db1c9caa-ce99-5d55-a4b3-4799bab29858 | note | Acceptance Criteria - Cables Lugged off correctly, terminals tightened to correct torque
794a234b-4103-5a9d-b34d-5c586a6a1746 | note | Verifying Document - Motor Inspection Sheets
c00d6a0e-1412-5aa3-b0f7-fe326c32bf95 | note | Frequency - Once
0bc28977-659b-55a2-96e2-6ebea1733300 | note | Inspection Type (Visual, other) - Visual + Photograph
4302563c-2b41-50da-ae1c-e23361c80aeb | note | Inspection: Key - I
a86151a8-2e1f-504a-898b-238126ee6f64 | note | Inspection: By - IP
ff38ecbb-be6b-4e07-a3b7-86e0e42f4e43 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1e8ddea4-4883-4d29-ba6c-14385ed7bc68 | checkpoint | 5.1 - VSD
e621889d-32c0-5ec1-bd92-62f18fdd4e1d | note | Inspection Point: Quality Control Activity - VSD Energised and set up, motor nameplate data entered, protections set, Labels attached
23c379e9-4792-5fcb-b289-842a66b469ad | note | Acceptance Criteria - VSD parameters set correctly, inputs set up as per drawings. analog i/o set correctly and verified to plc
91102be6-ef4d-5e9a-8255-48d8833a0b1b | note | Verifying Document - Switchboard acceptance test sheet.
cd706da6-5285-5f12-b394-26993e531161 | note | Frequency - Once
b8adc75e-77a2-5fd5-a6f9-e311ea4dda96 | note | Inspection Type (Visual, other) - Visual + Document
3745b8aa-ee6f-5426-901a-a7cd72daae21 | note | Inspection: Key - I
48eae12f-2423-5d4c-97f8-9b72593dcff2 | note | Inspection: By - IP
b5dda0fb-6adf-480d-8233-dbb814a694cc | checkpoint | 5.2 - Motors
26e71cf3-817a-504e-b860-ce675f96bf59 | note | Inspection Point: Quality Control Activity - Assembled and in position, inspection carried out and approved
3cda3185-0ba5-5196-8275-baeb28a765ed | note | Acceptance Criteria - Motors Tested, rotation direction confirmed, pumps operating as intended.
3cb5c9d3-0eaa-5fe3-a8d4-dc872bbbcb19 | note | Verifying Document - Motor inspection Sheet
f3082fc4-7eaa-5f55-8ea1-3dbe2c683ee1 | note | Frequency - Once
8b710a90-5f40-5869-86f7-cc5a04481ddb | note | Inspection Type (Visual, other) - Visual + Document
efa02dad-cd6c-5d02-b43f-3e16694c3dc8 | note | Inspection: Key - I
b1af8750-ea34-5257-bb72-03a5e0c85a4f | note | Inspection: By - IP
288bb8ed-b7cb-4300-9722-89f072634305 | checklist | 561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation | itp | 561482-ITP-003.1 - Wet Well Wall Penetration 1 preparation
70d2b7d8-0f17-46af-aa25-bb4162eb20bb | section | SECTION 3 – RECEIVING INSPECTIONS
831d5383-d131-4131-a95a-0695bb228c43 | checkpoint | 3.1 - Masonry drill bits 18mm
2f2ec1d4-b5c9-5022-9ebf-331b19e64cea | note | Inspection Point: Quality Control Activity - Verify correct quantity & type
50c297ef-6a44-502b-b686-521bd8cdc41c | note | Acceptance Criteria - Compatable with the drill unit
0dd98786-2f63-5823-b9c9-168a0cc435f2 | note | Verifying Document - Manufacturers Technical data & Physical fitment
00956f22-44e6-5bdc-9eb6-f26fda4f86c7 | note | Frequency - Once
4ed4d68c-4b9d-5d85-be2a-61fab0741828 | note | Inspection Type (Visual, other) - Visual + Photographs
057f0f5d-ec13-5466-9f36-69d71ade2670 | note | Inspection: Key - Inspection
1b9e42cb-559e-5ac8-8519-26309831c833 | note | Inspection: By - IP
51256ae4-f8eb-4aad-9388-5f99b54dced9 | checkpoint | 3.2 - Reinforcing Bar
e0df326f-cd3a-5d35-a021-5592c6300caa | note | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
a6a88c20-ce85-5979-ab7e-ef7fb5ded6f2 | note | Acceptance Criteria - Quantities correct. Dimensions correct.
92a27d7d-2361-585b-ada9-1cead959f190 | note | Verifying Document - Drawing M0003
c94061b2-051d-5df9-a86e-2074c12f5e2c | note | Frequency - Once
b4d02de9-89aa-59e7-8449-6529e6bfbf46 | note | Inspection Type (Visual, other) - Visual + Photographs
8920a18e-6b43-5c24-b2b7-0e3aacc21fc2 | note | Inspection: Key - Inspection
572dd9aa-1097-52c7-8f3b-70c99df509c8 | note | Inspection: By - IP
d8f4b626-be11-4e01-8397-e0a095c44a74 | checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
cf43255c-3e3c-5677-a7c4-6e862617f647 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
8931543f-3473-555b-b872-e55facacc074 | note | ○ Check expiration date.
63f3b29d-808b-574b-b458-ccb01de62485 | note | Acceptance Criteria - Quantities correct. Within expiration date
4248694b-5436-543d-9649-0731ee7dee54 | note | Verifying Document - HILTI Product Calculator APP. Delivery Docket
cbaf1df7-cef0-5860-8099-15573a209ef1 | note | Frequency - Once
3dbc79ac-85a5-5884-b58d-4c0c5dd6a773 | note | Inspection Type (Visual, other) - Visual + Photographs
238b3ed0-ad63-5e23-b5b5-9e650693bb72 | note | Inspection: Key - Inspection
4940acd8-3de9-58c8-9cd5-71666d24c7b2 | note | Inspection: By - IP
07963279-7330-400c-b183-282f8d249eb3 | checkpoint | 3.4 - Grout (Sika MonoTop 438R)
b3f2cbb0-a459-5f15-bc1b-68b0bfb7dc01 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
bebdb64b-ffbd-57fa-9eae-b759d47ed83a | note | ○ Check expiration date.
15b32474-7cee-5782-ad3b-4dabfcf1a2a5 | note | Acceptance Criteria - Quantities correct. Within expiration date
67b69021-00f7-59ea-b0ed-f8fad4183ea3 | note | Verifying Document - Delivery Docket
00a3afdf-770a-5d5a-9920-beef582dea14 | note | Frequency - Once
6cdc79b1-4c01-5f78-a867-370801cffd23 | note | Inspection Type (Visual, other) - Written/Submission
bbb63290-b8ae-5c9b-b1ad-62197ba21183 | note | Inspection: Key - Inspection
163c630c-ef83-50a8-9da1-02d27d0e4ce9 | note | Inspection: By - IP
628ee1fc-3780-44ee-adae-cbea0708361a | section | SECTION 4 – IN-PROCESS INSPECTIONS
97d347a8-108f-4510-a740-0fcaf4b5c661 | checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
b9e50428-bc80-59e3-9f0c-b1f639725e2c | note | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
edce4d73-347e-5386-a0d8-7cd4c15697fa | note | Acceptance Criteria - Approval from Engineer
f9010629-d394-551f-94b0-64116706d71f | note | Verifying Document - Drawing M0003
768024bd-f85a-5b9f-8a1e-938725fb20ff | note | Frequency - once
25373ab7-82a1-557b-ab54-fce66130b41f | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
4fb18328-b59c-5d33-a7ac-4627bda16e4f | note | Inspection: Key - V
371dcc04-417d-5f8e-80fb-c489a1658b56 | note | Inspection: By - CR
549e2aeb-3e36-4013-a0b3-b5173363e8c7 | checkpoint | 4.2 - Proceed with breakout. Hammer drill
f978e7dc-ec13-52fc-a6af-69f263e5ea7c | note | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
a2fd2d9c-9faf-5c01-a692-89c9ee75e0a6 | note | Acceptance Criteria - Approval to proceed from item 4.1
75900694-3c87-5cc5-ac40-5659a7985458 | note | Verifying Document - As per drawings listed dimensions & measurements
fc8beb5a-170e-5c34-998e-599f26cde7e8 | note | Frequency - once
3c036cfb-bc33-5b19-8f55-a86370b1e560 | note | Inspection Type (Visual, other) - Visual & Document
acf8a47d-30af-5ff2-853b-cf991c1da4ef | note | Inspection: Key - I
65361f03-4181-550e-ac46-ead919526566 | note | Inspection: By - IP
86c81254-a297-43e4-90e2-25971925947c | checkpoint | 4.3 - Pre-pour inspection
4d426552-4e3d-53a8-b844-0b6fc5f2951c | note | Inspection Point: Quality Control Activity - Engineer Inspection
b4e6bd5f-c0e3-56df-abb3-dd9e38a26290 | note | Acceptance Criteria - Dimensioin & Surface check. As per Drawing M0003 and notes.
62e9e1ff-6f39-5433-a616-6ba944b7a87c | note | ○ Approval to proceed via NTC.
06fa3152-e975-544f-9fa7-630fc7adc1a2 | note | ○ Correct profile achieved with 5mm roughness and any loose material removed
8702d979-e249-5a09-852f-30e4c4877c13 | note | Verifying Document - NTC or other written confirmation
b2442aed-3eea-55f7-97e3-4b22676b7594 | note | Frequency - once
0b41513a-208b-53c9-b461-933b716afc01 | note | Inspection Type (Visual, other) - Document
91467593-807b-52af-9f52-b0fa8c58f010 | note | Inspection: Key - H
253a022c-ee53-5d22-aa11-8fb14f56f1f3 | note | Inspection: By - CR
210e4ba5-1099-41cc-af18-2bc4ed10e931 | signoff | AUTHORITY HOLDPOINT
a82c2e9a-980a-44c0-b8e9-d90ab8bd6329 | checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
fb6203dd-fd1c-53f3-8b38-65fb11d6da7a | note | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
acf6bd14-76ba-57be-9bab-925efa7d5ba1 | note | Acceptance Criteria - As detailed on Drawings & specifications
e29d11a2-4f8a-594f-b47b-bff668a7081a | note | Verifying Document - Drawing M0003
d50ab8bc-dad3-5791-aed9-6dcdf4e63eaf | note | Frequency - once
4f4fbf52-631f-5b6f-b933-aa71361ae6bc | note | Inspection Type (Visual, other) - Document + Visual
740c2857-55b9-5885-8381-49c2c21de75f | note | Inspection: Key - I
b62bf4f2-ec40-50c5-aa83-69722c44b737 | note | Inspection: By - IP
55902cda-a715-460a-b173-131876a08525 | checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
0cb8c155-69a7-52ec-b72a-c16a8342e3a5 | note | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
72e0f55b-4f92-536e-96a3-a73c28f2a773 | note | Acceptance Criteria - As detailed on Drawings
715e818d-a28c-5c5d-b11b-e2e8f90fe7d1 | note | Verifying Document - Drawing M0003
29e45e54-2233-54bf-8a6f-0690e1a84358 | note | Frequency - once
eec6bdcc-24c3-5a1f-b3d6-788daac4d1b2 | note | Inspection Type (Visual, other) - Visual + Photographs
8a1dcdac-70bf-5072-b67a-530e786ac3eb | note | Inspection: Key - I
4d40c43e-4291-5357-836a-823f5ce559c1 | note | Inspection: By - IP
2d3be309-151c-4c8b-887e-b456cf37fa91 | checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
e65f1e4f-f759-521f-84da-4c5d2e50cea1 | note | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
3fb0b602-03fa-5018-a6ca-f20f81b00e2e | note | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
f234fa9d-3bd3-5072-97dd-c1ea57f91372 | note | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
0eba833b-cf6a-51f3-9aa9-bd558e627639 | note | Frequency - once
1564d1a8-b262-53db-a63d-f6ae24fcb73c | note | Inspection Type (Visual, other) - Visual + Photographs
15a61dd4-96c4-57ca-9a10-4e769bcc8f73 | note | Inspection: Key - I
d9e96fae-6ccc-53eb-920b-a9b3f842028e | note | Inspection: By - IP
4eddd335-7245-4395-97f1-f5ab7ce82d1c | checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
5947a888-b60e-5179-9c6f-6552260830a6 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
b14be2b8-b394-5adf-82d3-d9fb08f1b8e1 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
3bcd08f7-d2e2-537a-acc0-6f44075fc2a4 | note | Verifying Document - Drawing M0003
d8ded1b7-af78-5865-a078-9808545d84f5 | note | Frequency - once
c3cb1422-7d65-5867-846a-957f6cbd8934 | note | Inspection Type (Visual, other) - Visual + Photographs
e3928c7f-42d8-52c3-8598-9803dcbb4df6 | note | Inspection: Key - I
aaf6a2d9-39ba-56fc-b7e1-788813939b44 | note | Inspection: By - IP
b5d09d7b-b5c4-4d3f-8301-a4dd5a9a79fa | checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
f8bd7d98-a5c0-56a7-99c1-f8d3da09d1c3 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
671043ea-04b7-5ed0-a91f-164a70ad2757 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
18c5924f-4585-5dfe-ab31-6c0ed738bb80 | note | Verifying Document - Drawing M0003
53bb8161-5907-54f4-aa74-59b07dbd7018 | note | Frequency - once
3b32276f-81bb-5606-8f35-43a758ee2d10 | note | Inspection Type (Visual, other) - Visual + Photographs
c4905fe5-5b51-53e2-822b-c03ad891c555 | note | Inspection: Key - H
ce7ce692-a20c-50a2-9d7c-f5c22ec720ce | note | Inspection: By - IP
f4956bf3-31e3-4a59-9c8b-80ccc557eaf2 | signoff | AUTHORITY HOLDPOINT
3914c02b-767a-42e3-a8f5-48cca0445bb0 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
5281b3a1-ab7f-4902-a52e-9ebbae8ae090 | checkpoint | 5.1 - Final dimensional check
25005eb0-4ff0-5928-80ff-77a475076d7d | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
42f26a64-1d2e-5e62-b3e4-48919c618ef4 | note | Acceptance Criteria - Dimensions match the measurements shown on drawings
23d0a6c3-4477-52bc-8287-b532c99d2a50 | note | Verifying Document - Drawing M0003
4eb438bd-f9f6-5c24-ba2f-ef3927a0abe9 | note | Frequency - once
8f06c144-4ad1-5e1e-a966-ea3a846ff20d | note | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
0ebbc0ec-9fe0-5fea-b995-e6bf6f4de2ec | note | Inspection: Key - H
993797aa-e298-52fe-97f5-2a4bca1e6a33 | note | Inspection: By - CR
532cfe1f-4f8b-4745-ac7d-b1aeaf75317a | signoff | AUTHORITY HOLDPOINT
1ba94c58-b0b3-4a2f-a2b7-f7d80d3e1ad1 | checklist | 561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation | itp | 561482-ITP-003.2 - Wet Well Wall Penetration 2 preparation
b1169e19-b01c-4802-9a47-1bfec0c5fa54 | section | SECTION 3 – RECEIVING INSPECTIONS
bd566547-d426-4bfb-bc76-aaca0030a492 | checkpoint | 3.1 - Masonry drill bits 18mm
1a2de801-2662-50be-9ae4-267e7434adf1 | note | Inspection Point: Quality Control Activity - Verify correct quantity & type
1049b679-346b-57d4-8852-3bfb97047003 | note | Acceptance Criteria - Compatable with the drill unit
aea93f94-318d-5b67-9399-ee2aff0cdf2b | note | Verifying Document - Manufacturers Technical data & Physical fitment
fe23cc55-2ddf-5d36-8417-2c293687b49c | note | Frequency - Once
b8662d38-4ff9-5533-9ab3-0df4a31b8e2f | note | Inspection Type (Visual, other) - Visual + Photographs
5b690832-cd26-5838-9760-eb736079fe11 | note | Inspection: Key - Inspection
8e8b335e-7d51-5aad-aaeb-1bca6648b5b1 | note | Inspection: By - IP
e3daef1d-734c-43b2-8e60-a85916754393 | checkpoint | 3.2 - Reinforcing Bar
490034f7-1636-588a-8189-5e0aaa600d3e | note | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
b9227575-7b66-5226-b9a6-b87e5d6bd9fa | note | Acceptance Criteria - Quantities correct. Dimensions correct.
5097db3f-5d3c-580a-b50f-97b4a5897bb4 | note | Verifying Document - Drawing M0003
8950332e-043d-5d8b-b6bd-4232275da2a0 | note | Frequency - Once
0698354b-dca2-511e-8a80-8aa2ea2e454e | note | Inspection Type (Visual, other) - Visual + Photographs
32f696cf-389d-5bcd-82b7-ca779640d76b | note | Inspection: Key - Inspection
1f24ee52-9dfc-5998-a7c3-8b5db42c22ab | note | Inspection: By - IP
a30251df-2aa5-4961-80ee-b23dacd44141 | checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
70792bd7-7869-51e3-a82c-d3b24803d948 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
50c392c4-b68e-56dc-9cab-949278f985b9 | note | ○ Check expiration date.
31671e94-738b-5e04-9ec0-ab62c2085c97 | note | Acceptance Criteria - Quantities correct. Within expiration date
7af6b21a-6c3d-5879-91f7-1590f5e3c974 | note | Verifying Document - HILTI Product Calculator APP. Delivery Docket
26ddd092-3c5c-5bfd-b5bd-33be2b07a30e | note | Frequency - Once
ab99e089-0b8c-5fbe-8747-f95d688e69e2 | note | Inspection Type (Visual, other) - Visual + Photographs
34f567c9-a5e7-55ab-874d-114ec3395375 | note | Inspection: Key - Inspection
626a6d89-baaa-571a-91c0-80ed41c53b8d | note | Inspection: By - IP
0a10b923-c9d6-4011-9dbb-086214e82e6d | checkpoint | 3.4 - Grout (Sika MonoTop 438R)
0ab4a437-4317-5a4d-86c7-1acc2cef33c3 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
4b1ab8dc-0f92-5dc0-b8c8-6f3c953ef307 | note | ○ Check expiration date.
d2473af5-b90f-5501-80a9-3f91e67e42a9 | note | Acceptance Criteria - Quantities correct. Within expiration date
16a6ebbf-ea5a-501a-b8a4-94f8dd992c13 | note | Verifying Document - Delivery Docket
6c3028ad-7b92-51e0-b299-afd85c400a5d | note | Frequency - Once
0ec81f21-4359-5fe6-845b-4b7582264ee0 | note | Inspection Type (Visual, other) - Written/Submission
73e0511e-54ad-51de-a908-6cb4ce7e7c3d | note | Inspection: Key - Inspection
5941e82f-3d35-58e7-bb55-f27a6114b10d | note | Inspection: By - IP
fc152f8e-c6c9-4475-911e-a2dfd4391ba6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
76ec880c-e101-4ad5-9f75-293958dc9853 | checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
19c1fec6-0b04-5997-8a32-03a77935b4ee | note | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
cb3e2d79-373a-5c49-b2f8-20fdfec1451c | note | Acceptance Criteria - Approval from Engineer
90802df0-e025-5a18-a693-035fca4b8d98 | note | Verifying Document - Drawing M0003
8efa5235-d7d8-525a-8ebe-f80aa3667092 | note | Frequency - once
90881e0e-89d2-5733-b6ea-99218b24870d | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
05f6f690-2774-5284-bb27-db401829b25f | note | Inspection: Key - V
5ccf52a2-7c9e-575b-ae74-42903f2e66f4 | note | Inspection: By - CR
53ccfa49-87a1-4f1a-8793-54839f0c799f | checkpoint | 4.2 - Proceed with breakout. Hammer drill
ecc8fb97-7a56-5f5d-a364-a10b3b7e17da | note | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
429d2ae8-8a4a-5aa1-82da-4e216ae34ee4 | note | Acceptance Criteria - Approval to proceed from item 4.1
987ee841-930d-5071-b36e-59b7d71066a3 | note | Verifying Document - As per drawings listed dimensions & measurements
0c39f5d4-cb43-5adc-9c90-f106abc00d21 | note | Frequency - once
794a557b-21e1-534c-8d3d-a7fecfb56840 | note | Inspection Type (Visual, other) - Visual & Document
a625a9c8-a09e-59ba-8b67-fee6d95770cf | note | Inspection: Key - I
c1f94467-9558-5cbc-aab2-c9e476f784dc | note | Inspection: By - IP
f4cb6c2e-97ff-4302-ae1f-2ce295e74344 | checkpoint | 4.3 - Pre pour inspection
2394dd60-ca48-5bf3-809d-ae9fe164f1f6 | note | Inspection Point: Quality Control Activity - Engineer Inspection
855a76be-0015-5e8e-b0cb-178286ae117e | note | Acceptance Criteria - Dimensioin & Surface sheck. As per Drawing M0003 and notes.
3853936e-0caa-5f85-8fc5-1d56239b2028 | note | ○ Approval to proceed via NTC.
514b90d3-ab7f-5748-8bdf-3061957011ec | note | ○ Correct profile achieved with 5mm roughness and any loose material removed
8720d665-db13-56d4-87a2-27ecb0bc0854 | note | Verifying Document - NTC or other written confirmation
ee140a13-e954-509c-ab91-48d6648cf37e | note | Frequency - once
b3b11926-61e6-5bb4-8dd8-4e439ce33bf5 | note | Inspection Type (Visual, other) - Document
7a9aebbb-1129-5803-84e9-e0fcd82d9fba | note | Inspection: Key - H
8c0a229c-c5cd-5b6e-af90-cf50a501d3c9 | note | Inspection: By - CR
6061b745-b578-41c0-8d2b-32686098d6bd | signoff | AUTHORITY HOLDPOINT
34b642b5-d84c-4c6a-84fd-ea1cb2488072 | checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
a33c6a55-b703-560a-8c77-2e618c753677 | note | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
b91b352a-46f7-5fbf-bbbb-e03ae6883737 | note | Acceptance Criteria - As detailed on Drawings & specifications
79e108fa-c139-5e3d-a71e-d770acbb0180 | note | Verifying Document - Drawing M0003
46db40c8-88af-50cb-b8fd-87c9a77b9580 | note | Frequency - once
28d15d0a-4633-5509-9f55-9127761eba18 | note | Inspection Type (Visual, other) - Document + Visual
d14e6927-aa0e-5f35-89bf-d79f0a3ba9e3 | note | Inspection: Key - I
9833d1bd-4b2d-5e9b-9fba-354848efbab8 | note | Inspection: By - IP
8d125455-4968-43d2-9488-9dd64c336adf | checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
dee6e842-2af2-5ec3-8dcb-36aff3461ab8 | note | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
8a5e25af-1eea-551d-9f13-1ca04a8fcf95 | note | Acceptance Criteria - As detailed on Drawings
8542aba5-15a9-5b0f-a41f-285a9259a3cf | note | Verifying Document - Drawing M0003
e3f904a4-b6e5-578e-ad09-1c20d7cefbe7 | note | Frequency - once
42333b53-df33-5244-af8a-3fd2e384add4 | note | Inspection Type (Visual, other) - Visual + Photographs
887ec9f6-7381-5bfd-ac21-7983f0a6c166 | note | Inspection: Key - I
5206384b-6500-5738-a44c-25dc16e27687 | note | Inspection: By - IP
4ed548f2-1735-4d07-a1a8-d7395a5edeb4 | checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
137c0236-9139-55d9-9ce2-f2b7fdf27331 | note | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
9d650d33-9c9a-5a82-bb1a-5b824618430d | note | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
bf1bba4c-d06b-5c58-9ef2-cc8455a7c1f6 | note | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
bb56db9c-101f-574c-a936-e79a3bfaf3ec | note | Frequency - once
8974ee04-443e-57b6-a98f-da2416588dd6 | note | Inspection Type (Visual, other) - Visual + Photographs
7fab25a2-38c9-528c-8b7d-f6f4bad2491b | note | Inspection: Key - I
26da9048-7c3f-5630-afc1-74758ffb6fda | note | Inspection: By - IP
bc49a98b-da60-4346-8847-1459b67777cc | checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
64390c44-299d-51ba-9030-1d0c83cf98e8 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
0c135c3a-6ccf-5bff-a780-b7b672622a82 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
2005bf83-6d96-5395-94db-aa167895f5dd | note | Verifying Document - Drawing M0003
a942370c-2e1d-5255-b8e7-6c2cbbf90c03 | note | Frequency - once
05ced271-f35d-5eb4-a7ec-8346d9942736 | note | Inspection Type (Visual, other) - Visual + Photographs
34dc0e04-1877-5350-b233-a1d35f59db1e | note | Inspection: Key - I
c706d622-ed4b-535b-8bdc-5116b072f810 | note | Inspection: By - IP
66e245ac-0be0-46e1-88e6-220f6763a588 | checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
ce31c908-1efd-53e5-8abb-052d4ce54590 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
6fa29dba-0a3f-5c98-9f6f-3e3875bd36f9 | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
84255bb7-fc6a-5e25-9d6f-8104025cd09b | note | Verifying Document - Drawing M0003
c348a5bb-960f-500b-a9da-916cd9781430 | note | Frequency - once
772a7167-205f-5cf3-ac86-7d33015cc379 | note | Inspection Type (Visual, other) - Visual + Photographs
d08dceca-7ee0-508d-bc08-c306cc6d6819 | note | Inspection: Key - H
e7b79494-b0bb-5111-b8c6-cdde001f5a36 | note | Inspection: By - IP
613ab478-b1af-4f60-b9b2-32c453d259be | signoff | AUTHORITY HOLDPOINT
6c03f36d-008b-4d71-bfc0-819596f9ad63 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c2b141c2-efa7-4370-8868-7d93a82737af | checkpoint | 5.1 - Final dimensional check
c88c326a-661c-5f9e-8437-e85c2ff9c667 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
f86f00e5-9f04-562f-85f2-4423ece7ebfe | note | Acceptance Criteria - Dimensions match the measurements shown on drawings
0f36af1f-1d1d-5ada-90e8-182ecc283d03 | note | Verifying Document - Drawing M0003
5a82595b-ef88-5269-ba41-b5434253666c | note | Frequency - once
9bb9331f-c92d-5586-8d73-904a8f6c697d | note | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
d398248e-e32d-5f39-8d0e-594355ba4544 | note | Inspection: Key - H
73ad91b7-e3ee-5891-8aab-1dfbb3577155 | note | Inspection: By - CR
9ceaf1d0-3dcc-46a5-a7fa-08ff883c44b2 | signoff | AUTHORITY HOLDPOINT
1dc760eb-f1f5-4f4a-bca0-a0031132081b | checklist | 561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation | itp | 561482-ITP-003.3 - Wet Well Wall Penetration 3 preparation
5ed444c4-65b6-4d53-9046-3459123349d7 | section | SECTION 3 – RECEIVING INSPECTIONS
a9b5b906-95d9-4868-8f2d-6760c6fd566b | checkpoint | 3.1 - Masonry drill bits 18mm
c4a56371-f7fc-5cc2-b574-78e4277251a1 | note | Inspection Point: Quality Control Activity - Verify correct quantity & type
eccef8bf-a8af-5d3b-86d6-44d95e309c27 | note | Acceptance Criteria - Compatable with the drill unit
43423ac1-6857-5b3d-bde1-e87d1808e0a8 | note | Verifying Document - Manufacturers Technical data & Physical fitment
2aa2b0fd-f8b7-5795-8228-bb5ad76521e4 | note | Frequency - Once
767c77c5-8ef6-540e-ac1f-4a2c2c072652 | note | Inspection Type (Visual, other) - Visual + Photographs
91d4778f-b80d-5f10-b867-6c32cfa8df6b | note | Inspection: Key - Inspection
4ecf6cab-b4a1-56bb-bc4c-a3455af0732c | note | Inspection: By - IP
acbe9a7b-e785-4fda-90a1-a10095cfb745 | checkpoint | 3.2 - Reinforcing Bar
98ed4f1f-0e02-5f01-9795-02dfde9772a0 | note | Inspection Point: Quality Control Activity - Verify correct quantity & size/diameter has been delivered to site
bad348d8-f1c2-5abc-a3f3-d9ee8d8d07d8 | note | Acceptance Criteria - Quantities correct. Dimensions correct.
1f579878-5cef-560e-acfe-ecf9e64d3c11 | note | Verifying Document - Drawing M0003
d5023806-7f97-5a76-a850-f0deb10d2f50 | note | Frequency - Once
bc6b0e20-7c12-52d6-b83c-728ef314e48b | note | Inspection Type (Visual, other) - Visual + Photographs
7010a7d2-4042-543b-bdc7-c94da028b38b | note | Inspection: Key - Inspection
60bc3985-d3df-5cc1-8d85-9b57df6c129e | note | Inspection: By - IP
3a5c371f-ec21-438f-b1c9-df17615e4be6 | checkpoint | 3.3 - Hilti RE-500 Chemical Anchor
c5915dbb-d150-5f91-bf84-fe8ccb07b350 | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
47f3a1a6-406b-5001-8536-2068d7c1d882 | note | ○ Check expiration date.
6759d78a-5204-5703-bd05-83013fb523a0 | note | Acceptance Criteria - Quantities correct. Within expiration date
ee6286dd-63a7-59a9-a69e-c7c14be682c2 | note | Verifying Document - HILTI Product Calculator APP. Delivery Docket
2dfe4f7b-51c2-5ce0-ac49-9ca0d52f71ac | note | Frequency - Once
62e06b6d-566a-51f6-b409-38b9e8243798 | note | Inspection Type (Visual, other) - Visual + Photographs
1d52c1f7-d2f0-55c4-9128-6c05b4c3b737 | note | Inspection: Key - Inspection
82bd780e-bbbc-58fc-a621-9c25086ceadd | note | Inspection: By - IP
05b2ee05-f439-4e89-b116-28ab8cb89779 | checkpoint | 3.4 - Grout (Sika MonoTop 438R)
a971c529-f88a-5e93-b175-101e77777c3c | note | Inspection Point: Quality Control Activity - Verify correct product is delivered.
49511b0c-08e2-54a9-afc2-3c4a7371870d | note | ○ Check expiration date.
1fa37b5a-b2f6-5c93-92f0-e21ab4802cf7 | note | Acceptance Criteria - Quantities correct. Within expiration date
59c3406e-b013-547d-a65e-4652611da43e | note | Verifying Document - Delivery Docket
77d767cc-c9b2-5fe0-a15d-7cf8a2674211 | note | Frequency - Once
bef9f1ef-eba0-53d5-83ae-270729df0874 | note | Inspection Type (Visual, other) - Written/Submission
e490160d-0204-5f87-a437-42b50c98cfe0 | note | Inspection: Key - Inspection
4c5e6d94-8451-519e-b7ae-2b61476342ce | note | Inspection: By - IP
0cb96fa4-247a-4bb9-91f1-566ff64da61d | section | SECTION 4 – IN-PROCESS INSPECTIONS
c87814a9-5816-450a-9c8f-44ee67aade89 | checkpoint | 4.1 - Mark out penetration on both sides (wet & dry sides) using existing pipe as reference
9628bbf8-63ea-55a4-9926-0cafebfe3d05 | note | Inspection Point: Quality Control Activity - Check and verify dimensains against drawings
e7caf85a-ec9b-58b0-b542-01ed05441cba | note | Acceptance Criteria - Approval from Engineer
c4ea6020-dcf4-57a5-9d00-19bacc50ce4e | note | Verifying Document - Drawing M0003
0e7fff70-8af9-570b-ae6e-d89c254234a4 | note | Frequency - once
36c68a58-e735-578c-b357-5757c6ce91da | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
100cc10e-9b9d-5849-9f5d-62a52a3558fd | note | Inspection: Key - V
93cd02f5-5e48-510b-a1df-d09c207a254c | note | Inspection: By - CR
d4cf5233-cde6-4c3e-90f0-d1397abb5e62 | checkpoint | 4.2 - Proceed with breakout. Hammer drill
4f7934e8-3027-5811-8608-f2d3a3a60883 | note | Inspection Point: Quality Control Activity - Monitor work and progress report any issues
d8eb8bb1-4b37-5a9d-9bb3-b3322fd02857 | note | Acceptance Criteria - Approval to proceed from item 4.1
6d55a4cd-6d69-502a-87de-18bed92824de | note | Verifying Document - As per drawings listed dimensions & measurements
8a9aa87a-4356-5a45-a90f-aa819e8f6c72 | note | Frequency - once
7766ac91-8e05-527f-bba9-7cc53273f8f8 | note | Inspection Type (Visual, other) - Visual & Document
e3b6b701-53e7-5376-97c1-a56fd73985ad | note | Inspection: Key - I
603633b9-2429-5ec9-bc25-a6605b4478ab | note | Inspection: By - IP
c09ae30b-143b-431f-b94d-4af84899eec3 | checkpoint | 4.3 - Pre pour inspection
833de4c7-4893-5c89-8a7f-62bd7583617b | note | Inspection Point: Quality Control Activity - Engineer Inspection
76c99516-9f16-5e03-956b-739d4571960e | note | Acceptance Criteria - Dimensioin & Surface sheck. As per Drawing M0003 and notes.
07a0c299-b85b-55b8-a3c0-c103c89d7ed2 | note | ○ Approval to proceed via NTC.
0a75b353-2e83-5ea6-8015-a6d834864adf | note | ○ Correct profile achieved with 5mm roughness and any loose material removed
321493f8-28df-59ea-9242-748ad90dc494 | note | Verifying Document - NTC or other written confirmation
86ba8aa0-48a6-5c8e-8e21-6fafa0634e24 | note | Frequency - once
6f21602b-8cc4-5714-a127-530c38d34062 | note | Inspection Type (Visual, other) - Document
a1430b90-4bab-5e66-bf22-11a027058351 | note | Inspection: Key - H
85278ac7-dbd1-550b-b8ef-611b68ee5052 | note | Inspection: By - CR
6e883907-69a1-48f7-b45e-566e0d548225 | signoff | AUTHORITY HOLDPOINT
3dc4cb61-e9e4-4802-86df-3e833a7f5c94 | checkpoint | 4.4 - Procurement of Reinforcing bar, starters & trimmers
97c4cc04-222d-5243-823a-58d100ca0d82 | note | Inspection Point: Quality Control Activity - Check measurents and vereify correct fitment
8eeaea31-3068-5ebc-b759-742b1bf79779 | note | Acceptance Criteria - As detailed on Drawings & specifications
c3f3a011-3a05-5e8b-8ac4-678064257598 | note | Verifying Document - Drawing M0003
b055805d-3cfe-503d-aef2-924917bf14f8 | note | Frequency - once
bfe7ed94-68bc-581c-a2e1-50bc8f655d9e | note | Inspection Type (Visual, other) - Document + Visual
6b14f853-d9e7-5849-8d97-0cfb7d199700 | note | Inspection: Key - I
fec86473-1c61-528a-a26f-ca10ed0c1b9e | note | Inspection: By - IP
3cf924a0-2cfd-449b-a01f-7df9766eb4d6 | checkpoint | 4.5 - Installation of Reinforcing bar, starters & trimmers
f67c7b15-65f0-5528-98fc-a4654338ed8a | note | Inspection Point: Quality Control Activity - Drill holes around perimeter to receive reinforcing bar. Check for correct diameter & corret embedment
dc4399c0-f75c-55b0-b418-5c89c44cd1fb | note | Acceptance Criteria - As detailed on Drawings
418af4a8-b92e-5b41-a5df-607d758fe738 | note | Verifying Document - Drawing M0003
e7fdff39-7bb5-5f45-ac64-2368349903fe | note | Frequency - once
e1fb42e0-61f6-5771-b5db-0996dfae80f2 | note | Inspection Type (Visual, other) - Visual + Photographs
d65924ba-605d-5e21-ad83-c314eb177437 | note | Inspection: Key - I
76d46312-162f-597c-a547-a820ecc08d7a | note | Inspection: By - IP
af2afe16-2ab9-4de0-a1b1-ad666b7af2a3 | checkpoint | 4.6 - Install pipe spool with puddle flange to be cast within wall
1d374415-f5d4-56a9-901d-ec97decb98ae | note | Inspection Point: Quality Control Activity - Check that orientation is correct and is in alignment with pump assembly
df4fe819-2489-5c21-900e-bc2f8bde9c07 | note | Acceptance Criteria - As detailed on Drawings M0003 and drawing notes
d3f144a5-e997-532d-b010-f29f646b8197 | note | Verifying Document - Drawing M0001 Drawing M0002 Drawing M0003 Drawing M0004
18529ad3-7a5d-5630-8918-a49b1f0c8017 | note | Frequency - once
c15e88ff-81bf-5e33-92c4-1a29edb8db8a | note | Inspection Type (Visual, other) - Visual + Photographs
f9aaa5d0-90fb-5295-99d8-6f1530462e11 | note | Inspection: Key - I
b53f45fc-31b6-57a9-9b2d-1687deb42c19 | note | Inspection: By - IP
8969be87-5e13-4fba-a08c-e9242527ef00 | checkpoint | 4.7 - Hilti RE500. Chemical Anchor reinforcing bar, starters & trimmers into position
16e220ff-7e86-52fb-ad78-0bd8d62c71fe | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructions. Monitor curing times and temparatures. Use manufacturers calculator to determine product volumes. Sequence the installion to avoid obstruction
edafc1de-0bd3-57dd-8bd5-cfd303e80e7c | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.6
718cd957-3bea-56fa-90a8-1a5c6e0fba10 | note | Verifying Document - Drawing M0003
7eb7ca13-d5de-5c61-80f6-b5129254b733 | note | Frequency - once
629c2340-525b-5b6a-8631-972ea1748cff | note | Inspection Type (Visual, other) - Visual + Photographs
bb63396a-c44f-5506-a95b-b1faf2268419 | note | Inspection: Key - I
cdbd9e99-f650-5a44-94ec-53238b304c7b | note | Inspection: By - IP
3cf02a3e-caa1-4dba-b3a1-dc6b7a55140a | checkpoint | 4.8 - Chemically treat perimeter using product HYDROTITE CJ1020
67339f37-47da-51f5-83eb-e8198fd3c5e9 | note | Inspection Point: Quality Control Activity - Observe Manufacturers instructiuons & Health and safety requirements
bf4ed5af-58d4-501d-9928-782a6bfd321c | note | Acceptance Criteria - As detailed on Drawings and completion of item 4.7
8247bde7-2e88-59a2-97fc-1a692190a911 | note | Verifying Document - Drawing M0003
6efb568c-4396-56a4-9fb4-85c20ddef891 | note | Frequency - once
85fd3468-29ae-5932-b2db-8ebaa35e740d | note | Inspection Type (Visual, other) - Visual + Photographs
ebdc0b58-ef13-534f-9b83-87e9de533d89 | note | Inspection: Key - H
f063ad3e-dd68-54a8-a3f7-eea871543eea | note | Inspection: By - IP
94ab3dfd-ccc5-4d28-a550-beeee1be216b | signoff | AUTHORITY HOLDPOINT
e981f6ff-dc41-4a49-9cc0-dee4a37a3838 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1e63fe07-e964-4385-9234-46e0bb61b58e | checkpoint | 5.1 - Final dimensional check
2c44634c-a222-5354-b5a5-5aa35e2c4264 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
da34e358-c56c-55e7-be04-6f6359c00e6b | note | Acceptance Criteria - Dimensions match the measurements shown on drawings
2e7f6172-cee5-5605-a54c-bce5714f99b8 | note | Verifying Document - Drawing M0003
f902b2e7-0706-5350-b079-ab7371fa4059 | note | Frequency - once
2d309f47-5c33-57f2-8b5f-b124b3238552 | note | Inspection Type (Visual, other) - Visual + Photograph + Mark-up drawing
f2444cc3-9b93-5477-b868-6f470d914e3c | note | Inspection: Key - H
760136ad-1915-50bb-8abf-5013894b03d4 | note | Inspection: By - CR
9db7d794-ff29-4496-9bcc-9bcc56b884de | signoff | AUTHORITY HOLDPOINT
c0176c4b-1cb9-4e09-8eaa-fd3b67331c4b | checklist | 561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2 | itp | 561482-ITP-004.2 - Base. Pump. Motor Installation - Pumpset 2
852ee526-2121-4a19-a62e-596344d4adc0 | section | SECTION 3 – RECEIVING INSPECTIONS
84cbfd59-ba2a-48b0-bd48-cec37546f434 | checkpoint | 3.1 - Inspection of Plinths for pump 2
0944af89-4e92-5ff2-905c-089bb0548cf5 | note | Inspection Point: Quality Control Activity - Check overall condition. Cracks/fissures or breaks or areas of weakness
319468c4-7958-53d7-a7b7-5d755608a988 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
135c82ec-f9c1-5da5-bf73-d344009c98c8 | note | Verifying Document - Email or NTE to report
dd11f01c-1ea8-5ad5-ae71-a85eed798fc3 | note | Frequency - once
bf445cc0-85da-5887-9f85-27ccd22c7be9 | note | Inspection Type (Visual, other) - Visual + Photograph
2fb27d1f-ec8a-5de9-9573-6f1b8a1bcbb7 | note | Inspection: Key - C
4c1e8eb9-d3dc-5183-a6fb-b13241dbdf77 | note | Inspection: By - IP/B
9a1ca43e-7692-4ed4-8a24-b31831100704 | checkpoint | 3.2 - Delivery of Pump 2 to site from Downer storage facility
d61aa01f-8024-53ee-9002-b98beff2d500 | note | Inspection Point: Quality Control Activity - Check and verify that correct pump is delivered
7ee2bb0f-3786-549e-b3b6-705bbc95db3a | note | Acceptance Criteria - Pump is damage free
b377f5a4-bd10-5dce-ab8f-debd5a64a27b | note | Verifying Document - 1. KSB delivery docket.
8556bb09-e5f7-508c-88e5-4caa394e8439 | note | 2. Pump storage ITP
392496e6-a99b-5cef-9161-f011e1dcfc60 | note | Frequency - Once
df02cda1-5ddd-51bc-a6d6-ae782f3c269d | note | Inspection Type (Visual, other) - Visual
3cd6d7ba-2206-50da-8bd0-b77d4d3ced2e | note | Inspection: Key - C
26426cac-e99a-5ba9-983d-02b80f973c1d | note | Inspection: By - IP
954e8b13-ad6c-4c1e-8b52-d168b9859daa | checkpoint | 3.3 - Delivery of Pump 2 Motor to site from Downer storage facility.
0892dd42-8209-51c7-8400-ecfc185882f1 | note | Inspection Point: Quality Control Activity - Check and verify that correct motor is delivered
99f766cf-4270-5eb1-9736-eb124bd3cd90 | note | Acceptance Criteria - Motor is damage free
9e50a624-30cd-5d48-ac9c-3917d73db56c | note | Verifying Document - 1. KSB delivery docket.
b009fb85-608f-54f5-98f1-6199a512ad47 | note | 2. Pump storage ITP
15e60d4c-85be-52dc-b137-e3d4e6c60bdf | note | Frequency - Once
615cd180-da94-5c41-abfb-039e4b29c100 | note | Inspection Type (Visual, other) - Visual
8907eee1-2437-5d43-835c-4453792442ae | note | Inspection: Key - C
33ca49f8-2e60-56b5-b7f7-0d01a03914bd | note | Inspection: By - IP
34f206b9-afd9-457e-91af-e3753671e53d | checkpoint | 3.4 - Delivery of Pump & Motor mounting plate Downer storage facility
fa6f80e1-e7d9-5f62-ac53-55666f8d7581 | note | Inspection Point: Quality Control Activity - Check & Verify that correct Mounting plate is delivered
ed3e5d66-6685-586c-9538-4789013fca64 | note | Acceptance Criteria - Mounting plate is dumensionally correct and is damage free
329f7c4e-230f-5786-87e7-1ac4cfc286ad | note | Verifying Document - 1. KSB delivery docket.
349bb1ae-3ad9-54aa-a65e-5022af8efe90 | note | 2. Pump storage ITP
0f223b15-e080-59e4-85b1-805e8d6d289b | note | Frequency - Once
85d776f4-e13f-52aa-a570-f73d20c9b7ba | note | Inspection Type (Visual, other) - other
87d9b259-41f0-5d9e-b68e-602fb4474cbd | note | Inspection: Key - R
4ea29381-ef97-5ca6-8edc-abced362e6f4 | note | Inspection: By - CR
83b0d062-00ea-4e11-949e-c48b137b2a98 | section | SECTION 4 – IN-PROCESS INSPECTIONS
211f308a-ca17-4d48-ac63-5cac4e60c05c | checkpoint | 4.2 - On-site assembly
d23904cf-480e-598b-86e0-49ff7be2b2de | note | Inspection Point: Quality Control Activity - Correct Pump to Mounting Plate Assembly.
5e9b4823-e612-51c9-9e4e-d1b1afb7a9f0 | note | Acceptance Criteria - Ensure all fasteners are tight and toqued to manufacturers specifications
2ee4bfab-acdc-5872-aefb-42e95f4d9afb | note | Verifying Document - KSB documentation & Installation Instructiions
d34d7818-2765-52f9-bb1b-36a9fdbac04a | note | Frequency - Once/per pumpset
3f8d5d2e-cf3b-5fb0-b1e6-07e511fe6efe | note | Inspection Type (Visual, other) - Visual + Written
002eeeff-d20e-50be-9ea5-61e057b3e8ee | note | Inspection: Key - Inspection
5e9aabb9-7cac-515f-8af0-c4cd12a7071b | note | Inspection: By - IP
997cf824-83e0-4185-b250-4d19e4ef9899 | checkpoint | 4.3 - Pump 2 Installation
d2a905fe-2464-50b9-9b0d-5cf6635c3fed | note | Inspection Point: Quality Control Activity - Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction
f72417e0-a1e2-5c8d-9457-8fcf2d06e1bf | note | Acceptance Criteria - Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall
a16f3447-455e-56c6-90d6-7934f298ce26 | note | Verifying Document - Drawing M0001
8d8fc916-5413-5a76-a5cb-d6344ed90d14 | note | Frequency - Once
5c48086d-b44d-5cd9-8afa-d9168e18fa69 | note | Inspection Type (Visual, other) - Visual + Photograph
fd05b4ab-d8a8-5cad-9124-c2d3db507ca2 | note | Inspection: Key - A/D
e75ea7ce-5a0f-5a26-b098-0758c82b0e93 | note | Inspection: By - IP
f2c5caf5-11f8-4a5a-8335-fb4516a356ed | checkpoint | 4.4 - Pump 2 Motor Installation
9ab31a73-fa55-59be-a576-365f86a125fb | note | Inspection Point: Quality Control Activity - Motor/Pump shaft alignment
e5763ae3-8739-5050-b7c1-680e91e605af | note | Acceptance Criteria - Motor and shaft aligment as best as possible
5275eb14-ab5a-5f1c-95f7-99ad2d15a649 | note | Verifying Document - KSB documentation & Installation Instructiions. Nothing final alignment to be undertaken by a Technician - Ref: 561482-ITP-005.2
87c7e287-e622-59ab-9645-9e93b4b2b4eb | note | Frequency - Once
067f226d-8757-5ac4-a10b-0675002fd1d2 | note | Inspection Type (Visual, other) - Visual + Photograph
f2f141ff-df7f-59e9-b2f9-bff5e0671d1c | note | Inspection: Key - A/D
dee13af4-a63b-5eb4-a791-db18f977e500 | note | Inspection: By - IP
e26919e1-44ff-4f31-a8be-15cd528f4cc2 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
0912a208-d304-476e-97f1-0b94dfa91e56 | checkpoint | 5.1 - Pump 2 & Motor assembly complete
7e33aa1a-b72d-5df3-97d1-e1867f7b4a4a | note | Inspection Point: Quality Control Activity - Proceed with 561482-ITP005.2
6205ad35-6fda-5f9c-830f-911a0b4805f2 | note | Acceptance Criteria - Pump & Motor bolted to mounting plate and mounted to plinth.
dee0e475-15a7-5071-90a3-de114026ee70 | note | Verifying Document - This ITP
a99293ae-6679-53df-9214-ddefbcb96ffd | note | Frequency - once
f4b0c380-dd92-528a-acc8-248a73008f47 | note | Inspection Type (Visual, other) - Visual + Document
fff2c70d-72d1-51e5-82c1-93e30519b607 | note | Inspection: Key - I
6c95a871-a8d1-5772-80d8-a341a61b7a97 | note | Inspection: By - IP
da880a12-b43e-4edf-b9da-bea02b5ef762 | checklist | 561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3 | itp | 561482-ITP-004.3 - Base. Pump. Motor Installation - Pumpset 3
171b2e5b-339a-4f7b-98d6-38a92269a832 | section | SECTION 3 – RECEIVING INSPECTIONS
47850c6e-12e2-4972-9a21-0d73230aaf24 | checkpoint | 3.1 - Inspection of Plinths for pump 3
1083ea28-664d-5b42-aa30-d931ba59a9c2 | note | Inspection Point: Quality Control Activity - Check overall condition. Cracks/fissures or breaks or areas of weakness
e9275c00-33b9-55ba-9711-2ca0d8f39244 | note | Acceptance Criteria - Visual check and report any defects or areas of concern
c6add31b-60bd-51a2-988b-bf3a5afdc965 | note | Verifying Document - Email or NTE to report
a42a33eb-3d1a-5330-94d5-8655a8addb59 | note | Frequency - once
c2331a3c-a134-57df-b4bb-09ac7ae75ef7 | note | Inspection Type (Visual, other) - Visual + Photograph
bdf3c056-ef2e-5104-8d40-b23cdca9018e | note | Inspection: Key - C
4164830e-9048-5c17-92e4-da19e62da82f | note | Inspection: By - IP/B
44975ec3-feae-4658-8e83-fad7d6a28c1e | checkpoint | 3.2 - Delivery of Pump 3 to site from Downer storage facility
32ab29a3-3622-56c8-9723-1417a6880362 | note | Inspection Point: Quality Control Activity - Check and verify that correct pump is delivered
bf28d5cf-51c3-51ea-82e6-83680b3f1cbf | note | Acceptance Criteria - Pump is damage free
ac208a22-4fbd-572a-a079-8df9d186886d | note | Verifying Document - 1. KSB delivery docket.
4f549916-0e98-533d-aec8-5b7c34b35c26 | note | 2. Pump storage ITP
85ee8090-d905-5973-a343-568251e9d95c | note | Frequency - Once
a7d66ef6-d59e-52a9-b705-61d5b3be45a0 | note | Inspection Type (Visual, other) - Visual
3c809e28-4248-5020-b82b-e231a25627f7 | note | Inspection: Key - C
f6fd1bea-d1c5-5b39-9483-b4952c5320a2 | note | Inspection: By - IP
65a21a6a-3ab7-4044-ba97-9c2c03c8df62 | checkpoint | 3.3 - Delivery of Pump 3 Motor to site from Downer storage facility.
361a8997-4d4e-5d87-ac16-f29dea536c7f | note | Inspection Point: Quality Control Activity - Check and verify that correct motor is delivered
b0aa6018-15ae-51a5-925a-b8177d07386f | note | Acceptance Criteria - Motor is damage free
4727cb84-ec2c-5549-a4c7-b62935567e09 | note | Verifying Document - 1. KSB delivery docket.
47309c8a-339b-5273-bb2d-d15291d4e229 | note | 2. Pump storage ITP
17dbf657-31c5-53e4-a635-c7ac8e84bcdf | note | Frequency - Once
6d85dd0f-c025-5246-9f63-335b2a27757d | note | Inspection Type (Visual, other) - Visual
fa5974c8-8652-59ed-9b21-e57fc05e5f41 | note | Inspection: Key - C
9e915db2-2c73-55d4-8fa7-2cac62e3f325 | note | Inspection: By - IP
fd7c4b1c-2449-4e37-8c45-067380c5a087 | checkpoint | 3.4 - Delivery of Pump & Motor mounting plate Downer storage facility
807dbf09-b14f-59dc-8d97-b487efffe0a1 | note | Inspection Point: Quality Control Activity - Check & Verify that correct Mounting plate is delivered
ad51e87b-9dbd-5f6c-9bdc-4af02e718eba | note | Acceptance Criteria - Mounting plate is dumensionally correct and is damage free
b05c3591-cc64-5597-8659-ea02c97e1663 | note | Verifying Document - 1. KSB delivery docket.
3a45e670-2d45-5f11-b400-2bc27b840561 | note | 2. Pump storage ITP
02752286-fcde-571f-932d-04c39fca2b6e | note | Frequency - Once
5fe35890-8285-55c6-a8e2-3ae45eac11d0 | note | Inspection Type (Visual, other) - other
a936ecac-8a5c-529e-b281-16c1beecb2f0 | note | Inspection: Key - R
836025bd-8740-52cc-83ed-ee97656b967e | note | Inspection: By - CR
11c2bc38-cb69-403b-b028-6a57ec7a1926 | section | SECTION 4 – IN-PROCESS INSPECTIONS
89d41f40-be56-4205-be78-1f02ef921c12 | checkpoint | 4.2 - On-site assembly
bb4318d4-6d0f-57dc-8676-683e929ed6db | note | Inspection Point: Quality Control Activity - Correct Pump to Mounting Plate Assembly.
401e46f2-3719-525c-85da-3998a12e54af | note | Acceptance Criteria - Ensure all fasteners are tight and toqued to manufacturers specifications
a16e1c1b-6c26-588d-9d70-37a075fac1c1 | note | Verifying Document - KSB documentation & Installation Instructiions
787aca91-0d7d-5c37-a416-9e53f7f67942 | note | Frequency - Once/per pumpset
dc7ce1db-4e72-5b44-90fe-3712b60e8981 | note | Inspection Type (Visual, other) - Visual + Written
70942dc6-5b7b-5ab9-ab49-9316f13237bb | note | Inspection: Key - Inspection
b7828699-9297-589d-9642-a8d3608047ef | note | Inspection: By - IP
7806e442-ecb1-4054-b67a-7f00e3b0e5fb | checkpoint | 4.3 - Pump 3 Installation
b98d24d6-1fbc-592e-b598-4b80eb5e9733 | note | Inspection Point: Quality Control Activity - Correct Mounting plate position on plinth, correct use of fasteners and torque requirements, in accordance with KSB installation instruction
2bf60efc-1d07-5f59-8a72-b58052d97ba5 | note | Acceptance Criteria - Position is determined by the fixed pipework. Ensure alignment of flange face is parallel to wet well wall
59f8ebb7-2d46-5295-9cb5-41ffef664fe9 | note | Verifying Document - Drawing M0001
39d47a9e-e073-5f1e-8385-63eff2d8727d | note | Frequency - Once
da4974c2-6537-5298-8685-2231e3b50399 | note | Inspection Type (Visual, other) - Visual + Photograph
bf760d84-4564-5a23-b3a8-4253594905b9 | note | Inspection: Key - A/D
d36cdeed-a525-5688-972e-b51693de3817 | note | Inspection: By - IP
19b411e7-b891-41e9-a2f5-2ae278b50e24 | checkpoint | 4.4 - Pump 3 Motor Installation
7bffab20-f494-585a-931e-fab6eecdf073 | note | Inspection Point: Quality Control Activity - Motor/Pump shaft alignment
b4a3e3ed-f976-5b7c-bd4a-e81ac0c58292 | note | Acceptance Criteria - Motor and shaft aligment as best as possible
58dd5040-5542-53aa-b23d-de61ff1170fe | note | Verifying Document - KSB documentation & Installation Instructiions. Nothing filal alignment to be undertaken by a Technician - Ref: 561482-ITP-005.3
17f85d29-80b7-5070-baf4-ab921eecb953 | note | Frequency - Once
beb3311c-7f86-5210-a825-c06129977618 | note | Inspection Type (Visual, other) - Visual + Photograph
0a66979b-c3fe-5e48-ad7f-7d30ffa16869 | note | Inspection: Key - A/D
f7a2e0a0-d5c6-5efe-9c46-1a00cf70fa35 | note | Inspection: By - IP
e0e7b0f6-2e01-4458-82c1-6b15a5710627 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c0c2a096-b699-42c4-bf8c-9080214f042b | checkpoint | 5.1 - Pump 3 & Motor assembly complete
3a5ff1cb-b47a-5f4c-974f-6f7bcc3fcf2b | note | Inspection Point: Quality Control Activity - Proceed with 561482-ITP005.3
990689cc-55f4-5b69-bcef-1f1f3e16ba1a | note | Acceptance Criteria - Pump & Motor bolted to mounting plate and mounted to plinth.
ad31f0e2-d2e0-5385-94ef-09edab383081 | note | Verifying Document - This ITP
71399935-e36b-50d5-a61a-1979b1db3877 | note | Frequency - once
87d4aad6-4211-5c1d-9829-3bd54301127a | note | Inspection Type (Visual, other) - Visual + Document
7ba6a694-6a36-514b-81c5-9f89d49f7bcf | note | Inspection: Key - I
aa385e8e-1437-548e-b820-5afbda4d7479 | note | Inspection: By - IP
cf776114-6195-4b72-8b9f-d7eda9ea622b | checklist | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2 | itp | 561482-ITP-005.2 - Pump. Motor Shaft Alignment - Pump 2
fcc3f6cd-2b16-4e25-bc3e-893ac9d39f7e | section | SECTION 3 – RECEIVING INSPECTIONS
f61d0b52-8290-45db-b526-aa984c9aac2c | checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
c5a3a016-2274-570a-96a9-ba71a6ae5570 | note | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
59baec02-0980-5010-b49e-605b142d1167 | note | Acceptance Criteria - Completion of the assebmly to pump and motor 2 including mounting to the plinth.
28111e01-4316-54b3-984d-97481b10fdaf | note | Verifying Document - Downer 561482-ITP-004.2
9d92e142-6604-5aa8-a7db-e634ab48a789 | note | Frequency - once
1a5f6b5f-055f-5d6c-a408-1118d8f213ce | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
871f1cd6-d632-553f-9804-ebd26f922835 | note | Inspection: Key - QE
60f59dae-d7d7-54b2-938c-4d112adfd516 | note | Inspection: By - D / E
3cbb84b7-b719-41fa-b238-d8f1e137fa4f | section | SECTION 4 – IN-PROCESS INSPECTIONS
fdd805d9-ded6-44ad-b93e-9e87fe8fe8bf | checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 2
ae231f52-a04f-5b7e-9889-29c1a4474882 | note | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
952d1da7-e92b-5596-a722-ef2e38cddc38 | note | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
ccc041ca-1276-5cdc-a876-d241ce505348 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
3429c640-387f-5ee0-ae24-6d0fe9ffc625 | note | Frequency - once
7354e46c-1d82-5a44-93ea-01831f6d6900 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
a873ccd8-a74e-57f6-be90-9eda4d6bb923 | note | Inspection: Key - QE
4ee02c9f-98c1-5c25-9afd-b0d78eabe0e5 | note | Inspection: By - D / E
c22ef4f9-f701-4489-92b0-203b90616733 | checkpoint | 4.2 - Install drive coupling to Pump 2
179b174f-5e40-52b7-b508-33086056c1f0 | note | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 2
27b4aaeb-206a-56f2-b360-6a5b186f6013 | note | Acceptance Criteria - Completion of Item 4.1
d8726d32-37c5-58ce-a808-a6f4a82f0fbb | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
7cfe7920-7033-5cf7-916f-55e70c12374f | note | Frequency - Once
f7e651f8-e8de-5359-8cfe-30e52cb25726 | note | Inspection Type (Visual, other) - Visual + Photograph
2d226274-4de7-58f7-9497-d4dfa47a7c22 | note | Inspection: Key - A / I
40955d40-9cfd-50d2-a2c6-9fba1a0f6f41 | note | Inspection: By - IP
2406cc7d-0e69-46d4-932f-1cddfa5fef51 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
fe412602-90a4-4c76-a340-e52b69b48c6c | checkpoint | 5.1 - Pump 2 & Motor assembly
fe5a81b2-6c82-5edb-8f4b-2676532cf0ae | note | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
57963e0f-f27e-58c0-997e-be393c0d7b34 | note | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
f716c40d-6178-5f9f-8aff-65a0daeaa04d | note | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
e53402b0-f5f7-51bc-bad9-752d5f2ef0b1 | note | ○ Detailed report provided from specialist - Wallace Murray Electrical
ccacc0f0-da82-55a3-830b-1e63289f86ee | note | Frequency - once
7dc2feea-9690-575c-9a93-20dfe0fd9b77 | note | Inspection Type (Visual, other) - Visual + Document
62f8e1c7-6cfa-552c-9880-fe7f9eda7570 | note | Inspection: Key - I
324b6e40-59c6-5417-bf45-87fa8893b203 | note | Inspection: By - IP
5cd85ed7-0b91-401b-ba45-152d4961880c | checklist | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3 | itp | 561482-ITP-005.3 - Pump. Motor Shaft Alignment - Pump 3
7a375857-cb6f-4a86-bc78-9ada83fa342e | section | SECTION 3 – RECEIVING INSPECTIONS
27dcceae-aa2b-44d5-bf16-e8750fb5da12 | checkpoint | 3.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
5893dcb7-823b-53fc-90e2-ed7a5049ae76 | note | Inspection Point: Quality Control Activity - Downer to engage a specialist to laser align motor and pump shafts to within 0.025mm
e8a59a0c-671f-5815-a53c-33d98c03186a | note | Acceptance Criteria - Completion of the assebmly to pump and motor 3 including mounting to the plinth.
ebc75702-0c4e-51f6-8cd0-3d64d3a49a50 | note | Verifying Document - Downer 561482-ITP-004.3
048512a9-5467-5cea-9c36-dc4c7e61963d | note | Frequency - once
24c92551-7f22-59b3-bcd8-ca507cffe7b2 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
f240bc3c-0205-58f6-bdcd-cdd62bc343a7 | note | Inspection: Key - QE
0e5b566a-8dcf-566f-b4bf-f36f3d1683ac | note | Inspection: By - D / E
371e6ee1-41e8-4751-8542-a125f745120c | section | SECTION 4 – IN-PROCESS INSPECTIONS
ae2aa987-58d0-4046-b92d-6a5e58daa4b2 | checkpoint | 4.1 - Align pump and motor shafts and install coupling - Pump & Motor Assembly 3
94f927e1-e24c-5f8b-adf4-ae53f8a22775 | note | Inspection Point: Quality Control Activity - Engage Engineering Specialist to adjust and align motor and pump shafts using laser alignment
c82bbd30-5e21-5029-a5be-3213fccd4832 | note | Acceptance Criteria - Pump and motor shafts are aligned to the specified tolerances on X-Y-Z axis to tolerance of 0.025mm
a7370b22-f297-55ab-a381-a68958038191 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
15b723b7-2f2d-51db-839c-de7c4b08fbf6 | note | Frequency - once
f22e0acb-e13e-5790-84c2-32cc3ec37fb5 | note | Inspection Type (Visual, other) - Visual + Photograph + document provided by specialist
9de4197e-aa94-520d-9013-03e47bde7aba | note | Inspection: Key - QE
5d2bbc37-6777-5175-a06f-e6aa9b336feb | note | Inspection: By - D / E
bd4a6dde-2312-4ad4-bf2a-7ee9dc86c756 | checkpoint | 4.2 - Install drive coupling to Pump 3
3e8086cd-ab5c-51d1-8d0d-0544ae8a2dc6 | note | Inspection Point: Quality Control Activity - Completion of the nstallation of shaft drive coupling - Pump 3
5f622266-cffb-5738-9a52-1fa00d38ab68 | note | Acceptance Criteria - Completion of Item 4.1
8bc8a698-46e6-5b26-a66b-2f4abd61db60 | note | Verifying Document - Report provided by Engineering Specialist - Wallace Murray Electrical
8c21c70e-7d8b-53a4-a808-4edf4490f52a | note | Frequency - Once
b14c57e7-6cd2-5c06-a2a3-18014ea77fe3 | note | Inspection Type (Visual, other) - Visual + Photograph
03aef200-c098-56f9-a677-caca5d3ba887 | note | Inspection: Key - A / I
01abb95a-5825-5a44-83bf-c9335708ef24 | note | Inspection: By - IP
84de3274-b806-4364-bf27-9eb2f3010bb9 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
e5ffc516-3461-4033-8375-11c79c4253c7 | checkpoint | 5.1 - Pump 3 & Motor assembly
5a8b6fa7-6d32-56cc-8715-eaacd1625404 | note | Inspection Point: Quality Control Activity - Final inspection & check. Rotate motor/pump assembly by hand to esnure smooth operation
030e7ebd-e0e8-532a-9826-454b82d22c03 | note | Acceptance Criteria - Pump/Motor assembly completed and laser alignemt completed and verified. Drive coupling installed
44504101-c5f3-585f-a1ec-50900f8ab3b2 | note | Verifying Document - As per methodology, Shaft lignment verification & Manufacturers Instructions.
a87b5f7e-2cad-56f0-9241-bb9b5c787630 | note | ○ Detailed report provided from specialist - Wallace Murray Electrical
3f381d50-90a2-5d54-a32e-26d9cf34891b | note | Frequency - once
3dde77c1-afad-50eb-81b4-0835e4e5d12a | note | Inspection Type (Visual, other) - Visual + Document
9a9a70e3-975a-50d1-badd-29fd03d6a9e0 | note | Inspection: Key - I
40b63d3d-0ebf-5ddd-95e4-24814ffca5df | note | Inspection: By - IP
b8eff675-8b3a-47b5-b0db-e9ef0bd8c878 | checklist | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1 | itp | 561482-ITP-006.1 - Pipe & Fitting Installation Pump 1
d8606108-ebfb-423c-8430-5a2335d9b85c | section | SECTION 3 – RECEIVING INSPECTIONS
e9765e7b-4e31-4d23-bf9b-1f5a05af5352 | checkpoint | 3.1 - Stainless Steel Pipe components
67672620-43ef-5a3f-8b7d-6e1b4a5ef88c | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
79d47014-2ca7-5cfa-be4a-c9b9927e0b2f | note | Acceptance Criteria - Documents from the supplier/Manufacturer
6bae09bf-4975-5f73-81b0-f7b6195cf537 | note | Verifying Document - Mill Certificates & Welding certificates
82d24078-91c9-50e8-841c-0600d5f5171c | note | Frequency - Once
abc8b964-d056-53d2-b016-c466a5fc5291 | note | Inspection Type (Visual, other) - Documentation
31145320-c8a3-5798-b5e8-bf64eab9acc7 | note | Inspection: Key - C
6dd768ad-70dd-5a61-9fa0-00a1e643b3a9 | note | Inspection: By - IP
b9fa7e86-aee2-4b55-aaaf-845611b82a1e | checkpoint | 3.2 - Stainless Steel Pipe components
aa78ee3e-9b8c-5a94-a55a-150d28caf04d | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
d25722c5-8e9b-50d8-b5f8-228e72e77e11 | note | Acceptance Criteria - Quantities as shown on the drawings
f0467330-f29e-5459-bbf5-2d1ad12bfd48 | note | Verifying Document - Drawing M0001
3dd1fee4-1dd6-5528-ac44-c83da3e5dc13 | note | ○ Drawing M0002
8ec8dab6-b2a2-5f41-84c5-68158f351b6e | note | ○ Drawing M0003
a3cf5de5-668d-5c90-b8ea-bda32360f224 | note | ○ Drawing M0004
ab38019e-37f1-554a-90b0-d0a88e6f55eb | note | Frequency - Once
2411d3f4-a043-54a5-966b-9e758c53a73f | note | Inspection Type (Visual, other) - Visual
7421e0bc-2d56-52e6-ad11-29b4885464bb | note | Inspection: Key - C
57263c10-8b0a-51e8-8566-03d959482438 | note | Inspection: By - IP
1e3b5505-301b-4a29-85ef-378048a4b6a0 | checkpoint | 3.3 - Stainless Steel Pipe components
fa5912f0-d69d-551d-8b73-a37aca1d6dbb | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
a9a59311-7f10-56a6-8875-854aef1ed8d3 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
a0ff312a-3346-52c0-9ffe-d23e37b9d0fe | note | Verifying Document - Drawing M0001
e6a50a71-93d6-5954-99b7-09be0ae25ab1 | note | ○ Drawing M0002
9f0fc32b-8cc1-5494-884c-114d84cca37a | note | ○ Drawing M0003
4fd0c703-4d9d-5683-8c7e-c575907027d4 | note | ○ Drawing M0004
90a4b2b3-04ef-541a-b28c-2eac602fbb63 | note | Frequency - Once
0c169dde-f5be-5f3b-ac8f-56758c46aea1 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
b2cc7987-ffec-5e07-94e0-60d289f6ca07 | note | Inspection: Key - D
c0ad7035-c3e3-565f-898f-896a4d3dfc12 | note | Inspection: By - IP
de3fe68f-67fd-439f-bdd2-e67a9354e14e | checkpoint | 3.4 - Valves & Ancillaries (Blanking Flange)
3da76aee-349f-548a-935d-80884f6213bb | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
1a35a80a-1ef0-5d1d-bc01-b392a4b9541a | note | Acceptance Criteria - Must be on the Approved Products list
c33a1f54-b26f-5d32-9c9c-c67b0c06c647 | note | Verifying Document - Specification - Approved Materials list
8fef2806-344c-56dd-833b-aa1310066493 | note | Frequency - Once
f8e07a5d-c12b-5d6d-ae15-5e2a5da97d69 | note | Inspection Type (Visual, other) - Visual
6b14be53-cca0-5163-bcb9-a5d93530105e | note | Inspection: Key - C
645c18ec-fa19-5d8c-b789-1095999dc6e9 | note | Inspection: By - IP
a73108ff-003f-4c10-bbfe-df23cf36fc34 | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
05147020-0c68-5762-93af-258dfaf1b51f | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
14efc88d-e2aa-5377-a626-67d7737f40b5 | note | Acceptance Criteria - Must be on the Approved Products list
696fb468-eeb1-5f60-b200-57347879e2c8 | note | Verifying Document - Specification - Approved Materials list
704a5f48-6ecd-5973-a1b3-9322a2f9552d | note | Frequency - Once
cc791cf9-1b96-5040-bf34-90c121eb497c | note | Inspection Type (Visual, other) - Visual
fc8bae6f-d177-5a8a-8b7f-374f11e64fc7 | note | Inspection: Key - C
5975537e-aae6-5b8c-b387-a1d2f291baa9 | note | Inspection: By - IP
ca555757-2216-49b6-ada2-259186b44f79 | section | SECTION 4 – IN-PROCESS INSPECTIONS
234ce304-6996-47d8-997d-dafd6c7f0803 | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
d9ca77c5-f64a-539a-9fe0-28f36b7cfa87 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
70ecac8f-b2b8-58a1-a13c-d42bdb992f79 | note | Acceptance Criteria - Use diametrically opposed touque sequence
94c12448-4346-5a89-b860-bcc54a177aa2 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
5caa2650-7916-5f43-a0b4-4918b4e20503 | note | Frequency - Each flange
030df472-58b0-53dd-82b7-14d4fcc69cf5 | note | Inspection Type (Visual, other) - Record & attach to ITP
8784db47-019a-52ed-9b2d-dde375ebc6ec | note | Inspection: Key - Inspection
a32c9cde-52ee-5438-8c43-a11b9f4c3746 | note | Inspection: By - IP
cd3c3b76-a124-443f-bd7a-f241674c00c6 | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
ddda5591-02d7-5b21-bb7a-5c46fb966a8a | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
d55462eb-3c5a-587a-89d1-56750fb7120f | note | Acceptance Criteria - Use diametrically opposed touque sequence
ac3d693e-57fa-561e-98f7-1f9e12038f1b | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
71fc488d-23d0-5ea2-9c76-172ea8453304 | note | Frequency - Each Flange
5864a802-cce4-569f-a8fc-8a1542b3c03d | note | Inspection Type (Visual, other) - Record & attach to ITP
2b56a0bd-da85-51c1-8053-a98ab741d001 | note | Inspection: Key - Inspection
0920fd53-3c16-53a4-9085-1ac43130254b | note | Inspection: By - IP
aefae2ae-bff1-4069-90b3-ba748ce0dbee | checkpoint | 4.3 - Blanking Flange150mm (suction side)
c28c4bd3-0700-55f6-81d8-e8868952bbd6 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
bdb3082e-1fa6-5440-b97f-b6d80f08a2dc | note | Acceptance Criteria - Use diametrically opposed touque sequence
26dc2a55-4ea6-55da-90c4-8a5df5cc2564 | note | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
fe50b6d0-badf-5848-ab72-868ace4ef695 | note | Frequency - Each Side of Valve
eb043b32-75c3-556a-931d-deb608a867bc | note | Inspection Type (Visual, other) - Record & attach to ITP
fdacc0d6-5f18-58c5-bf4e-5b780132abc9 | note | Inspection: Key - Inspection
cb133296-8ba9-56ba-9367-e97629a0e40d | note | Inspection: By - IP
874ae99a-8535-440d-8a6e-be877dcd371b | checkpoint | 4.3 - Blanking Flange150mm (Discharge side)
1ad00f9d-520f-50ea-bd68-6c273e456590 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
79556b7e-21ca-5610-95ae-03b0ba7a7b5d | note | Acceptance Criteria - Use diametrically opposed touque sequence
c131d0cb-7c77-57bf-ac0c-a3fb5713784c | note | Verifying Document - As per WSA-109 Australian Water Standards Guidelines - 80N.m
a6e4dc1d-cea6-57b6-b8a5-e7e9271b29f5 | note | Frequency - Each Side of Valve
811bea7d-2158-515d-959f-2c0f00aa9212 | note | Inspection Type (Visual, other) - Record & attach to ITP
beae2312-2df3-5242-9531-4917116f3ea3 | note | Inspection: Key - Inspection
a65a3fa0-4638-587b-95c1-70b08cb1478c | note | Inspection: By - IP
a0be18aa-0a41-472c-bf1b-87273405f569 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
7af52dfa-a61c-4d58-b3bc-5f3b3f0e0f7a | checkpoint | 5.1 - Final inspection to installed pipework
b4ca4837-155d-54c0-b11e-346e8acaebca | note | Inspection Point: Quality Control Activity - At completion of pipework
befff066-16e5-5cac-b4ac-5abf0f3723ce | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
1d877c3b-4812-5e5e-81f4-95eeb14450b0 | note | Verifying Document - As per drawings
41278976-0f33-56d1-af3f-c4abf6517896 | note | Frequency - once
9edb0b65-5090-59bb-bf56-95b053c7da62 | note | Inspection Type (Visual, other) - Visual
c142ee9e-93e7-595f-aff9-0fdb87fabdf0 | note | Inspection: Key - I
500f23bd-15ff-54fa-8a1d-c8e3f432f5bc | note | Inspection: By - IP
ecdf23f9-2dce-4a64-ad57-ff520af84341 | checklist | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2 | itp | 561482-ITP-006.2 - Pipe & Fitting Installation Pump 2
b9880f77-e1c8-44ce-94c2-cebf2646204e | section | SECTION 3 – RECEIVING INSPECTIONS
96911d34-4328-4c52-b275-d0ad6c03d911 | checkpoint | 3.1 - Stainless Steel Pipe components
1ca77c7c-bf6c-55eb-814f-8e84200ea91d | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
69e0455c-9c4e-511b-9431-44cd9ca76673 | note | Acceptance Criteria - Documents from the supplier/Manufacturer
0c2734df-b74d-51a2-a2a8-47ca3e96b553 | note | Verifying Document - Mill Certificates & Welding certificates
4b4df5a7-4df7-5703-b323-e1792e8435a9 | note | Frequency - Once
d99316f8-7912-52d3-814a-2a6e34b79d3e | note | Inspection Type (Visual, other) - Documentation
2d915948-4443-5143-b2a5-23b4b2c140d9 | note | Inspection: Key - C
e83ac92d-6b01-51ad-b656-c79f916796e1 | note | Inspection: By - IP
0281de9e-c1b8-4367-a651-282796551903 | checkpoint | 3.2 - Stainless Steel Pipe components
2e6501e2-6581-5988-bbbf-179e959e88d8 | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
92f4b7dc-d94e-5b88-9fd3-0181d796c402 | note | Acceptance Criteria - Quantities as shown on the drawings
67ccecd8-69d4-5df3-b076-dd0b8756b050 | note | Verifying Document - Drawing M0001
fddb0806-6092-508c-a395-4f5f75f8a155 | note | ○ Drawing M0002
8886385b-ad13-534e-9f39-7bafa5bfb056 | note | ○ Drawing M0003
fdf90a21-824a-5768-804c-e8c947cc4506 | note | ○ Drawing M0004
a1c7d928-3df6-55c4-bf05-db7f4404cf1e | note | Frequency - Once
8737336a-050d-5d21-8472-3671a54b1483 | note | Inspection Type (Visual, other) - Visual
7f53d69c-1c3e-515e-a4bf-a524fd8be644 | note | Inspection: Key - C
9ef1e997-e97d-5121-8ee2-98162dbff7f3 | note | Inspection: By - IP
2309c2ea-68be-44a9-8302-9c0606e25188 | checkpoint | 3.3 - Stainless Steel Pipe components
8d83767a-1648-56f4-a597-8ed6f8380a5f | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
d14e2a9d-e65c-5b0a-be71-b807bd957027 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
5bd07c60-fd46-5908-a55e-e92a2de589f3 | note | Verifying Document - Drawing M0001
436245b2-1d0c-57e1-8aec-4d5df3700fbe | note | ○ Drawing M0002
bcd8cdf7-ce9a-5ced-a1fd-3d370fe812bd | note | ○ Drawing M0003
5670afc3-34a9-597c-a0c0-15579afe5cf6 | note | ○ Drawing M0004
963a9be0-a0bc-5343-866e-36a95c9ff1fe | note | Frequency - Once
29b42713-3f21-59e5-a8dc-1ad7caa31c58 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
5f7f2485-615b-53e4-81ce-dc94987ea330 | note | Inspection: Key - D
6621146e-afb0-502c-914d-eb37ea737e30 | note | Inspection: By - IP
3e16f3e6-42cf-4b22-b499-3a42452d0401 | checkpoint | 3.4 - Valves & Ancillaries
8aeaac1c-c901-5d40-b14c-e5b74e5bf42f | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
f8bc6db5-14d7-5676-a47c-93751f390838 | note | Acceptance Criteria - Must be on the Approved Products list
ba85bc8c-ab3d-5d6b-91be-8991911237fa | note | Verifying Document - Specification - Approved Materials list
5b8cddff-db5e-5747-b6da-49cd73a7f5d0 | note | Frequency - Once
255c6152-10a0-5f43-a880-947037fd0f83 | note | Inspection Type (Visual, other) - Visual
6b42a257-4535-554f-95a8-85aec352cf41 | note | Inspection: Key - C
0e9615cd-a0ad-5264-9721-d32136f41f66 | note | Inspection: By - IP
1d305302-a30a-4912-8f5b-bdc71feca59d | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
bfef5849-5b28-5637-b5c1-68f423af4355 | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
c477352d-5940-5742-9d6a-578b6a5b3fd4 | note | Acceptance Criteria - Must be on the Approved Products list
76e0c7a9-e1eb-5689-8f13-129a4114756f | note | Verifying Document - Specification - Approved Materials list
1ba82a15-4e16-5321-8bc0-1a7aececfe25 | note | Frequency - Once
700bbfed-cca6-581a-ab04-5880857b1c3c | note | Inspection Type (Visual, other) - Visual
4d91a056-9d58-5ee8-a927-07c6185935cd | note | Inspection: Key - C
5a1da9fb-833a-5d04-b36f-deb01cec82f8 | note | Inspection: By - IP
58018d37-34f5-4cb8-a119-6deab1f412f6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
d6747565-bff8-4321-9945-002f3452ecc2 | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
5611d823-2f7c-5390-952b-3c7fc5cf5b01 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
aa1a8fee-607f-56dd-baff-db3175e363ae | note | Acceptance Criteria - Use diametrically opposed touque sequence
556e4882-147a-55f5-83a1-cadeb808f0d9 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
e053d352-c643-5343-8643-18016b447bdb | note | Frequency - Each flange
19aa908e-1457-5deb-9ea0-a0c48c48a269 | note | Inspection Type (Visual, other) - Record & attach to ITP
93dfc4c7-5e24-5a72-85bb-89787013cdaf | note | Inspection: Key - Inspection
c5ebfab9-ede5-55ca-81e8-3afb7eaa6255 | note | Inspection: By - IP
30328ebf-df38-4bc4-bab4-3fb159ddcac2 | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
dfdb7daf-640d-5971-bbb8-6b4bcc687b55 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
86d43d3e-2599-5f34-bebe-d4fd71178f8a | note | Acceptance Criteria - Use diametrically opposed touque sequence
aa492383-856f-5268-a57f-9b17ac58e4a8 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
2989b14d-b129-5dda-9547-c7b2b0af22dc | note | Frequency - Each Flange
8848765d-a6ad-55a7-ba42-a1d70e0d71d5 | note | Inspection Type (Visual, other) - Record & attach to ITP
c17377b7-550e-5d1e-bd77-37ea4e61c759 | note | Inspection: Key - Inspection
13376683-82cb-5b62-864d-6f732344d5e9 | note | Inspection: By - IP
33bf0813-5649-4ba1-8e50-021015259516 | checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
c88d13e6-fd25-5b51-bf35-b70cc7887658 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
1e7defdd-25e1-511f-b5c4-1905fa029fdb | note | Acceptance Criteria - Use diametrically opposed touque sequence
04526a9e-aa93-59e6-ae75-fddb7971917d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
a86685e2-0e0d-59dc-9111-76bf2205c013 | note | Frequency - Each Side of Valve
b59f6f92-8a7f-5eba-885b-4b52e7237e5d | note | Inspection Type (Visual, other) - Record & attach to ITP
7d321e87-18d8-5f40-9d7b-4e322c9b0a15 | note | Inspection: Key - Inspection
8990b10f-32bf-5d62-b05b-0b82ccb0801b | note | Inspection: By - IP
9b7e863b-cd0a-4ff3-9a74-515c0d40b176 | checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
a48d90ae-82fe-5233-bd66-4e686e72b2f4 | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
4d90d7c6-8895-5bf4-b85a-7713f7e39b4d | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
781a06a1-af8b-52f2-9f00-56c477bd1909 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
806b0b2a-8c4b-5dea-9ff6-3b790343bfe6 | note | Frequency - Once
36382eac-9dc8-5927-a4af-78d217505a4a | note | Inspection Type (Visual, other) - Record & attach to ITP
0e627b03-c207-598f-8225-09442e1336c8 | note | Inspection: Key - Inspection
3353e402-eab8-5b45-9851-42fb90356b25 | note | Inspection: By - IP
5a83b1c1-8876-4250-b65d-ee9da2f35050 | checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
81e50aae-8f77-5470-ab6f-2a2e2c196333 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
a573a8d7-c9f8-559a-b18a-5425d20f41af | note | Acceptance Criteria - Use diametrically opposed touque sequence
62c6d8b6-bc93-59ff-a168-5315908b8647 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
158f44a9-84f9-54a5-97bf-ddbe4bbad44e | note | Frequency - Once
517a35cf-6616-5926-8e05-eefea773b971 | note | Inspection Type (Visual, other) - Record & attach to ITP
e17b08cb-08a8-55ca-a9ff-c9f07c1f56eb | note | Inspection: Key - Inspection
d2a7b2e0-5fb1-5c4e-9c72-7b700b1e0fb3 | note | Inspection: By - IP
941b9736-617f-4385-9d4c-b0e6817f37bb | checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
d1fa2a07-1b60-5dd7-abd8-1453ff6e4a2b | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
f2980767-a659-51ce-8079-9ea2c13ec066 | note | Acceptance Criteria - Use diametrically opposed touque sequence
3fe7d66c-b900-5128-b854-560c3479e413 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
fe919e49-f083-58ee-b72b-91c0ec7641bc | note | Frequency - Once
f724fd6c-4264-5f2a-868d-cdbfe8de81c9 | note | Inspection Type (Visual, other) - Record & attach to ITP
ba7960e7-bd71-5bb6-8c43-e06007ddde1d | note | Inspection: Key - Inspection
5bbb5043-b9a1-56cf-8a78-1b6a60f82e6c | note | Inspection: By - IP
7d28013e-08a6-451c-8899-0b1a746cc8b2 | checkpoint | 4.7 - 150mm swing check valve. Item # 7
68fedaf9-1c93-52f8-8494-ccc105f996b2 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
a8f688d7-93aa-5b6e-9469-075f65178db8 | note | Acceptance Criteria - Use diametrically opposed touque sequence
c8ba7434-f511-5c49-a37a-36db29a00022 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
7e666594-265e-5bcd-8c1c-ff2ed6d9a15f | note | Frequency - Each Side of Valve
60a5f616-5575-5f5f-8058-6dd7fe19633b | note | Inspection Type (Visual, other) - Record & attach to ITP
55107423-76a6-5897-9ffa-3b7f2ea4af32 | note | Inspection: Key - Inspection
560b2abf-8eca-5c0d-be4a-5d1a01e19563 | note | Inspection: By - IP
f8549c83-313d-436d-be67-c3d451d64d8c | checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
ca7cab1a-1b5c-55b8-87aa-0799bf9b2293 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
0cfd491f-0e90-5dfd-b0ad-e030e97ae621 | note | Acceptance Criteria - Use diametrically opposed touque sequence
02bdc93c-e0a7-5f8b-9487-5848d26917fa | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
64389bfd-f807-583c-82fb-0871e8d1c01b | note | Frequency - Once
c36c7b08-aceb-56df-b0bb-ebbcbe9ecdab | note | Inspection Type (Visual, other) - Record & attach to ITP
7702735e-619c-5592-8720-626b24c70212 | note | Inspection: Key - Inspection
0406c148-cce0-510e-bca8-296a55d02692 | note | Inspection: By - IP
b7716a82-861b-438e-8787-925137762fb9 | checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
decf3ce8-edf3-5a76-80e1-3da848e0fe8d | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
d626b6c0-483e-541b-bf86-ff7391bc3819 | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
301e77bc-f1bc-5d5d-b87d-0452a23b6372 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
3563dc44-029b-5290-a2c1-b2236befd340 | note | Frequency - Once
381d90d5-95a8-5f72-8a27-8bc534da706e | note | Inspection Type (Visual, other) - Record & attach to ITP
18aac799-0742-5ab4-9a34-0bdb3e479e09 | note | Inspection: Key - Inspection
0cace3a1-a025-5494-b9f0-5733503b2d35 | note | Inspection: By - IP
3603ab52-fe18-476c-94e5-0424786ca1f4 | checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
613fd92e-aae0-5759-bd40-e3eacfbd46c8 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
6f79b1de-5e89-5d8c-9f88-1a06b6589cfa | note | Acceptance Criteria - Use diametrically opposed touque sequence
88a2feda-4480-54d3-a5ff-de3ee216cde3 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
cb284ec9-8031-5b30-80b9-36a15b0d402c | note | Frequency - Each Side of Valve
43721e36-87af-55a4-a053-bc15ca9b818b | note | Inspection Type (Visual, other) - Record & attach to ITP
a8f8d25f-7be5-5f2f-add1-81c17ff56564 | note | Inspection: Key - Inspection
0cd9f547-d66a-5629-a5eb-75060ed5a389 | note | Inspection: By - IP
11901f3e-bad4-476f-9353-5bd85eb6d399 | checkpoint | 4.11 - Pipework bracketing installed and is secure.
fdbb4115-1f02-5f6c-87ec-78431e7f23f4 | note | Inspection Point: Quality Control Activity - At completion of pipework
bd4766f0-a879-5893-a35e-edffc4a7584f | note | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
6d6cf4a5-3422-519f-881a-ea13227d7b6e | note | Verifying Document - As indicated on the drawings
39f4cd8a-f3a7-5bca-bd6a-922163e9c699 | note | Frequency - once
827754bb-ba28-5e8d-963f-6bf3d621ec9b | note | Inspection Type (Visual, other) - Visual
fa247592-bcc4-5d5e-ac1b-340d18aa614a | note | Inspection: Key - I
3b2fc194-2ffe-5380-9d62-14f093c87b43 | note | Inspection: By - IP
82f82659-7981-4ab8-9106-de9eef390547 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
b15fce3b-9ae2-4f16-a2d4-09d96b0acff5 | checkpoint | 5.1 - Final inspection to installed pipework
56eb81d5-3d61-5517-b44f-e1a39cacc9a6 | note | Inspection Point: Quality Control Activity - At completion of pipework
1a1dd471-95ec-598c-9a5e-751b709eb234 | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
7ef4cf0e-89f7-5e4c-8816-011089a43493 | note | Verifying Document - As per drawings
de0e872c-0b95-5304-85cf-38246875cb19 | note | Frequency - once
9ad6143d-254a-5120-9d01-878b06c1852d | note | Inspection Type (Visual, other) - Visual
7a864cc4-8d05-5475-9940-1b6353fa7adc | note | Inspection: Key - I
c9892299-d337-56f1-a9c3-e5cc795b04ee | note | Inspection: By - IP
559938ce-47b6-4e93-a7d5-54028306e682 | checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
e471ec81-aedb-518f-8302-a91804279c2d | note | Inspection Point: Quality Control Activity - At completion of pipework
e1ed3373-38a8-50a9-be8e-493c8a0d7736 | note | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
fe28191c-66e5-5205-bcfd-b87735094642 | note | Verifying Document - As per drawing schematics
3a726664-27a0-521c-a989-123ba74f2a6e | note | Frequency - once
2456b281-b35e-5116-b2b6-401fe6351b81 | note | Inspection Type (Visual, other) - Visual
82a9c429-392e-5900-9b8f-3043d16a7bb3 | note | Inspection: Key - I
832f2628-66df-5624-9099-3ece0f4f20df | note | Inspection: By - IP
92a84c7a-489c-41af-bd0e-ad686a4146a1 | checkpoint | 5.3 - Pipework bracketing installed and is secure.
3e3a7bda-df45-5036-992c-7de32f2f4cfa | note | Inspection Point: Quality Control Activity - At completion of pipework
f38349a3-375a-5916-a563-1712c62d9bae | note | Acceptance Criteria - Pipework complete and installed
d5475874-c751-5ed5-957d-af6419b79c28 | note | Verifying Document - As per drawings
94649beb-7e6c-58f0-94b6-e4b1edaa5356 | note | Frequency - once
36576e85-e91d-5db6-9caf-b33940f329af | note | Inspection Type (Visual, other) - Visual
5552ad98-941f-5916-8eb3-84151c5b5f44 | note | Inspection: Key - I
c5e393ae-714d-5506-9f78-bd60eaac0efb | note | Inspection: By - IP
cfb97827-fd38-4581-bc10-2e87e551ab85 | checklist | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3 | itp | 561482-ITP-006.3 - Pipe & Fitting Installation Pump 3
b42c6ac3-9255-4690-9283-4b31fb8454ac | section | SECTION 3 – RECEIVING INSPECTIONS
d0fede74-778d-4039-9331-52d1cdd65e22 | checkpoint | 3.1 - Stainless Steel Pipe components
c5261988-f054-51c9-8b4c-04b4e3670aee | note | Inspection Point: Quality Control Activity - Obtain the mill certificates for the materials used - 316L Stainless Steel
90992016-0cb2-58dd-aac0-205155fb4a76 | note | Acceptance Criteria - Documents from the supplier/Manufacturer
612e0151-a290-52ff-803f-03f5025bfbc4 | note | Verifying Document - Mill Certificates & Welding certificates
303e51ca-5fc0-5d2c-b83b-2b56eaf237e1 | note | Frequency - Once
a49bcd6a-a74f-5ffc-bdbb-c2a6950ae3fc | note | Inspection Type (Visual, other) - Documentation
79d45f11-90d8-54a2-8f8b-5a9b302c8d6e | note | Inspection: Key - C
c42324be-2eb0-5ca4-b956-62d44bff93f7 | note | Inspection: By - IP
8a9744e4-c18e-413a-aa00-1e123e2da9b4 | checkpoint | 3.2 - Stainless Steel Pipe components
93e85615-459e-59ba-b9a9-67ff7ff2230a | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been delivered
74c2a989-78f2-52aa-aa61-7824b3283fd3 | note | Acceptance Criteria - Quantities as shown on the drawings
c80fee4e-2aa0-5b6a-8e70-75f208f1f132 | note | Verifying Document - Drawing M0001
4d455161-f3a4-5d85-b6ae-46a0f4a3b725 | note | ○ Drawing M0002
122b0d82-d4b1-5114-833f-04df1be2aca2 | note | ○ Drawing M0003
98cfc088-855b-5608-a4e5-11caa6460a8b | note | ○ Drawing M0004
96b552a5-f253-5f49-816f-80ac78fccb3a | note | Frequency - Once
ab978ea9-71c3-5c1d-bdb3-b85cc676c1d3 | note | Inspection Type (Visual, other) - Visual
56a7278b-8b07-5c55-ace3-7851639b12a4 | note | Inspection: Key - C
cf9e8a08-cd79-512c-8d7b-4493f8616352 | note | Inspection: By - IP
ccaf9a83-66b6-4782-a28e-ca7e65417faa | checkpoint | 3.3 - Stainless Steel Pipe components
1f1d2f1e-050b-5b7b-83b5-2dc8b7e34179 | note | Inspection Point: Quality Control Activity - Take delivery of components from Supplier. Verify all components have been manufactured to the correct dimensions
17818ac9-ebc8-5160-abc6-55ad05762a60 | note | Acceptance Criteria - Dimensions & orientation as shown on the drawings
711ab90d-75c1-5152-a09a-f6b7c75da0a6 | note | Verifying Document - Drawing M0001
8261307c-0f5b-5458-92c6-f7350a95895c | note | ○ Drawing M0002
e96ae188-664f-5016-aa7a-85cdcc5486f1 | note | ○ Drawing M0003
a33b8f79-b4bf-5779-b809-59a232eaae00 | note | ○ Drawing M0004
80482a50-0812-50ac-923e-d8cba19197ba | note | Frequency - Once
5432dcd7-2792-5b10-b041-823a3fb7d994 | note | Inspection Type (Visual, other) - Visual Dimension Inspection
1f7a3f41-27e5-5d8e-abf2-2d80e1644422 | note | Inspection: Key - D
82869995-fb43-5875-825a-bc7c7419e6f1 | note | Inspection: By - IP
46dda6c9-eda8-4598-94a5-de7b19142f97 | checkpoint | 3.4 - Valves & Ancillaries
0e35853f-36d9-5eb3-be60-a18c65ca4cb3 | note | Inspection Point: Quality Control Activity - Check and verify that the Manufacturer & Type is approved for use by the client
96b1d56b-7663-5304-97b5-ee7039382770 | note | Acceptance Criteria - Must be on the Approved Products list
796279dc-466b-5071-8d06-f1398902b3e9 | note | Verifying Document - Specification - Approved Materials list
bb1e9ae0-5fed-5657-833a-77e67aa19c45 | note | Frequency - Once
7b3d49b5-4630-5e2f-8a4b-a9537db863f3 | note | Inspection Type (Visual, other) - Visual
caa595ac-254a-568e-9dc9-2b148a9e66c7 | note | Inspection: Key - C
4aa88059-8c23-561c-9487-e9f2c3accdde | note | Inspection: By - IP
2de45f86-3031-446a-b7a7-762599ae6ade | checkpoint | 3.5 - Dress Sets (gaskets & fasteners)
3a0f1f99-1269-5fe6-9828-3c6e6ac4156d | note | Inspection Point: Quality Control Activity - Check and verify that the dress sets are compatible with the flanges and the gasket material is correct. Check correct quantities/sizes/flange patterns etc
8f9cb03d-8536-5e99-a00c-678a24383dad | note | Acceptance Criteria - Must be on the Approved Products list
1cce3895-a10a-51aa-8c5c-71400c8cf6cd | note | Verifying Document - Specification - Approved Materials list
620833ed-05a6-54c6-a9d4-e103b05392e3 | note | Frequency - Once
0fde40c1-4319-5aeb-8476-be8b3f397606 | note | Inspection Type (Visual, other) - Visual
b0c0e7d7-9e0b-5c67-a93c-218a10dd15fe | note | Inspection: Key - C
50ca292e-0c4f-5a2b-bfe4-f9a2835b031a | note | Inspection: By - IP
1082815b-7f12-46f4-9644-53168c3469c6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
f5970011-e40e-4088-b276-83d52ce4e0fe | checkpoint | 4.1 - Fasten Wet Well side/pick-up to spool (cast in wall) Item # 1
f355917e-fb89-5e8f-af9f-27c9c7e6fe28 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners
537059cc-1d7e-53da-ba51-3b8ff85a3653 | note | Acceptance Criteria - Use diametrically opposed touque sequence
0b9dc1c6-98a4-5ddb-bde9-be90e4d9620d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
6b96b962-7b72-5c6e-bbac-108c8f7a0006 | note | Frequency - Each flange
c851e559-1641-5c9d-b748-bf96129dfd4f | note | Inspection Type (Visual, other) - Record & attach to ITP
15db1b77-09c7-5ac7-8a8a-0b726ef473f9 | note | Inspection: Key - Inspection
63a365ba-80fe-5ce4-8932-d345328a1b14 | note | Inspection: By - IP
854e8896-1f6d-4066-a508-2217683d4f2c | checkpoint | 4.2 - Fasten Dry Well side from spool (cast in wall) Item # 2
f7f7c8bf-5cb6-53dc-9bae-453c31febc73 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
7b36e7c6-ebab-5a11-b189-ef975fa4f733 | note | Acceptance Criteria - Use diametrically opposed touque sequence
58b33258-be7d-5eea-8cc7-d96aaf1f417d | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
b3e821db-b62e-5a15-b85b-0948edd9f0b7 | note | Frequency - Each Flange
577fb6a9-197a-5aed-865a-d50c26ce0e70 | note | Inspection Type (Visual, other) - Record & attach to ITP
d93fce37-d7a6-52d5-ab11-5a9bf6809568 | note | Inspection: Key - Inspection
3c3aeb3a-2ad6-5b6a-966d-e6518052c073 | note | Inspection: By - IP
29d4a627-364f-4b14-a925-4864b028b8c9 | checkpoint | 4.3 - Isolation Valve 150mm Item # 3 (suction side)
0375ec7b-7d15-57d9-98d2-8e7a543a7ad4 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
482efba2-a973-515e-8a77-ed5ef032b14c | note | Acceptance Criteria - Use diametrically opposed touque sequence
39cd518a-9e5b-57e6-a1f5-3443096bfc0f | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
f61b8005-d97d-5593-8a5c-4ff7843afc30 | note | Frequency - Each Side of Valve
c2687255-cc87-5ad2-ba69-828d75baea83 | note | Inspection Type (Visual, other) - Record & attach to ITP
4fd3cec5-6b22-5c4b-b5bd-4cb0fbb91c5c | note | Inspection: Key - Inspection
7957a4a6-5c9c-57e4-a737-f55aa8af4313 | note | Inspection: By - IP
78efdffc-e0d1-4a57-a893-d9d17664779b | checkpoint | 4.4 - 150mm Dismantling joint (suction side) Item#4
a232328d-1f84-5b34-ab76-5b73f4a5dd9a | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
b1565531-640b-5c9a-8273-2b4821279298 | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
830f0a34-7b0f-5759-a540-74605dbf42ce | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
6bff1e55-d2dc-5be7-a076-27329adebcb4 | note | Frequency - Once
44ddfa07-81c0-5538-a6fd-cb9bf95634d8 | note | Inspection Type (Visual, other) - Record & attach to ITP
39aea7bc-928e-5903-8dab-9226fba79dfa | note | Inspection: Key - Inspection
53da1185-624a-573e-9108-c132fcbd0dc6 | note | Inspection: By - IP
983d988b-0e8d-45e6-94aa-7f067703fe6b | checkpoint | 4.5 - 150mm Flange Adaptor Spool. Item # 5
22ae6640-b6ab-5ade-bfe8-4e59b38da88f | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
577d5fce-8180-5838-9847-3d688ea8078a | note | Acceptance Criteria - Use diametrically opposed touque sequence
466efce7-f27c-5037-815e-77fcb0958732 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
66b484d4-df7e-513c-a96e-1b8106804c11 | note | Frequency - Once
ffab5aca-e2a5-505f-a931-81ce19d90787 | note | Inspection Type (Visual, other) - Record & attach to ITP
15ea6d3c-e4f6-5cd4-a165-b997725bb5ff | note | Inspection: Key - Inspection
83c77a7e-2270-5660-85b2-0a2dcd246852 | note | Inspection: By - IP
ff1b21a6-f2fe-4b77-8173-9ea539eccbb1 | checkpoint | 4.6 - 100mm to150mm Sweeping Flange Adaptor Spool. Item # 6
3d1fe5a6-3833-508a-bf2d-0f13ab178d49 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
2e9f5604-b5d7-5cc6-8d38-74062df8e349 | note | Acceptance Criteria - Use diametrically opposed touque sequence
abc9e1db-baa8-5220-ade7-c52485950a5f | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
ee43245d-7ab0-5f11-bc12-f726955fb47f | note | Frequency - Once
d2da54c9-2b8f-5c09-8efb-af0a07c2c819 | note | Inspection Type (Visual, other) - Record & attach to ITP
9e08647e-0b81-512f-81e2-5ee3c4a730c0 | note | Inspection: Key - Inspection
4083040e-dd17-5967-baa4-9f923ce2b4e6 | note | Inspection: By - IP
84784027-b08b-4162-976b-21c4fe506445 | checkpoint | 4.7 - 150mm swing check valve. Item # 7
e007c05f-4528-5056-b3be-fa1f538a265b | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
b319815a-8042-5f77-b56c-03fd9a010d9c | note | Acceptance Criteria - Use diametrically opposed touque sequence
f465c2ab-ac7e-53a3-b9c4-cf11223ff9dc | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
9fccb7f6-dea7-55c0-8b1f-3afd00e35696 | note | Frequency - Each Side of Valve
4f985bc2-20c8-5a6c-ae90-eb4583041f36 | note | Inspection Type (Visual, other) - Record & attach to ITP
5a1a4954-7b01-5fd9-98a4-5e8be388130a | note | Inspection: Key - Inspection
94d6fb25-27af-55c3-8d3e-f99519bb3b99 | note | Inspection: By - IP
a770471e-9117-4df3-a739-ce233c50b5d4 | checkpoint | 4.8 - 150mm Sweeping Spool (discharge). Item # 8
ff881459-5ae1-5ff5-8ae0-c5369e90a1f5 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
02184b3f-322e-5b0e-a5e8-70106b42815e | note | Acceptance Criteria - Use diametrically opposed touque sequence
6c86f0d4-c930-5b68-a35b-6a7f18890bcc | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
8644d680-9739-5c18-9126-37d15ff4cf23 | note | Frequency - Once
e4bff31f-3106-5ec2-9085-4dd165a8a89c | note | Inspection Type (Visual, other) - Record & attach to ITP
1e23501d-30c4-547d-b5a4-75fabad412ee | note | Inspection: Key - Inspection
d1c248be-adc4-5ce1-b9d7-6836a54f663f | note | Inspection: By - IP
60ada0fe-835e-48f4-918d-bc6975b1649a | checkpoint | 4.9 - 150mm Dismantling joint (discharge side) Item#4
e5da41ac-543b-5c5f-a433-1ad58616d74e | note | Inspection Point: Quality Control Activity - Torque fasteners to relevant water standards
b98d7e7c-9852-5827-855f-c0dcff68ad3a | note | Acceptance Criteria - Use diametrically opposed touque sequence and manufactruers instructions
8957ed58-2574-5547-9aca-9a9df9cc6ca1 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
5d126ca8-0c2e-5ba1-aaa9-53f7d939dc4d | note | Frequency - Once
8437cc27-e011-5886-b9c6-a07a6caf6475 | note | Inspection Type (Visual, other) - Record & attach to ITP
1009570e-8d54-5add-ac16-1f9183d87b1e | note | Inspection: Key - Inspection
365cda3d-1a48-5e5b-aa2b-abf18b90e42e | note | Inspection: By - IP
638157d3-3704-46a1-8a15-694a4dc3de01 | checkpoint | 4.10 - Isolation Valve 150mm Item # 3 (discharge side)
5fd86e09-fa49-5167-ad1a-5b5336f49421 | note | Inspection Point: Quality Control Activity - Install gasket, bolts & nuts and tighten. Torque fasteners to relevant water standards
84bafd06-76e3-5197-927f-692dd9ff29fa | note | Acceptance Criteria - Use diametrically opposed touque sequence
5c3073c1-dd0d-5525-a388-5eef3f2bbc14 | note | Verifying Document - As per WSA-109 Australiann Water Standards Guidelines - 80N.m
76f19e05-b359-5b93-9187-8f3e78ef659d | note | Frequency - Each Side of Valve
765b8401-b109-5016-8ec6-a3ca954b58e2 | note | Inspection Type (Visual, other) - Record & attach to ITP
15b9e92e-f86b-5682-93cb-b5b83a1692de | note | Inspection: Key - Inspection
c3eed160-23a7-5a81-9f94-6a36ae3f1a6d | note | Inspection: By - IP
7ada870e-4791-485f-98bc-28bc940bf291 | checkpoint | 4.11 - Pipework bracketing installed and is secure.
e57d93b4-344c-54cf-8b18-5c385752d8c9 | note | Inspection Point: Quality Control Activity - At completion of pipework
565a8e62-b6eb-5a39-97fb-409ffea4f689 | note | Acceptance Criteria - Pipework complete and installed. Adjustable brackets
f761ac55-9b2d-5d21-bbb1-311c9def2252 | note | Verifying Document - As indicated on the drawings
d2d1ab37-64be-5247-98b3-69974f35b001 | note | Frequency - once
7d310d1f-fd2c-508c-a296-a6a4141fb9ca | note | Inspection Type (Visual, other) - Visual
fb78e04f-851b-5693-b98c-78ed9038210d | note | Inspection: Key - I
b5bc7163-808d-5024-b340-c0f0cdbc4ac2 | note | Inspection: By - IP
d791a7e9-3ae7-4fd1-99eb-e8ba37d0929e | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
06eac443-4ff1-4eca-80fa-3fc62b4def83 | checkpoint | 5.1 - Final inspection to installed pipework
ad903ae2-fc4b-5736-bdbc-85d2b2b3606b | note | Inspection Point: Quality Control Activity - At completion of pipework
3d0199d3-c4b1-58f8-9d34-b11941790c6d | note | Acceptance Criteria - Flanges are straight and bolts tightened all threads sealed and leak free
163207f0-641e-51d1-9a7c-4a39ae75fc57 | note | Verifying Document - As per drawings
60db29ca-3bca-5fda-9f81-6b88f6d641b5 | note | Frequency - once
fca7dc03-6751-5cb1-a956-7864a139045b | note | Inspection Type (Visual, other) - Visual
5e9b541a-5cc1-52f7-917b-7b751b284b66 | note | Inspection: Key - I
6e1dea6f-aba1-5369-9bbc-7ad039e32527 | note | Inspection: By - IP
02ed4267-273f-4fba-a0cc-8a29aa4e0e97 | checkpoint | 5.2 - Instrumentation. e.g. Pressure transducers and sensors are fitted correctly - No Damage
152cd870-74d1-5982-8143-c31480428267 | note | Inspection Point: Quality Control Activity - At completion of pipework
a3c23e62-1611-5ac3-a93e-b6ec7779c358 | note | Acceptance Criteria - Pipework is installed and correct fittings installed to accept the instrumentation
511ccd85-cfd8-58a8-b1bc-8da5c6e52864 | note | Verifying Document - As per drawing schematics
91ccd3c9-814f-5a5b-99bd-254fe5a4a2f4 | note | Frequency - once
e5b88775-4a7b-53a7-8aad-1a7996192535 | note | Inspection Type (Visual, other) - Visual
e5860c8a-1ffb-5663-8314-32acac5b437b | note | Inspection: Key - I
5198f3f0-ba55-5d05-b523-ae2ef08c5553 | note | Inspection: By - IP
66dfa977-ec12-496a-b3c7-0f81ca7931d2 | checkpoint | 5.3 - Pipework bracketing installed and is secure.
6d270fbc-facc-5a6c-917b-ac9a85071b88 | note | Inspection Point: Quality Control Activity - At completion of pipework
11e86d63-2962-500c-b784-9bde6c6ecdf6 | note | Acceptance Criteria - Pipework complete and installed
0f297426-3853-59b0-9e41-7765922019be | note | Verifying Document - As per drawings
8bd62f33-3999-5f6a-8264-8f6aef453293 | note | Frequency - once
a07bd5e3-6693-599d-a840-5b8c43406a34 | note | Inspection Type (Visual, other) - Visual
c4b4d552-6e28-5728-8e9d-9d35cca50d6b | note | Inspection: Key - I
eb2166f4-24d0-5d16-a977-13f7bdc081ce | note | Inspection: By - IP
2d811e6b-5f68-4566-884a-670cda68e9e7 | checklist | 561482-ITP-007.1 - Wet Well Wall Penetration 1 pour | itp | 561482-ITP-007.1 - Wet Well Wall Penetration 1 pour
22565930-02ed-47f8-bad0-430492d2b5dd | section | SECTION 3 – RECEIVING INSPECTIONS
6107b9b2-3892-4769-b565-dc6392124642 | checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
3e263f13-ac94-50a2-90c2-bb04d9d3dff4 | note | Inspection Point: Quality Control Activity - Calculate Quantity
ac8ee9aa-aa58-59b5-b2f8-32dbc81b6164 | note | Acceptance Criteria - Correct volume to be calculated
fb0d8403-34be-520c-8571-1109c2963761 | note | Verifying Document - Product Datasheet
7ed15ed7-7c94-5d9c-9622-c84a3612655f | note | Frequency - Once
3aa542a0-8115-506c-8d4a-fc74ea622ddd | note | Inspection Type (Visual, other) - Written
85af33fa-b9e3-5e81-b5cc-6f14dbfe4d97 | note | Inspection: Key - R
5655b928-07be-522d-a0e4-3404f96086d9 | note | Inspection: By - CR
5d8fee43-1a9a-4b1e-a3fd-dfaddd761847 | checkpoint | 3.2 - Installed Reinforcing
8fad7073-4491-51a3-9d3d-6218b72da051 | note | Inspection Point: Quality Control Activity - Measure and check
b120ad3a-e746-5f43-a945-14b76604a782 | note | Acceptance Criteria - Matches Design Drawings
6a72a2bd-797d-5c01-944a-a302eb87d72e | note | Verifying Document - Drawing M0003
97cab6d5-4c09-5ecc-9cf0-d32f5d29bb1d | note | Frequency - Once
11cf89d3-103f-591d-92fd-6bc638d22b30 | note | Inspection Type (Visual, other) - Visual + Photographs
0e96cc18-bbec-52d8-a000-51c83180acbe | note | Inspection: Key - V
c398f192-8eda-5645-ad61-ad6c78d1d042 | note | Inspection: By - IP
a2e27920-d9f3-4157-882c-b80651633182 | checkpoint | 3.3 - Spool/Puddle Flange
e714f129-396e-5a70-8f25-d3418d00ded1 | note | Inspection Point: Quality Control Activity - Measure and check
b473b24f-5e51-57ae-b64e-25ce32a91364 | note | Acceptance Criteria - Pipework is straight and parallel to structure & pump
973ce2c0-9192-5114-8e2c-994fde379926 | note | Verifying Document - As per drawing M0001 & M0002
9787efda-c91e-5d9d-8fd6-1d8e98591ed4 | note | Frequency - Once
2ba46067-e7ef-53c0-a18d-42c357b04f4d | note | Inspection Type (Visual, other) - Visual + Photographs
d0e7f62e-0a69-5000-8d9e-3c5eb1964b8d | note | Inspection: Key - V
af9e0262-aef3-5516-876f-7399361295db | note | Inspection: By - IP
3a0d5b87-cb8f-4807-910b-d9d6a2f3f463 | section | SECTION 4 – IN-PROCESS INSPECTIONS
c43ba4cb-ff41-4154-a14a-7f6ccaddaa20 | checkpoint | 4.1 - Boxing of penertation
8d749ef8-5cfb-5281-a295-d0dc2d1f4851 | note | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
5d87c58d-2c86-5f5f-b8b4-5f204409ace8 | note | Acceptance Criteria - Matches Design Drawings by dinension and configuration
a430130d-6b23-5ab2-948f-424c5fdf3436 | note | Verifying Document - Drawing M0003
f3b738bc-fc9d-55a4-8b21-ee7cccd0bb56 | note | Frequency - Once
5c9f3b32-4700-56cf-a076-401e76067273 | note | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
eb4eea91-8669-5b47-983a-512ca9f81b11 | note | Inspection: Key - H
39995cf0-109c-5818-80c0-2959c9587207 | note | Inspection: By - CR
0e54279f-0ad0-4a70-866e-7458970c6b0c | signoff | AUTHORITY HOLDPOINT
72f1d584-c8ac-4f9d-a112-be0cc94521bb | checkpoint | 4.2 - Mixing of Grout
994ecbd0-a8e3-548e-bcf9-3b48a2d17d6b | note | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
131e123a-7693-557a-93cf-3400a37332f5 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
0803c047-3a74-522c-a334-6c18c17b2b3f | note | Verifying Document - Product technical instruction sheets or certificate (if delivered)
c606ccc3-eb64-54c9-a166-3cb886324f15 | note | Frequency - once
d73b9fee-d98e-52d0-9353-0b32045c4ffc | note | Inspection Type (Visual, other) - Document
361142bd-2f08-5458-a966-e65d14d18634 | note | Inspection: Key - I
e68133af-3681-5fee-afd3-d6f9ca6a1a2a | note | Inspection: By - IP
cb94ee82-6070-4dee-b497-bdfcbe12641b | checkpoint | 4.3 - Casting of wall penetration
1952d89c-d341-5ea3-8167-09f2cc81ba2c | note | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
bd69721e-3265-5eed-b400-77d9f0eced33 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
e660cdfa-aad7-5200-a0e1-a0324c599800 | note | Verifying Document - Product technical instructions
950effc7-7e56-5b69-aa1b-abaf15ab65d2 | note | Frequency - once
c7012365-ec6a-59cd-b3ef-9dc6d65ef9b5 | note | Inspection Type (Visual, other) - Dodument + Visual
855670dc-412e-56e5-9dd4-c56b0db47f26 | note | Inspection: Key - I
e5f6738b-b9ac-5e51-bac5-1438b1d3b8ac | note | Inspection: By - IP
fcdb6e17-b738-43b3-9fdb-7888f8efc96f | checkpoint | 4.4 - Vibrate
3aec6c0e-f38b-5b1c-9d07-2c971e24c81d | note | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
edbc8222-6e18-5195-80d4-e388a94a9811 | note | Acceptance Criteria - Grout Placer Approval
86dcffee-1199-5ab7-9d58-04e0767bbee2 | note | Verifying Document - This ITP
40f841bc-09c0-578f-9ad3-02a4e58a12d9 | note | Frequency - once
0f3a9c5f-003c-5172-a4c7-831361b67b33 | note | Inspection Type (Visual, other) - Visual + Photographs + Short video
29a3d63c-9b1e-55a0-bce1-b83352e84081 | note | Inspection: Key - I
39c2e6e0-20b5-5b0e-903f-7bdcf429cd4a | note | Inspection: By - IP
031afd3d-1b7d-49cd-873e-1cea799eb633 | checkpoint | 4.5 - Monitor curing process
bd0fd0c0-63e5-5593-9a1b-c5e8438f4ee6 | note | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
34db7514-b2b5-5080-a978-1f7b438502ce | note | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
1dac76f4-8bcc-50a9-895b-fb8b84dbb8f6 | note | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
adf83959-a6e5-5e68-8d65-8eba08e60de6 | note | Frequency - once
ddf48fcf-d842-55f0-baf9-5cb326034f6d | note | Inspection Type (Visual, other) - Visual
b21dc596-50be-5cb6-b961-801bfdf8c54b | note | Inspection: Key - I
c64cbdf9-dcf1-55ba-89a0-8bc155f763de | note | Inspection: By - IP
cbe59882-8d84-4a4e-81ca-860e8205e92a | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
1da42167-ae12-4739-9349-be1dc4cea0f2 | checkpoint | 5.1 - Remove boxing
7e3981d7-6dd8-51ba-b60d-c945cff4ab88 | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
a69405f1-89f3-5d35-849f-bdcb9d211f8c | note | Acceptance Criteria - Time period as indicated on programme
7643bdb1-c591-5325-badc-607941c97364 | note | Verifying Document - This ITP
29fc7592-e87b-5853-84a1-eab500cd1cf7 | note | Frequency - once
2ef7ddc4-7331-5492-8958-13bd52efd559 | note | Inspection Type (Visual, other) - Visual + Photograph
bd658325-a60e-5ca1-97d4-119818b8a595 | note | Inspection: Key - I
3092f82f-f21d-5416-bec1-c06f9693aeeb | note | Inspection: By - IP
bc1420ff-2527-4de3-9429-46c6593839cf | checklist | 561482-ITP-007.2 - Wet Well Wall Penetration 2 pour | itp | 561482-ITP-007.2 - Wet Well Wall Penetration 2 pour
304a71b0-deca-4284-b9e9-7cdecd82de84 | section | SECTION 3 – RECEIVING INSPECTIONS
446fa00e-d91d-4d5e-86f8-0ea0861158b4 | checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
b09f668c-1acb-5f77-8cda-5f7a03bcc2a6 | note | Inspection Point: Quality Control Activity - Calculate Quantity
16c0e77d-a0ce-51c2-b7e3-cc755f887fe0 | note | Acceptance Criteria - Correct volume to be calculated
83ff47a5-22ff-5cf5-a119-981f9f014097 | note | Verifying Document - Product Datasheet
ce5042e5-6f48-5b75-ac84-40ae241a9e05 | note | Frequency - Once
667f302a-729f-5749-8ae5-587f7433681d | note | Inspection Type (Visual, other) - Written
8040d909-f17d-50d2-abe7-2d990959f939 | note | Inspection: Key - R
79ff5fec-a062-5457-b8e4-51a09d7cc26c | note | Inspection: By - CR
9746883d-98f1-45b2-acaa-dddb08aaf916 | checkpoint | 3.2 - Installed Reinforcing
48bfec64-8f64-5a82-a569-426cabc33102 | note | Inspection Point: Quality Control Activity - Measure and check
ad5171e1-b46e-5d28-a0ab-2c6f8e834c84 | note | Acceptance Criteria - Matches Design Drawings
a8201a93-6501-5c11-904e-baabfe50266c | note | Verifying Document - Drawing M0003
a88b3469-3d2b-5ec4-8069-82f78305a11e | note | Frequency - Once
378afb55-f88a-545d-a1e2-16c63f82a916 | note | Inspection Type (Visual, other) - Visual + Photographs
3e904b51-018b-51c3-9812-1b7e32f57195 | note | Inspection: Key - V
bc3ed07b-c7b8-5ec9-9d61-6c81737f81cc | note | Inspection: By - IP
bd5eb125-8e54-46ee-a545-f2819f597d9d | checkpoint | 3.3 - Spool/Puddle Flange
22c279cf-9d78-57f6-8ed0-850b002fd0e7 | note | Inspection Point: Quality Control Activity - Measure and check
ac9d9943-4385-5bb8-8331-b426c6c7de69 | note | Acceptance Criteria - Pipework is straight and parallel to structure & pump
c3a07b8a-d1c1-577e-8a45-b9a600a5e23d | note | Verifying Document - As per drawing M0001 & M0002
b09e84da-f1e4-5402-8bac-c14a07c75ad1 | note | Frequency - Once
812a12b5-183b-5c5d-bb7b-789fcf795efd | note | Inspection Type (Visual, other) - Visual + Photographs
960e6986-5e19-5f18-b880-7e8aa386e69e | note | Inspection: Key - V
fb0bfee5-5a80-5f59-b51c-60f9ae9309ca | note | Inspection: By - IP
e97a1b88-c827-4bdd-8e16-86ec3852bda6 | section | SECTION 4 – IN-PROCESS INSPECTIONS
1ab7247c-e1f5-4664-a563-257538bcbe02 | checkpoint | 4.1 - Boxing of penertation
58b1e467-dc7e-5147-a2a2-7f987ecad595 | note | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
818e413c-dddb-5961-b433-6617113bb206 | note | Acceptance Criteria - Matches Design Drawings by dinension and configuration
92b011a5-cd2c-5664-be04-ad8c1dc979cc | note | Verifying Document - Drawing M0003
237a8813-902f-5e61-8ced-e737e4136472 | note | Frequency - Once
ffd5b831-35f3-510e-a72c-75c0f27a4384 | note | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
4d2ce3d7-5d09-5444-b93b-ac072c1066e8 | note | Inspection: Key - H
d15aa45c-c854-5767-8471-22f500910d25 | note | Inspection: By - CR
f765d1f0-6366-4d87-ae92-270206985be4 | signoff | AUTHORITY HOLDPOINT
9462aaab-9a05-43d2-a13e-275a7a4f2144 | checkpoint | 4.2 - Mixing of Grout
cacc832b-8d5c-5b54-ae8e-5bff87262e0f | note | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
d337d0ca-626a-547c-ac16-f9a5de5e92c0 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
7f5baf11-3fd2-5f06-9eb9-47b39dc97107 | note | Verifying Document - Product technical instruction sheets or certificate (if delivered)
0e01ab11-5f98-5068-9f42-9d03631a3e90 | note | Frequency - once
a4c64f07-842c-5ea7-b3be-d0cd5a40103c | note | Inspection Type (Visual, other) - Document
81afd770-ae94-50e3-bbad-45c83b61e724 | note | Inspection: Key - I
331f19c5-4200-5f1a-92bd-13c6dc4cfc02 | note | Inspection: By - IP
5e308600-f7ea-4735-b153-09b7168731cc | checkpoint | 4.3 - Casting of wall penetration
2a1066bf-c5fd-508c-a8ea-0dd52e1712f5 | note | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
47e8e339-25d3-5ff0-8f2a-26cdd49103cd | note | Acceptance Criteria - As per manufacturers instructions/guidelines
756cd71b-ea0f-590e-83fc-20506dbac9df | note | Verifying Document - Product technical instructions
67af0522-30c4-5f9d-8431-3b4eb236bd0c | note | Frequency - once
420f4762-77dd-5d2e-ba95-b432b975ed45 | note | Inspection Type (Visual, other) - Dodument + Visual
9495d3a0-526f-5409-b1c5-3ba7c86f19af | note | Inspection: Key - I
0a1baa04-189e-5aac-aafa-56b311797ec7 | note | Inspection: By - IP
a769a468-c560-4199-940e-e679c77b945b | checkpoint | 4.4 - Vibrate
7cee828a-433c-5f05-ade0-07b90bba34b0 | note | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
cb752ae0-d39a-5cf0-98a8-1ce73b7f23a1 | note | Acceptance Criteria - Grout Placer Approval
a41925cc-f88d-53f8-bb08-870dcb26a98f | note | Verifying Document - This ITP
862b7064-d975-599c-9662-ebd507984932 | note | Frequency - once
55b9f770-ff5e-5409-abfe-2278f10f3905 | note | Inspection Type (Visual, other) - Visual + Photographs + Short video
08e5b26e-d236-5a29-b496-1f14576ed585 | note | Inspection: Key - I
d2839bd6-32dc-58dc-97f6-6812c2ec43b9 | note | Inspection: By - IP
115f39c0-de85-4ae2-b447-d39310d613d6 | checkpoint | 4.5 - Monitor curing process
f7d8d8a4-584a-59bc-b5bd-fd09bb0f9fd4 | note | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
62493fb8-05b5-574a-bfb6-9669e6a5f816 | note | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
cfb336e0-5061-5dc4-999b-cd57a6b18c00 | note | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
8e51eaad-4c84-5bf6-b951-ca6974f473a1 | note | Frequency - once
0c13a9b4-757e-5dc9-adce-22c7c8c0b77e | note | Inspection Type (Visual, other) - Visual
026108b2-9fc3-5509-ba34-9c43f203fb90 | note | Inspection: Key - I
f2475628-65b3-5331-9704-77b822bcf96e | note | Inspection: By - IP
6b17e4b6-2885-4c70-8419-b2aa6013c102 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
c44061e9-a12c-4627-96bf-8111a4091041 | checkpoint | 5.1 - Remove boxing
e35ab971-04fe-5543-9d62-3d7c751c4c6e | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
4f2acf46-0b77-5bb0-a7e6-79d37e3ac093 | note | Acceptance Criteria - Time period as indicated on programme
3124708e-cfce-5c48-b443-4cd93f7d3d8a | note | Verifying Document - This ITP
52306257-62b3-5f57-b6f3-c00508ea21be | note | Frequency - once
33f7b4c9-ca77-525e-a44d-bc174cd55a82 | note | Inspection Type (Visual, other) - Visual + Photograph
8de2e360-ffc5-55e4-8f68-e10919a47d6c | note | Inspection: Key - I
189349ab-a3de-554a-a3d7-a65f7b1dc72f | note | Inspection: By - IP
04e34cac-7864-4ea8-be15-d3ad0351be9a | checklist | 561482-ITP-007.3 - Wet Well Wall Penetration 3 pour | itp | 561482-ITP-007.3 - Wet Well Wall Penetration 3 pour
06b0360d-0b21-4cc7-adc4-1820304f11c5 | section | SECTION 3 – RECEIVING INSPECTIONS
1424cc86-5d5f-4425-893d-9eff87b8a173 | checkpoint | 3.1 - Grout - SIKA MonoTop- 438R
867db15b-32e7-581b-8c4f-432622d0a50b | note | Inspection Point: Quality Control Activity - Calculate Quantity
bebd161a-d067-5d2d-a8aa-02b36ea4bb00 | note | Acceptance Criteria - Correct volume to be calculated
3a2c21de-d657-5f6c-bc52-9dda28934b26 | note | Verifying Document - Product Datasheet
f418ea4d-12a3-5816-96d2-978b0bff8b56 | note | Frequency - Once
21f2238a-bd9b-53ac-bfd3-777546856f3c | note | Inspection Type (Visual, other) - Written
1541954d-8c94-53df-ab70-06340bc41b7e | note | Inspection: Key - R
6bf755e4-fd10-56ba-98e8-91a2949b0d56 | note | Inspection: By - CR
ae70a5ba-d80f-4519-906b-22b8610dcbef | checkpoint | 3.2 - Installed Reinforcing
320befab-143c-52cf-8340-04ceeaa1568f | note | Inspection Point: Quality Control Activity - Measure and check
d31629d8-f724-5704-b351-d2b81627f359 | note | Acceptance Criteria - Matches Design Drawings
20b31b0a-6e22-5ca2-81b6-440f24a50ce8 | note | Verifying Document - Drawing M0003
c3a4ca37-9e0f-5168-b2f4-f35337067bb1 | note | Frequency - Once
83d94740-e4c0-58f7-a720-76166c76506e | note | Inspection Type (Visual, other) - Visual + Photographs
19dd9dd3-e5a3-5ca0-9c09-aac27bb4ad8d | note | Inspection: Key - V
cd606fdf-ee62-5b82-a4df-a4e06bee5ed6 | note | Inspection: By - IP
db7a8721-9ccb-43c7-bee5-32bb4ae370cb | checkpoint | 3.3 - Spool/Puddle Flange
83aef12f-4a1e-5374-a23d-a211da057a4b | note | Inspection Point: Quality Control Activity - Measure and check
bc1b9770-0aad-5370-a45a-5711bda889cd | note | Acceptance Criteria - Pipework is straight and parallel to structure & pump
dd78d8d1-5458-5cf8-b985-e25603639439 | note | Verifying Document - As per drawing M0001 & M0002
ad8e9905-b451-5e4f-b464-c2ce7839e662 | note | Frequency - Once
c2bbdc77-50ac-51ab-a922-483dc755fc8a | note | Inspection Type (Visual, other) - Visual + Photographs
2117d8d1-221a-58fb-ba03-fb7ee6ca704d | note | Inspection: Key - V
da359d0c-5ce7-53af-b049-009c87aa2af2 | note | Inspection: By - IP
f2106543-ee3a-4d0c-b5b2-d4e7152951ba | section | SECTION 4 – IN-PROCESS INSPECTIONS
7a302fd3-57f3-41d3-9ed3-ff81de64d1a4 | checkpoint | 4.1 - Boxing of penertation
622f7910-c5d6-5147-9147-83cdbd83b394 | note | Inspection Point: Quality Control Activity - Measure & Check. Ensure perimeter of boxing and pipe penetration is sealed to stop grout spill.
c2db3a3c-728e-52ee-94b1-f7d13ab7c236 | note | Acceptance Criteria - Matches Design Drawings by dinension and configuration
9c116b54-9078-5a30-9e76-916eae5fccbd | note | Verifying Document - Drawing M0003
6823b22b-9900-5960-8aad-223a9a4f276c | note | Frequency - Once
c94e6d23-04b5-543e-ba3b-1a9a997bf431 | note | Inspection Type (Visual, other) - Visual + Inspection HOLD POINT
dd476045-050f-5416-a939-6865718f1d47 | note | Inspection: Key - H
364503a6-324e-5c9a-96cd-b02a0b8e3d67 | note | Inspection: By - CR
f0483e66-5fbb-45ae-af36-b06543456593 | signoff | AUTHORITY HOLDPOINT
1f4e5af4-4b43-40fc-94d9-154344dff69a | checkpoint | 4.2 - Mixing of Grout
2f01ccb7-bdd3-5d7a-8c1c-b17d25aebe05 | note | Inspection Point: Quality Control Activity - Ensure product is on hand & plenty of clean fresh water is readily available
82c91494-42e8-50ec-a6ab-eed646bbe920 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
e4aa97a3-ff34-5098-85cf-38ec79b35e98 | note | Verifying Document - Product technical instruction sheets or certificate (if delivered)
60799850-85f2-59e6-9b78-6d5b1275527e | note | Frequency - once
15b55ff5-0c03-552f-b75a-b4f0375691e9 | note | Inspection Type (Visual, other) - Document
b5a9fbae-9d85-5f7e-807e-bfd001dacd54 | note | Inspection: Key - I
461b7755-1d8a-5709-97ba-33642ff993ef | note | Inspection: By - IP
c98d0f80-4268-45e0-876f-0e269f4bdd5d | checkpoint | 4.3 - Casting of wall penetration
9e34b393-f557-5970-9f0d-8c0ad51dcea8 | note | Inspection Point: Quality Control Activity - Monitor the consistency and quality of the grout fill
137a3dfd-3b7f-5e4b-8d09-922cd04f8012 | note | Acceptance Criteria - As per manufacturers instructions/guidelines
311db0c9-fa8d-5bd4-93c0-29ca2b6a9cc3 | note | Verifying Document - Product technical instructions
d4d358cd-0811-57ff-9f01-7cad8c1e6db8 | note | Frequency - once
a91f6608-2f54-56f6-b8a3-b7a46baad0cf | note | Inspection Type (Visual, other) - Dodument + Visual
4ed0deee-20c0-579a-982e-6ec705d2c683 | note | Inspection: Key - I
04cd47f6-bf64-51cf-aa7e-ff74906182f9 | note | Inspection: By - IP
3b43b6e5-5e17-49fe-ada3-a5f9089b1ec5 | checkpoint | 4.4 - Vibrate
03b9b58d-d8d4-5482-b7ba-b9d8297e6a66 | note | Inspection Point: Quality Control Activity - Vibrate to remove entrained air. Ensure all air is removed
16670e7e-6717-58e8-b644-47f62d7f8f4d | note | Acceptance Criteria - Grout Placer Approval
f52486f9-171b-5fff-b79b-877f282c37bb | note | Verifying Document - This ITP
bd5f59f1-31a4-537f-ac78-36e5a0362b62 | note | Frequency - once
1444437b-022f-5369-a456-d0de623017b2 | note | Inspection Type (Visual, other) - Visual + Photographs + Short video
55644158-f90f-5b71-b076-ee03fe2333eb | note | Inspection: Key - I
7f87888f-8f7e-55b1-8099-01ad664e762b | note | Inspection: By - IP
dde21492-2b9c-4418-bf22-40e6953218be | checkpoint | 4.5 - Monitor curing process
4b6cf333-de95-5f7f-a76a-e58291f6c571 | note | Inspection Point: Quality Control Activity - Monitor curing inspectiong the boxing and areas of potential grout leakage.
e8408b5f-936c-58d6-8755-af7025e580a1 | note | Acceptance Criteria - No evident shrinkage or deformation. Repotr any issues to Engineer
694e6da1-b86f-54fc-8ee8-562158606634 | note | Verifying Document - As per drawings allowing 7 days curing time. Boxing can be removed after 72 hours
ed544cb2-6586-561e-9c6b-76e4d2e9e883 | note | Frequency - once
72766d84-38b0-55fa-826c-1aae81ad1e70 | note | Inspection Type (Visual, other) - Visual
33f8781b-07bb-57e5-9591-1b12206c649b | note | Inspection: Key - I
63dc05a9-bc18-59f0-9dd0-32bca517af1a | note | Inspection: By - IP
e183d0f6-2891-4218-8c26-ac36f805058f | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
3545f43d-e115-44ae-a573-3d35a84c41fb | checkpoint | 5.1 - Remove boxing
91ae54fa-1288-5fad-a57c-2eb95939d81a | note | Inspection Point: Quality Control Activity - At completion of all items on this ITP
b99e077a-6282-5693-a33a-50f5866d9919 | note | Acceptance Criteria - Time period as indicated on programme
0ede7792-4f59-578a-8431-fe23ed23489e | note | Verifying Document - This ITP
f7d7c046-0cf3-5193-8db3-b52fbdb2935d | note | Frequency - once
4ce08250-4549-58c9-b6f2-44fb18777ea3 | note | Inspection Type (Visual, other) - Visual + Photograph
adbbc3b7-3357-5bfa-bb2f-beb0f4461d7c | note | Inspection: Key - I
85b3f843-bd58-5fb7-a7b9-4f0f529ff805 | note | Inspection: By - IP
7642b5f8-f11d-41d5-a802-8db12ba8dea4 | checklist | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection | itp | 561482-ITP-008 - Wet Well Wall - Final Pre-fill inspection
897643ba-07af-4fcc-9320-841be3674d04 | section | SECTION 3 – RECEIVING INSPECTIONS
f12897b8-2b19-4264-9d16-42ec0f75a2d0 | checkpoint | 3.1 - Grout Castings (Penetrations 1 through 3)
bbc24578-6407-5fb2-87a4-22a89aa22937 | note | Inspection Point: Quality Control Activity - Inspection of castings.
1960f9a4-e39d-5777-9cb5-076082b89e82 | note | ○ Inspection for air pockets, cracks, fissures oa any other imperfections
97f30c4c-8e07-5f50-b455-edb28f25b28f | note | Acceptance Criteria - Completion of ITP's
8291fbb4-3c36-54fe-a95f-d5d7b1f80349 | note | ○ 561482-ITP-007.1.
5415109c-1002-5bbb-ba2b-16e662c062c7 | note | ○ 561482-ITP-007.2
20101704-dd44-597d-82b5-793b4ebfdb21 | note | ○ 561482-ITP-007.3
bc9e9c4b-864a-596b-b322-2662d0bf79fe | note | ○ Elapsed time of 7 days post pour
5c3ae48d-5b25-5eee-9cc8-ba630ee25ca0 | note | Verifying Document - None
2b700765-d981-540c-96f8-f727c3f9d53e | note | Frequency - Once
deb94657-1d35-5ce7-a4c7-6dbc56fd2403 | note | Inspection Type (Visual, other) - Visual + Photographs
ff873624-7bb1-58cd-9e65-32762746ec6d | note | Inspection: Key - A
ba4a9bd9-fd41-5d9d-85b4-40efc743858f | note | Inspection: By - IP
ed33693f-5050-4464-b663-4c31b7f705be | section | SECTION 4 – IN-PROCESS INSPECTIONS
4398457c-53ea-4878-b3f2-05c38dbb46e6 | checkpoint | 4.1 - Removal of Formwork - Penetration 1
81700b0b-2834-547d-a639-62c439fab0ff | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
a19fa2b4-f00e-5aac-ae07-7f43fba12d91 | note | Acceptance Criteria - Approval from Engineer
0c09195a-9013-572f-b485-d4b6f6636f05 | note | Verifying Document - Drawing M0003 and annotations
e6445a2c-04e9-560a-ba23-8f41776f7998 | note | Frequency - once
1c23c4c9-9d9d-5306-8410-6f8f80072714 | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
8e6a1f4b-6c42-5174-9513-1ad7d4a49711 | note | Inspection: Key - H
e4b0b284-d8cd-50c3-a136-f8fefefa4414 | note | Inspection: By - CR
27aad9ec-dddb-4327-82f9-6e481d97e00f | signoff | AUTHORITY HOLDPOINT
fe3fc288-1354-4f7d-ad6d-ced6772537a5 | checkpoint | 4.2 - Removal of Formwork - Penetration 2
1bcb0277-bbea-5c3f-b6d5-4675eb1122fe | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
8f8ac064-69cf-54e4-baa9-5921c31de038 | note | Acceptance Criteria - Approval from Engineer
0b9df010-81f4-5943-bbd1-aa19d0c4bc5a | note | Verifying Document - Drawing M0003 and annotations
19cf21a7-dad6-5d56-9cda-933c2dc367e3 | note | Frequency - once
04ef2d56-a9b9-5734-b416-9de66b3e7aae | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
0826d7a9-8f47-5ec4-b114-ae067da1c8f1 | note | Inspection: Key - H
a6810b6f-a70f-59bc-8b5a-db9636c29f62 | note | Inspection: By - CR
b526b4c1-206e-4f12-9884-73bf700865ff | signoff | AUTHORITY HOLDPOINT
ff744b9f-c905-4283-847e-ce6947edf9b5 | checkpoint | 4.3 - Removal of Formwork - Penetration 3
887ed539-bb4f-5ee0-aa5b-327974690aea | note | Inspection Point: Quality Control Activity - Check and verify quality of casting both wet well side and Dry side
c085d689-1989-5e62-a9f9-6c30de97001f | note | Acceptance Criteria - Approval from Engineer
f7ec5165-5cbc-514f-b2f0-938c3bf17b03 | note | Verifying Document - Drawing M0003 and annotations
424af3f2-734b-5721-a712-857dc7a0d265 | note | Frequency - once
6628437f-3487-5b82-abeb-3bece3e164f5 | note | Inspection Type (Visual, other) - Document + Visual + Photograph + Engineer site Inspection
6e3b5c08-6cf3-5bbf-88ce-731af695c479 | note | Inspection: Key - H
b057500b-60f8-51fa-8e7f-ce393267b5e3 | note | Inspection: By - CR
b8e43e6d-9f5d-4384-bb1d-c3dbb1521a14 | signoff | AUTHORITY HOLDPOINT
104aaff7-4e81-4310-bf89-4718162073a7 | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
cf3a3214-1823-4c0f-b725-03dc72aeb464 | checkpoint | 5.1 - Clean tank of any Downer construction debris
b98ea6b2-cb7a-5eea-92fa-5b9680b6be1a | note | Inspection Point: Quality Control Activity - Upon removal of boxing and any remedial activities
4ada1e9a-9a4c-5bce-99cf-aecc8c1094e5 | note | Acceptance Criteria - Client Representative acceptance
5f48caee-6e20-59c1-87fe-9c9e844a4b17 | note | Verifying Document - NTC and or other written conformation
2acc671d-940e-5c5d-8fae-152a0a8452c9 | note | Frequency - once
c4421634-8691-5a3f-b840-b0a2df82a5c5 | note | Inspection Type (Visual, other) - Visual Inspection + Photograph
19195ceb-9546-5f78-8959-f716fab30a5c | note | Inspection: Key - H
d50ce20e-2a04-5b93-8167-795a1e60677f | note | Inspection: By - CR
d29e6a87-f5ad-4034-a5d7-4f1a9070e11d | signoff | AUTHORITY HOLDPOINT
b7f75978-2fd3-4215-86b6-e73e8a0bfb7e | checkpoint | 5.2 - Approval to fill Wet well
49c8b265-279c-5837-9b8a-021a862fc6ae | note | Inspection Point: Quality Control Activity - All activities and pre-checks required by client
f4f1b8f0-5849-5b06-af8e-a23c5ce96bb3 | note | Acceptance Criteria - Client Representative acceptance
f4216815-cb23-5beb-9b57-8b52951edb3b | note | Verifying Document - NTC and or other written conformation
88c15c67-3cf1-579e-b988-c0b3424b6dfa | note | Frequency - once
11fd71d4-2b13-5c8c-a2c8-c7b9330b4774 | note | Inspection Type (Visual, other) - Visual Inspection + Photograph
1c45a350-c4fe-5d14-9f0d-97d9dc90250a | note | Inspection: Key - C
ed334922-9caf-5771-8cf5-d8ba726de1a7 | note | Inspection: By - CR
3d8dfc7a-b3b3-46a1-8a94-e96081489568 | checklist | 561482-ITP-009.2 - Pre Commissioning Testing Pump & Valves - Pump 2 | itp | 561482-ITP-009.2 - Pre Commissioning Testing Pump & Valves - Pump 2
a1098b31-6510-491d-9684-4ad4edc650f6 | section | SECTION 3 – RECEIVING INSPECTIONS
d2a874cd-9e62-406c-8585-9e5f5599b2bf | checkpoint | 3.1 - Fill Wet Well
3ac5fcef-359f-53a3-8f95-b0183bc33a9c | note | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
1e2097af-ece9-521d-825c-b1d16c3419da | note | Acceptance Criteria - Completion of 561482- ITP-008
8a8965e0-a87d-5a62-b62e-b13b3455d0c5 | note | Verifying Document - This ITP
43176f61-e08f-51d7-8de5-68524bbdedc8 | note | Frequency - once
9e053bdd-25ce-5126-9e51-a84fca43be84 | note | Inspection Type (Visual, other) - Visual
91bbd7e0-2d59-5649-a0d6-4c027c53fb8a | note | Inspection: Key - Inspection
74b4a376-4a31-54d7-8c08-951e946fb256 | note | Inspection: By - IP
5040c1ef-6230-4865-aa06-37cfe0369223 | section | SECTION 4 – IN-PROCESS INSPECTIONS
9374e418-aa8d-4310-b9d7-7cff8027b3e0 | checkpoint | 4.1 - Filling of pipeline
2fe5bcb6-b04c-51a0-803d-f58a762176c5 | note | Inspection Point: Quality Control Activity - Remove Entrained air
abb4137f-cf2b-5947-bed4-a5f3ac247edb | note | Acceptance Criteria - Bleed until water visible
d11917f4-acd8-5176-8fa5-9ca6240a9217 | note | Verifying Document - None
6852009b-e2b4-52ec-b5cb-79cad68b5baf | note | Frequency - once
557f43a5-5c8a-5158-b901-fa0d87bcce6f | note | Inspection Type (Visual, other) - Visual
713a6a23-681d-5325-b76f-6d5d0433a10a | note | Inspection: Key - Inspection
b811d2c2-c72f-5344-af12-af61bf2ba4bc | note | Inspection: By - IP
05a6818a-db99-4742-b40c-11010c18d8c3 | checkpoint | 4.2 - Visual Check over of Pump 2 and motor
d7a7efb6-efda-55e4-8ce8-e9013726cde3 | note | Inspection Point: Quality Control Activity - Look for any visible leaking
f826f6c8-c50a-5eff-a1ee-fdcdea35a00a | note | Acceptance Criteria - All pipework connections tight All Cable & Terminations secure
3e40ef1a-c8b4-5d55-9ffb-1d126c246a9f | note | Verifying Document - This ITP
ccc3f76e-d099-5cb9-be48-3a46e643b352 | note | Frequency - once
521f7d55-8344-52bd-a81b-a46e92aae8df | note | Inspection Type (Visual, other) - Visual
6ccb898c-88e0-5030-8b47-b19afd69aaef | note | Inspection: Key - Inspection
af22993c-dbcf-5317-ae9a-e04758051d40 | note | Inspection: By - IP
c3deba62-7e30-4987-8d8d-bd7252c03d1f | checkpoint | 4.3 - Bump Start Pump 2
94144506-9038-590c-bdf1-a184ba7c5b67 | note | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
801c0dea-1518-57c9-8b77-518ff3a479e7 | note | Acceptance Criteria - Rotation direction is correct
510d0a52-2dec-5b9b-a135-a92c94feef7e | note | Verifying Document - Pump build sheet literature
7ff05f03-656b-5475-937b-5baba9fabcb1 | note | Frequency - once
f3cd18c6-61e2-5cfa-aa47-48e44bdc258e | note | Inspection Type (Visual, other) - Visual
806263e6-cb4a-5ca5-9558-daa29129d8c2 | note | Inspection: Key - Inspection
530ad8e8-6072-5d57-90c7-11b36e0ec053 | note | Inspection: By - IP
b527b231-5826-4105-9b9f-4b6dd5910a09 | checkpoint | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 2
824f59a9-67be-59c2-ba5b-e78976182f2c | note | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
bd29f52d-bc91-5a0c-aa3f-1226592687f1 | note | Acceptance Criteria - No visible leaking as per Item 4.2
462dde64-6712-5e0a-a67b-66f5ccb3aa5c | note | Verifying Document - To meet Specification requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure 30Bar)
afa04178-f971-5ac0-ae0d-33379e4b5758 | note | Frequency - once
6a6a99f7-4e99-51ad-83e6-78927d58ed40 | note | Inspection Type (Visual, other) - Visual
6ea0006f-4959-52c5-b8b9-84052a4ab992 | note | Inspection: Key - Inspection
3273caa0-93bc-51af-a03e-bb6a282f9c4d | note | Inspection: By - IP
fa9300a1-abd7-47a3-96f6-51dcb5b4b53b | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
ad72b869-2e80-4b56-914a-1e718baabf1d | checkpoint | 5.1 - Pump 2 rotation direction
e7dc7f2b-e1ea-5185-9383-141739e26899 | note | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
22b93a0f-d8eb-5a9c-aedd-69205e8f1fb6 | note | Acceptance Criteria - Pump rotation direction is correct and matched the technical information
548e4d32-baae-5817-80a0-e5dbb6c50bec | note | Verifying Document - This ITP
87433843-1c71-5933-839f-0984856daf1f | note | Frequency - Once
a1956f7a-a705-568f-b000-d17f7bad8426 | note | Inspection Type (Visual, other) - Record on ITP
d8127cc0-7a40-555c-a796-68aca1be59df | note | Inspection: Key - Inspection
393bd472-385f-5500-b0bd-88384ea145af | note | Inspection: By - IP
c9243a22-49d7-4625-bf3c-a1ae682a8d99 | checkpoint | 5.2 - Pump 2 pressure test pass
919175b7-390b-5269-a0d6-a3da8ce8b4b8 | note | Inspection Point: Quality Control Activity - Record Gauge pressure
95885160-b00e-50f2-802e-1620a8afad41 | note | Acceptance Criteria - Pass - no pressure loss or visible weaping
903ea7dc-1280-5f9c-b1db-c6a3d8960084 | note | Verifying Document - This ITP & Specified Pressure testing document
a7b20dab-57f9-5f54-96c5-c52355a0e660 | note | Frequency - Once
50b9a7c2-12b8-5df0-b7f8-f6a43a6d3550 | note | Inspection Type (Visual, other) - Visual / Photo
b9c15a9d-c45e-5d47-a3dd-35ebaad57ea6 | note | Inspection: Key - Inspection
9c38cb23-ecd7-596f-b3be-946ce35f5a3b | note | Inspection: By - IP
19536531-7646-4390-9028-d15e92b5ca70 | checklist | 561482-ITP-009.3 - Pre Commissioning Testing Pump & Valves - Pump 3 | itp | 561482-ITP-009.3 - Pre Commissioning Testing Pump & Valves - Pump 3
f5ee21e3-c380-489e-a375-c594369abc92 | section | SECTION 3 – RECEIVING INSPECTIONS
e17ed63b-ae10-43f1-83d2-684e8dac5623 | checkpoint | 3.1 - Fill Wet Well
a406d618-3b83-5173-82b7-3199c38966d2 | note | Inspection Point: Quality Control Activity - Pressure testing between suction and discharge isolation valves
4a7132ce-8c36-59ad-a9b3-adbbc4d21d93 | note | Acceptance Criteria - Completion of 561482- ITP-008
ce5262fa-f7a1-5d0c-9a2a-17c5fee017e2 | note | Verifying Document - This ITP
630ec3ab-abdc-54bc-91fd-c1fafe2fa544 | note | Frequency - once
efffccbe-3d19-5d0f-878a-5ba64b284e19 | note | Inspection Type (Visual, other) - Visual
5e8a6cd3-f8e9-5a8e-8e4a-e7373e27185f | note | Inspection: Key - Inspection
6b8ea53a-4422-5cd9-ab56-ef44efbff52e | note | Inspection: By - IP
bb596c2c-fd4d-442f-b6a9-25869e7e04ae | section | SECTION 4 – IN-PROCESS INSPECTIONS
b607cf96-1e75-4457-8a82-0325ff761db3 | checkpoint | 4.1 - Filling of pipeline
7d0a60ce-1f3a-5569-8378-e959cae1d905 | note | Inspection Point: Quality Control Activity - Remove Entrained air
efcb01c9-fac2-5311-92bc-54fc7606bfe7 | note | Acceptance Criteria - Bleed until water visible
930b733d-f40c-5634-a913-93fa0420563a | note | Verifying Document - None
e22d2024-1f19-577e-82d6-58d0c5c23e8a | note | Frequency - once
e60813d2-e120-584a-8772-512a81d7108b | note | Inspection Type (Visual, other) - Visual
40c08716-0dfe-5496-9528-8ece5cf5965f | note | Inspection: Key - Inspection
606b0e20-04f4-5a86-940f-b219c3716b6f | note | Inspection: By - IP
edead84b-52cf-4ea6-8194-31408fc151f6 | checkpoint | 4.2 - Visual Check over of Pump 3 and motor
96587daa-7dee-5405-bd4f-64c4afdbbfba | note | Inspection Point: Quality Control Activity - Look for any visible leaking
16404f5a-a379-5eb0-839f-5b176d1d8d8d | note | Acceptance Criteria - All pipework connections tight All Cable & Terminations secure
f71b6bea-b45c-5ec5-94a1-47a39881f8fd | note | Verifying Document - This ITP
b6e53a4f-ac2a-5006-88f9-4cd221ace649 | note | Frequency - once
9f7fbef1-a875-59f3-af82-ecea3adb4154 | note | Inspection Type (Visual, other) - Visual
11851e23-c3ba-58cd-8d58-9bf68fc05edf | note | Inspection: Key - Inspection
c4e70415-3eb8-50cf-8298-46d548480ddf | note | Inspection: By - IP
99a8e15f-03bb-4080-8790-268b5ffd13f0 | checkpoint | 4.3 - Bump Start Pump 3
796817c6-3b0f-53d5-b8bf-f616a3ffa544 | note | Inspection Point: Quality Control Activity - Check for correct pump rotation direction
fd9d2aca-4847-5c85-9d76-9215d3868e1b | note | Acceptance Criteria - Rotation direction is correct
2f6babda-658d-5cf2-8548-ea2321e111e1 | note | Verifying Document - Pump build sheet literature
28687dc4-beb9-503b-92d2-32317a346fce | note | Frequency - once
924f6a1f-12b2-518e-8a41-1ea32368f3a4 | note | Inspection Type (Visual, other) - Visual
818cb764-33fb-512c-9be2-274e3e462774 | note | Inspection: Key - Inspection
3cd0f972-7954-5855-8745-b22421b6ad18 | note | Inspection: By - IP
9cbb0aa4-b33b-4351-b6eb-adcacd92e9ed | checkpoint | 4.4 - Pressure testing between suction and diacharge isolation valves - Pump 3
c8f2632e-60be-5bbf-9769-f59299f17157 | note | Inspection Point: Quality Control Activity - VSD Energised, water in pump pipelines
be6672df-2dcf-5a74-8d2e-07dd9709d88d | note | Acceptance Criteria - No visible leaking as per Item 4.2
17123f11-5717-5f7a-bc36-d945a1d9b9a6 | note | Verifying Document - requirements and not to exceed pump manufacturers maximum pressure (Pump flanges 16Bar, Seal max pressure
bfdd3f3e-9046-5732-b17f-4a7f51737a90 | note | Frequency - once
55f22676-1eae-5894-ab64-2dab47bb245d | note | Inspection Type (Visual, other) - Visual
801c4350-3d7e-59ef-8871-82d131e74897 | note | Inspection: Key - Inspection
0a84125b-fef9-5b4e-b9ec-69d4e7964080 | note | Inspection: By - IP
0bc61717-8ce2-45e8-a932-a4e18290071d | section | SECTION 5 – FINAL INSPECTION AND HANDOVER
ea26b2fc-32ff-4e05-8717-37e2705b0265 | checkpoint | 5.1 - Pump 3 rotation direction
a62814a2-411e-5d47-b74f-908e396bc6ca | note | Inspection Point: Quality Control Activity - Pump rotation direction as per manufacturers technical information
894e701a-a406-5fdc-b18c-268a71ad34b5 | note | Acceptance Criteria - Pump rotation direction is correct and matched the technical information
e0764d9d-ec62-57bd-a05f-a9036e1d9d4a | note | Verifying Document - This ITP
45d1f1ff-b903-54bb-b313-bff15b18c6d3 | note | Frequency - Once
75b2d8f8-edd1-5504-9056-673b79e3c35a | note | Inspection Type (Visual, other) - Record on ITP
aebc42ab-6f77-568f-aceb-d1cc549ff231 | note | Inspection: Key - Inspection
3275f012-5e19-54f6-a427-1ff725e6adfe | note | Inspection: By - IP
74521f3b-d76a-40da-8e17-019be4ac41d4 | checkpoint | 5.2 - Pump 3 pressure test pass
3382e1f8-c4c4-59d4-9166-9bd6b7374d0a | note | Inspection Point: Quality Control Activity - Record Gauge pressure
5ec863dc-7e4f-579d-8b4b-436fc64d1241 | note | Acceptance Criteria - Pass - no pressure loss or visible weaping
ae198692-e00f-5747-96a7-1345988b49fa | note | Verifying Document - This ITP & Specified Pressure testing document
85980809-1907-567e-8e93-559f15468159 | note | Frequency - Once
70e438a0-314b-5a3a-9791-201c8bfbe6cc | note | Inspection Type (Visual, other) - Visual / Photo
1c7d7cda-188d-57ac-a5c2-3778c80e90aa | note | Inspection: Key - Inspection
6ad5284f-dbf1-5ca9-8fd5-d812cd88feda | note | Inspection: By - IP