## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 561482-ITP-010 - Commissioning | itp |  |  |  |  | 561482-ITP-010 - Commissioning
section | SECTION 3 – RECEIVING INSPECTIONS
checkpoint | 3.1 - Ensure installation complies with Electrical regulations and GHD specification (whichever more stringent)
label | Inspection Point: Quality Control Activity - Prior to livening up Electrical board
label | Acceptance Criteria - Installation in compliance with Electrical Regulations
label | Verifying Document - Electrical COC
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual, Metering
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 3.2 - Ensure the Mechanical Installation is installed in accordance with the Drawings & Specification
label | Inspection Point: Quality Control Activity - Prior to system testing & flushing
label | Acceptance Criteria - All items are as per specified and installed to best trade practice
label | Verifying Document - Completed ITP's
label | Frequency - Once per ITP
label | Inspection Type (Visual, other) - Visual, Metering
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 4 – IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Commissioning of switchboard
label | Inspection Point: Quality Control Activity - Switchboard modifications carried out, livened, subcircuits isolated
label | Acceptance Criteria - switchboard mounted controls operate as expected
label | Verifying Document - Switchboard ITR
label | Frequency - Once
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.2 - Commissioning of motors
label | Inspection Point: Quality Control Activity - motors installed and terminated
label | Acceptance Criteria - confirmation of correct wiring configuration.
label | Verifying Document - Specific motor ITR's
label | Frequency - once per motor
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.3 - Commissioning of VSD's
label | Inspection Point: Quality Control Activity - VSD's not energised
label | Acceptance Criteria - Power supply to VSDs correct as per supply/design
label | Verifying Document - electrical drawings for site.
label | Frequency - once per VSD
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.4 - Commissioning of VSD's
label | Inspection Point: Quality Control Activity - VSD's powered up, before test running.
label | Acceptance Criteria - VSD's set up correctly for motors connected.
label | Verifying Document - VSD ITR's
label | Frequency - once per VSD
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.5 - rotation test of motor
label | Inspection Point: Quality Control Activity - VSD's configured, set to run at low speed
label | Acceptance Criteria - Motor Rotates in correct direction
label | Verifying Document - Specific motor ITR's
label | Frequency - once per motor
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.6 - Verification of local motor controls
label | Inspection Point: Quality Control Activity - motor operation confirmed, water in system.
label | Acceptance Criteria - controls operate as expected, e-stops do not automatically reset upon release.
label | Verifying Document - Specific motor ITR's
label | Frequency - once
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.7 - Verification of PLC inputs
label | Inspection Point: Quality Control Activity - PLC Installed, outputs made to a safe state,
label | Acceptance Criteria - Verification of input and output operations. verification of analogue input operation
label | Verifying Document - Automation ITR
label | Frequency - once
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.8 - Commissioning of swing check valve microswitch
label | Inspection Point: Quality Control Activity - Check valves installed
label | Acceptance Criteria - Signals verified to PLC
label | Verifying Document - Automation ITR
label | Frequency - once
label | Inspection Type (Visual, other) - visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.9 - Re-commissioning of pressure transducers
label | Inspection Point: Quality Control Activity - Pressure transducers installed, no pressure on system
label | Acceptance Criteria - Pressure transducers read as expected, output to plc verified and range confirmed. Verified against external gauge.
label | Verifying Document - Automation ITR
label | Frequency - once per PIT
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.10 - Re-fill pumps with water
label | Inspection Point: Quality Control Activity - Open Valves slowly on suction & discharge side of pump
label | Acceptance Criteria - Bleed pumps and any high points in pipework
label | Verifying Document - This document
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.11 - Turn on pump 1 - Check for correct operation
label | Inspection Point: Quality Control Activity - Pressure transducers and flow meters installed, pressurised system
label | Acceptance Criteria - Correct operation of instrumentation (Flowmeter & pressure transducer)
label | Verifying Document - Automation ITR
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
checkpoint | 4.12 - Turn on pump 2 - Check for correct operation
label | Inspection Point: Quality Control Activity - Pressure transducers and flow meters installed, pressurised system
label | Acceptance Criteria - Correct operation of instrumentation (Flowmeter & pressure transducer)
label | Verifying Document - Automation ITR
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - IP
section | SECTION 5 – FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Water supply is un interrupted and purged of any air
label | Inspection Point: Quality Control Activity - Bleed of entrained air
label | Acceptance Criteria - Wet well is full
label | Verifying Document - This document
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - QE
checkpoint | 5.2 - Controls systems are operational and functioning as intended as per the Functional Description
label | Inspection Point: Quality Control Activity - Automation functionality verification
label | Acceptance Criteria - As per GHD design
label | Verifying Document - Commissioning plan
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - QE
checkpoint | 5.3 - Pumps are operating correctly and changeover as per the control strategy.
label | Inspection Point: Quality Control Activity - Automation functionality verification
label | Acceptance Criteria - As per GHD design
label | Verifying Document - Commissioning plan
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - QE
checkpoint | 5.4 - Pump flow is achieving the expected flow rate. Flow rate recorded and provided to Engineer
label | Inspection Point: Quality Control Activity - Correct setup of VSD
label | Acceptance Criteria - Flow rate matches design data
label | Verifying Document - Pump datasheet
label | Frequency - Once
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - I
label | Inspection: By - QE
checkpoint | 5.5 - System successfully communicating with DCC network
label | Inspection Point: Quality Control Activity - RTU communicating
label | Acceptance Criteria - Connectivity to client network
label | Verifying Document - Commissioning plan
label | Frequency - Once
label | Inspection Type (Visual, other) - Verification form Client
label | Inspection: Key - I
label | Inspection: By - QE, Client
checkpoint | 5.6 - DCC Water technicians attend for operation & handover. Client Instruction
label | Inspection Point: Quality Control Activity - Operator attendance
label | Acceptance Criteria - Acceptance by DCC Operations
label | Verifying Document - Commissioning plan
label | Frequency - Once
label | Inspection Type (Visual, other) - Verification form Client
label | Inspection: Key - A
label | Inspection: By - QE, Client
checkpoint | 5.7 - Operation & Maintenance Manual
label | Inspection Point: Quality Control Activity - Commissioning complete, system in operation
label | Acceptance Criteria - Installation complete, all technical data obtained
label | Verifying Document - Published Operation & Maintenance Manuals
label | Frequency - Once
label | Inspection Type (Visual, other) - Review of Documents
label | Inspection: Key - A
label | Inspection: By - QE
checkpoint | 5.8 - Mark Up drawings for As-Builts
label | Inspection Point: Quality Control Activity - Commissioning complete, system in operation
label | Acceptance Criteria - Installation completed
label | Verifying Document - Red-Line Mark up Drawings
label | Frequency - Once
label | Inspection Type (Visual, other) - Review of Documents
label | Inspection: Key - A
label | Inspection: By - QE