## Sheet1
| Current ITP |  | Updated ITP checklist
ITP title | Temp DB Checklist | ITP title | Temp DB Checklist
1 | Are all final circuits protected by an RCD | 1 | Have all old tags, labels and stickers been removed before use?
2 | Are all DB doors lockable | 2 | Has the DB be cleaned before use? (any rubbish, old materials or dirt removed)
3 | Are all DB’s securely fixed in position | 3 | Is the temp DB in good order and constructed of robust material capable of withstanding damage?
4 | Are all switchboards labelled correctly | 4 | Are socket outlets in DB in good working order, if no, replace or repair
5 | Are all final circuits labelled at board | 5 | Are all DB’s securely fixed in position except for free standing ones that take into account external forces
6 | Are all live parts at DB inaccessible | 6 | Are all DB doors lockable
7 | Are socket outlets in DB in good working order | 7 | Are all live parts at DB inaccessible
8 | Are empty glands and holes covered over | 8 | Access to DB is clear of materials
9 | Is switchboard door lockable, fitted with a retaining bar, and unable to be removed without the use of a tool | 9 | Are all final sub-circuits of construction wiring protected at the switchboard by an RCD with a maximum rated residual current of 30mA?
10 | Is emergency lighting provided adjacent to switchboard | 10 | Are all switchboards labelled correctly - label fixed to the switchboard stating ‘KEEP CLOSED – RUN ALL LEADS THROUGH BOTTOM’
11 | CCEW form been completed? (Take photo of each page) | 11 | Are all final circuits are labelled at board
|  | 12 | Are empty glands and holes covered over
|  | 13 | Exposed building wire at cable glands must be in enclosures, either push in and tighten or rewire if too short.
|  | 14 | Circuits > 100A per phase not individually switched. Separate circuits onto individual isolators.
|  | 15 | Correct circuit breakers on outgoing circuits
|  | 16 | RCD Load rating is sufficient
|  | 17 | The EVAC POD is istalled on a fixed wired final sub.
|  | 18 | Switchboard with socket has insulated tie off barr
|  | 19 | DB has a marked isolating switch which will isolate supply to all sub-circuits and sub-mains originating from the switchboard, including socket outlets on the switchboard?
|  | 20 | Is there emergency lighting adjacent to the switchboard
|  | 21 | Has RCD testing been completed and displayed on the Temp DB?
|  | 22 | CCEW form been completed? (Take photo of each page)