## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | Temp Board Install Checklist |  | Temp Board Install Checklist
| section | Details
| checkpoint | Have all old tags, labels and stickers been removed before use?
| checkpoint | Has the DB be cleaned before use? (any rubbish, old materials or dirt removed)
| checkpoint | Is the temp DB in good order and constructed of robust material capable of withstanding damage?
05309c44-8149-5888-afd2-61113b4d102d | checkpoint | Are socket outlets in DB in good working order, if no, replace or repair
1e1ba356-921f-51dd-a87a-3f7207656bdd | checkpoint | Are all DB’s securely fixed in position except for free standing ones that take into account external forces
549e8a9c-2777-565a-b341-b94e61e78b09 | checkpoint | Are all DB doors lockable
22c78e1a-6c83-5da5-b46b-a525ab1c333a | checkpoint | Are all live parts at DB inaccessible
| checkpoint | Access to DB is clear of materials
f8b572f6-7684-5c54-9309-5d3804bf7299 | checkpoint | Are all final sub-circuits of construction wiring protected at the switchboard by an RCD with a maximum rated residual current of 30mA?
151ad821-c758-563a-af74-4e0cfed14095 | checkpoint | Are all switchboards labelled correctly - label fixed to the switchboard stating ‘KEEP CLOSED – RUN ALL LEADS THROUGH BOTTOM’
3c958be7-32e3-5583-9c9b-cca8c36a79b0 | checkpoint | Are all final circuits are labelled at board
49254fbe-659b-523e-841c-e2efe94d407e | checkpoint | Are empty glands and holes covered over
| checkpoint | Exposed building wire at cable glands must be in enclosures, either push in and tighten or rewire if too short.
| checkpoint | Circuits > 100A per phase not individually switched. Separate circuits onto individual isolators.
| checkpoint | Correct circuit breakers on outgoing circuits
| checkpoint | RCD Load rating is sufficient
| checkpoint | The EVAC POD is istalled on a fixed wired final sub.
3d6e1103-af07-5279-9163-c8012240224d | checkpoint | Switchboard with socket has insulated tie off barr
| checkpoint | DB has a marked isolating switch which will isolate supply to all sub-circuits and sub-mains originating from the switchboard, including socket outlets on the switchboard?
2fb2de5c-de9a-5031-8097-38e36f3e6395 | checkpoint | Is there emergency lighting adjacent to the switchboard
| checkpoint | Has RCD testing been completed and displayed on the Temp DB?
3e48b3df-e204-550a-beff-3fbead59de3c | checkpoint | CCEW form been completed? (Take photo of each page)