## Sheet1
3.1 | Ensure installation complies with Electrical regulations and GHD specification (whichever more stringent) | Prior to livening up Electrical board | Installation in compliance with Electrical Regulations | Electrical COC | Once | Visual Metering | I | IP | 3.1 - Ensure installation complies with Electrical regulations and GHD specification (whichever more stringent) | Inspection Point: Quality Control Activity - Prior to livening up Electrical board | Acceptance Criteria - Installation in compliance with Electrical Regulations | Verifying Document - Electrical COC | Frequency - Once | Inspection Type (Visual, other) - Visual Metering | Inspection: Key - I | Inspection: By - IP | 3.1 - Ensure installation complies with Electrical regulations and GHD specification (whichever more stringent)
3.2 | Ensure the Mechanical Installation is installed in accordance with the Drawings CHAR(AMP) Specification | Prior to system testing CHAR(AMP) flushing | All items are as per specified and installed to best trade practice | Completed ITP's | Once per ITP | Visual Metering | I | IP | [8 empty] | Inspection Point: Quality Control Activity - Prior to livening up Electrical board
4.1 | commissioning of switchboard | Switchboard modifications carried out, livened, subcircuits isolated | switchboard mounted controls operate as expected | Switchboard ITR | Once | visual | I | IP | [8 empty] | Acceptance Criteria - Installation in compliance with Electrical Regulations
4.2 | commissioning of motors | motors installed and terminated | confirmation of correct wiring configuration. | Specific motor ITR's | once per motor | visual | I | IP | [8 empty] | Verifying Document - Electrical COC
4.3 | commissioning of VSD's | VSD's not energised | Power supply to VSDs correct as per supply/design | electrical drawings for site. | once per VSD | visual | I | IP | [8 empty] | Frequency - Once
4.4 |  | VSD's powered up, before test running. | VSD's set up correctly for motors connected. | VSD ITR's | once per VSD | visual | I | IP | [8 empty] | Inspection Type (Visual, other) - Visual Metering
4.5 | rotation test of motor | VSD's configured, set to run at low speed | Motor Rotates in correct direction | Specific motor ITR's | once per motor | visual | I | IP | [8 empty] | Inspection: Key - I
4.6 | Verification of local motor controls | motor operation confirmed, water in system. | controls operate as expected, e-stops do not automatically reset upon release. | Specific motor ITR's | once | visual | I | IP | [8 empty] | Inspection: By - IP
4.7 | Verification of PLC inputs | PLC Installed, outputs made to a safe state, | Verification of input and output operations. verification of analogue input operation | Automation ITR | once | visual | I | IP
4.8 | commissioning of swing check valve microswitch | Check valves installed | Signals verified to PLC | Automation ITR | once | visual | I | IP
4.9 | Re-commissioning of pressure transducers | Pressure transducers installed, no pressure on system | Pressure transducers read as expected, output to plc verified and range confirmed. Verified against external gauge. | Automation ITR | once per PIT | Visual | I | IP
4.1 | Re-fill pumps with water | Open Valves slowly on suction CHAR(AMP) discharge side of pump | Bleed pumps and any high points in pipework | This document | Once | Visual | I | IP
4.11 | Turn on pump 1 - Check for correct operation | Pressure transducers and flow meters installed, pressurised system | Correct operation of instrumentation (Flowmeter CHAR(AMP) pressure transducer) | Automation ITR | Once | Visual | I | IP
4.12 | Turn on pump 2 - Check for correct operation | Pressure transducers and flow meters installed, pressurised system | Correct operation of instrumentation (Flowmeter CHAR(AMP) pressure transducer) | Automation ITR | Once | Visual | I | IP
5.1 | Water supply is un interrupted and purged of any air | Bleed of entrained air | Wet well is full | This document | Once | Visual | I | QE
5.2 | Controls systems are operational and functioning as intended as per the Functional Description | Automation functionality verification | As per GHD design | Commissioning plan | Once | Visual | I | QE
5.3 | Pumps are operating correctly and changeover as per the control strategy. | Automation functionality verification | As per GHD design | Commissioning plan | Once | Visual | I | QE
5.4 | Pump flow is achieving the expected flow rate. Flow rate recorded and provided to Engineer | Correct setup of VSD | Flow rate matches design data | Pump datasheet | Once | Visual | I | QE
5.5 | System successfully communicating with DCC network | RTU communicating | Connectivity to client network | Commissioning plan | Once | Verification form Client | I | QE Client
5.6 | DCC Water technicians attend for operation CHAR(AMP) handover. Client Instruction | Operator attendance | Acceptance by DCC Operations | Commissioning plan | Once | Verification form Client | A | QE Client
5.7 | Operation CHAR(AMP) Maintenance Manual | Commissioning complete, system in operation | Installation complete, all technical data obtained | Published Operation CHAR(AMP) Maintenance Manuals | Once | Review of Documents | A | QE
5.8 | Mark Up drawings for As-Builts | Commissioning complete, system in operation | Installation completed | Red-Line Mark up Drawings | Once | Review of Documents | A | QE