## Table 1
Abbreviations
Third Party |  | TP |  |  | RSA Contractors |  | RSA | Nominated Project Personnel |  |  |  |  | NPP | Principle Contractor |  |  |  | PC
Surveyor |  | SUR |  |  | RPEQ |  | RPEQ | Supervisor |  |  |  |  | SUP | Inspect |  |  |  | INS
Test |  | TST |  |  | Project Engineer |  | PE | Witness Point |  |  |  |  | WP | Hold Point |  |  |  | HP
Visual |  | VIS |  |  | Check |  | CHK | Written |  |  |  |  | WRI | Monitor |  |  |  | M
Milestone |  | MST |  |  | Review |  | R
Inspection and Test Plan Details | [13 empty] | Contractor |  |  |  | Client
Item | Inspection Activity |  | Work By |  | Standard / Spec |  | Criteria |  |  |  | Frequency |  | Record | Resp |  | Type | Signoff | Resp | Type | Signoff
1 | Lot Identification |  | Contractor |  | Technical Specification |  | Location of Works identified in accordance with project technical specification |  |  |  | 1/Lot |  | ITP Verification Checklist/Lot Map | RSA |  | CHK |  | ACC | CHK
2 | Underlying Lot Conforms |  | Contractor |  | Technical Specification |  | Foundation preparation works are cleared, proof rolled, no soft spots or organics. |  |  |  | 1/Lot |  | ITP Verification Checklist/Lot Map | RSA |  | CHK |  | ACC | CHK
3 | Fill placement |  | Contractor |  | Technical Specification |  | General Fill Placed in continuous, approximately horizontal layers for the full width of the area, having a compacted thickness of not more than 300 mm or less than 75 mm. If the surface of any layer is smooth, it must be scarified to a depth of approximately 30 to 50 mm prior to the placement of the next layer. ≥ 96 % standard MDD. -2% to +2% of OMC |  |  |  | Each Lot |  | ITP Verification Checklist/Lot Map | RSA |  | WP |  | ACC | WP
4 | Survey |  | Contractor |  | Technical Specification |  | RSA shall submit 25%, 50%, 100% tank pad foundation fill placement completion. |  |  |  | 1/Lot |  | Survey | RSA |  | HP |  | ACC | HP
Test Details | [6 empty] | Normal Testing Level | [7 empty] | Required Result(s)
Item | Test |  |  | Description |  |  | Max Lot Size |  | Min Test Frequency |  |  | Min No of tests |  |  | Criteria
1 | AS 1289 5.7.1 |  |  | Hilf Dry density ratio, Moisture Content | [7 empty] |  20 |  |  | -2% dry to +2% wet OMC DDR 96%
2 | AS1289 |  |  |  PSD  Atterberg Limits  Emerson | [7 empty] |  5  5  5
Contractor Construction Manager:
[6 empty] | (Print Name) |  |  |  | (Signature) | [5 empty] | (Date)
Client Superintendent:
[6 empty] | (Print Name) |  |  |  | (Signature) | [5 empty] | (Date)
Document Status
Revision Status |  | Responsible Person |  |  | Signed |  | Dated | Revision
Draft By: |  | Madhu Achana
Reviewed By:
Submitted By:
Approved By: