## Sheet 1
|  |  |  | Project: | Salford Street Watermain Renewal |  |  | Lot Number
|  |  |  | Project Location | Salford, Moana, Wilton, Waihopai Streets |  |  | Scope Of ITP
|  |  |  | Job # 549262 | Contract CC1842 |  |  | Sub Contractor |  | SM Civil
Inspection & Test Plan / Checklist
|  |  |  | Signatory |  | Role |  | Person(s) Responsible
|  |  |  | Requiring FH Signature |  | Site Engineer |  | Brendon Ferguson
| Action | H | Hold Point for Engineers Representative | Requiring FH Manager Representative |  | FH Job Manager |  | Joe Findley
|  | W | Witness for Engineers Representative | Requiring Engineers Representative |  | Engineers Representative |  | Nick Watt
|  | H | Hold Point internal |  |  | Contractors Foreman |  | Johnny McCarthy (SM Civil)
|  | M | Monitor |  |  | Environmental Advisor |  | Ciccone Tweedie
[6 empty] | STMS |  | FH STMS
No: | Inspection / Test Point | ACTION (W, M, H) | Conformance Criteria (What's Required) | Detail | Frequency | Inspection / Test Method | Verification Records | Standard | Signatory | Date(s) | Signature
1.0 Pre-construction
1.0 General
D1.5 | Pre-work site inspection/Existing asset assessment | H | Carry out inspection and video existing assets and condition throughout work areas. | Existing asset assessment completed | Pre-Construction | Inspection | Copy on file |  | Engineers Representative
2.0 Project Plans
D1.19 | Contract Programme | H | The Contractor shall submit to the Engineer an appropriately detailed programme for approval. |  |  | Submission | Approved Contract Programme |  | Engineers Representative
D1.3 | Site Management plan | H | Engineer to accept the CMP prior to any work commencing on site | CMP including safety, quality and environmental plans submitted for approval | Prior to any work commencing on site | Submission | NTC |  | Engineers Representative
C1.7 | Traffic management Plan | H | Approved by road controlling authority | Traffic Management Plan to be approved Pre-construction | Pre-Construction |  | TMP on file |  | Engineers Representative
D1.6 | Heritage Authority induction | H | Heritage induction to be completed | All personnel who are undertaking work are required to be present at archaeological induction | Pre-Construction
D1.3.3 | Inspection Test plans | H | Approved by the Engineer | The ITP is a Contractor-generated document that outlines the specific inspection and testing requirements used by the Engineer’s Representative to monitor the Contractor’s quality. | Pre-Construction |  | NTC,Copy on file |  | Engineers Representative
D1.11 | Residents notification | H | Enginer approved letter distributed 48hrs prior to construction commencing. | Residents notifications completed |  |  | Letter on file |  | Engineers Representative
D1.7 | Customer and Stakeholder Communication Management Plan | H | Engineer to accept Customer and Stakeholder Communication Management Plan |  |  | Submission | Approved CMP |  | Engineers Representative
3.0 Service Location/Potholing
D1.8 | Service Plans | H | All Service Plans onsite and understood by all | Apply for BeforeUDig, contact anyone not on BeforeUDig | Pre-Construction | Witness | Plans Onsite & Signed ITP |  | Site Engineer
D1.8 | Service Location Investigation Completed | H | Complete the service locate with the authorised people | Inform Engineer about any significant clash | Pre-Construction | Witness | Plans Onsite & Signed ITP |  | Engineers Representative
2.0 Pre Commencement checks
4.0 Material checks
D1.29.3 | AP 65 Tests | H | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | one initially | Testing | Test result | NZS 4407:1991 | Engineers Representative
D1.29.3 | AP 65 Tests | H | In accordance with NZS 4407 | AP65 Subbase MDD | one initially | Testing | Test result | NZS 4407:1991 | Engineers Representative
D1.29.4 | AP 40 Tests | H | In accordance with NZS 4407 | AP40 Basecourse particle size and sand equivalent | one initially | Testing | Test result | NZS 4407:1991 | Engineers Representative
D1.29.4 | AP 40 Tests | H | In accordance with NZS 4407 | AP40 Basecourse MDD | one initially | Testing | Test result | NZS 4407:1991 | Engineers Representative
D2.5.3 | Butt Weld joint | H | Butt weld samples to be tested by independant laboratory | Should meet the requiremnts of AS/NZS 2033, the PIPA guidelines and the manufacturer's specifications. | 1 test weld from first 100m and 1 from last 100m and 1 weld test for every 50 weld | Testing | Test result |  | Engineers Representative
3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm)
| Link in at intersection of Layard Street and Salford Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail A in sheet 15 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x6) | As per detail A in sheet 15 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D5.4.2 | Isolation Valve SALFORD LAYARD VALVE CH16 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#107 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#108 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#111 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#112 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#115 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#116 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#117 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant SALFORDFH1 at CH 90 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#121 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#125 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of High Street and Salford Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail B in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail B in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D5.4.2 | Isolation Valve SALFORD HIGH VALVE CH127 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#127 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#131 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#133 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#132 Salford Street needs confirmation | H | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | CONFIRMATION REQUIRED | Photos | AS/NZS 4129 | Engineers Representative
D5.5 | Fire Hydrant SALFORDFH2 at CH 175 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#137 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#141 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#143 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Terrace Street and Salford Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail B in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail B in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#147 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve SALFORD TERRACE VALVE CH237 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#151 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#202 Terrace Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house on Salford Street needs confirmation between 202 Terrace Street and 154 Salford Steet | H | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | CONFIRMATION REQUIRED | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#153 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#154 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#157 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house on Salford Street needs confirmation between 154 and 156 Salford Steet | H | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | CONFIRMATION REQUIRED | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#156 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant SALFORDFH3 at CH293 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#161 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house on Salford Street needs confirmation between 156 and 162 Salford Steet | H | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | CONFIRMATION REQUIRED | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#162 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Lamond Street East and Salford Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail C in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail C in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
| Link in at intersection of Cruickshank Crescent and Salford Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail B in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail B in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D2.7 | Trenching and excavation | M | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | Daily | Inspection | RCP and digging checklist | NZS 4407 | Site Engineer
D2.9.1 | Pressure testing & disinfection | H | AS/NZS 2566:2 Section 6.3 | pressure testing of the new PE main | Prior to link in | Testing | Test records | AS/NZS 2566:2 Section 6.3 | Engineers Representative
|  | H | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Disinfection of the new PE main | Prior to link in | Testing | Test records | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Engineers Representative
D1.3.3 | Engineer's inspections | H | Inspection report | Enginer's inspection for pipe, concrete pre pour, pre sealing | As required | Inspection | Email |  | Engineers Representative
C1.18 | Surface Reinstatement | H | Engineer's Approval | Mark out the trench including overcuts | Prior to surfacing | Inspection | Email |  | Engineers Representative
|  | H | NDM testing | Provide NDM test results for AP65 and AP40 layers | Prior to surfacing | Testing | Test records |  | Engineers Representative
4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm)
D5.4.2 | Isolation Valve CRUICKSHANK VALVE CH358 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#178 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant SALFORDFH4 at CH397 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#182 Salford Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#192 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#188 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#8 Sommerset Lane | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#185 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house on Sommerset Lane needs confirmation at #8 | H | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | CONFIRMATION REQUIRED | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#1 Sommerset Lane | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant MOANAFH1 at CH512 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#183 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#177 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#171 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#176 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#165 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#174 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house on Moana Street needs confirmation at #172 | H | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | CONFIRMATION REQUIRED | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#170 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#163 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#162 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#159 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#158 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#154 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant MOANAFH2 at CH647 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#150 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#151 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house on Moana Street needs confirmation at #151 - potential duplicate | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#145 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#146 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#141 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#142 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#138 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant MOANAFH3 at CH725 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D5.4.2 | Isolation Valve MOANA-WILTON CH748 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
| Link in at intersection of Moana Street and Wilton Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail D in sheet 15 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x3) | As per detail D in sheet 15 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D2.7 | Trenching and excavation | M | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | Daily | Inspection | RCP and digging checklist | NZS 4407 | Site Engineer
D2.9.1 | Pressure testing & disinfection | H | AS/NZS 2566:2 Section 6.3 | pressure testing of the new PE main | Prior to link in | Testing | Test records | AS/NZS 2566:2 Section 6.3 | Engineers Representative
|  | H | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Disinfection of the new PE main | Prior to link in | Testing | Test records | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Engineers Representative
D1.3.3 | Engineer's inspections | H | Inspection report | Enginer's inspection for pipe, concrete pre pour, pre sealing | As required | Inspection | Email |  | Engineers Representative
C1.18 | Surface Reinstatement | H | Engineer's Approval | Mark out the trench including overcuts | Prior to surfacing | Inspection | Email |  | Engineers Representative
|  | H | NDM testing | Provide NDM test results for AP65 and AP40 layers | Prior to surfacing | Testing | Test records |  | Engineers Representative
5.0 Wilton Street - Layard Street to Moana Street (DN125mm)
| Link in at intersection of Layard and Wilton Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail M in sheet 15 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail M in sheet 15 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D5.4.2 | Isolation Valve WILTON-LAYARD CH14 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#126 Layard Street needs confirmation | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#125 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#131 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#128 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WILTON FH01 at CH83 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#37 High Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#41 High Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Wilton Street and High Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail E in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x1) | As per detail E in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
| Removal of existing cross and reinstated with straight through pipe at SW corner of Wilton Street and High Street | W | Pipe reinstated through old line and thrust protected | As per typical details sheet 18 |  | Inspection | Photos | AS/NZS 4130 | Site Engineer
D5.4.2 | Isolation Valve WILTON-HIGH CH125 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#40 High Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#143 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#147 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WILTON FH02 at CH179 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#150 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#149 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Wilton Street andTerrace Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail F in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x1) | As per detail F in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
| Removal of existing tees (2) and reinstated with straight through pipe and associated bends/thrust protection at SW corner of Wilton Street and High Street | W | Pipe reinstated through old line and thrust protected | As per detail L in sheet 16 and typical details sheet 18 | per connection | Inspection | Photos | AS/NZS 4130 | Site Engineer
D5.4.2 | Isolation Valve WILTON-TERRACE CH235 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#159 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#162 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#166 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#165 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WILTON FH03 at CH294 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#167 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#170 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#175 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Wilton Street and Lamond Street West | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail G in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail G in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D5.4.2 | Isolation Valve LAMOND-WILTON | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#177 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve WILTON-LAMOND CH347 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#180 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#181 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#184 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WILTON FH04 at CH387 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#185 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#188 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#189 Wilton Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#133 Moana Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D2.7 | Trenching and excavation | M | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | Daily | Inspection | RCP and digging checklist | NZS 4407 | Site Engineer
D2.9.1 | Pressure testing & disinfection | H | AS/NZS 2566:2 Section 6.3 | pressure testing of the new PE main | Prior to link in | Testing | Test records | AS/NZS 2566:2 Section 6.3 | Engineers Representative
|  | H | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Disinfection of the new PE main | Prior to link in | Testing | Test records | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Engineers Representative
D1.3.3 | Engineer's inspections | H | Inspection report | Enginer's inspection for pipe, concrete pre pour, pre sealing | As required | Inspection | Email |  | Engineers Representative
C1.18 | Surface Reinstatement | H | Engineer's Approval | Mark out the trench including overcuts | Prior to surfacing | Inspection | Email |  | Engineers Representative
|  | H | NDM testing | Provide NDM test results for AP65 and AP40 layers | Prior to surfacing | Testing | Test records |  | Engineers Representative
6.0 Waihopai Street - Layard Street to Moana Street (DN180mm)
| Link in at intersection of Layard and Waihopai Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail H in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail H in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
| Removal of existing teeand bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Layard and Waihopai Streets | W | Pipe reinstated through old line and thrust protected | As per detail L in sheet 16 and typical details sheet 18 | per connection | Inspection | Photos | AS/NZS 4130 | Site Engineer
D5.4.2 | Isolation Valve WAIHOPAI-LAYARD CH15 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#90 Layard Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#92 Layard Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#4 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#7 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#8 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#18 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WAIHOPAI FH01 at CH90 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
| Link in at intersection of Waihopai Street and High Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail I in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail I in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#11 Waihopai Street needs confirmation | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Engineers Representative
D8.3 D8.4 | Lateral connection to house no#22 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve WAIHOPAI-HIGH CH126 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#26 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#25 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#29 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WAIHOPAI FH02 at CH178 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#30 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#38 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#33 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Waihopai and Terrace Streets | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail J in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail J in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
| Capping of existing tees to blank abandoned ends. Intersection of Waihopai and Terrace Streets | W | Tee ends blanked and thrust protected | As per typical details in sheet 18 | per connection | Inspection | Photos | AS/NZS 4130 | Site Engineer
D5.4.2 | Isolation Valve WAIHOPAI-TERRACE CH238 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#42 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#46 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#52 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WAIHOPAI FH03 at CH285 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#53 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#54 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#58 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
| Link in at intersection of Waihopai Street and Lamond Street West | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail I in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail I in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#60 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve WAIHOPAI-LAMOND CH347 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
D8.3 D8.4 | Lateral connection to house no#62 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#64 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#71 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#66 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#70 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.5 | Fire Hydrant WAIHOPAI FH04 at CH393 | W | Hydrant outlet is between 200mm & 400mm from the finished ground level | The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
|  | W | Paint marking, RRPM and Hydrant marker | Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11 | Per each hydrant | Inspection | Photos | NZS 4522 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#75 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#74 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D8.3 D8.4 | Lateral connection to house no#78 Waihopai Street | W | The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep. | As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4 | Per each connection | Inspection | Photos | AS/NZS 4129 | Site Engineer
D5.4.2 | Isolation Valve WAIHOPAI-MOANA CH438 | W | Spindle height to be max 600mm from surface | The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9 | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Thrust wall installed | Thrust wall constructed as per fig.W9 of page 17 of the drawings | Per each valve | Inspection | Photos |  | Site Engineer
|  | W | Surface box finish | cast iron valve box to be flush with the finished surface level. | Per each valve | Inspection | Photos |  | Site Engineer
| Link in at intersection of Waihopai Street and Moana Street | W | Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling. | PE to DI connection to be done as per the detail K in sheet 16 of the drawing | Before backfilling | Inspection | Photos |  | Site Engineer
|  | W | Thrust protection to be constructed (x2) | As per detail K in sheet 16 and typical details as per sheet 18 | Before backfilling | Inspection | Photos |  | Site Engineer
| Removal of existing tee and bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Waihopai Street and Moana Street | W | Pipe reinstated through old line and thrust protected | As per detail L in sheet 16 and typical details sheet 18 | per connection | Inspection | Photos | AS/NZS 4130 | Site Engineer
D2.7 | Trenching and excavation | M | In accordance with NZS 4407 | AP65 Subbase particle size and sand equivalent | Daily | Inspection | RCP and digging checklist | NZS 4407 | Site Engineer
D2.9.1 | Pressure testing & disinfection | H | AS/NZS 2566:2 Section 6.3 | pressure testing of the new PE main | Prior to link in | Testing | Test records | AS/NZS 2566:2 Section 6.3 | Engineers Representative
|  | H | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Disinfection of the new PE main | Prior to link in | Testing | Test records | NZS 4404:2004 Appendix C AS/NZS 2566:2 Section 7 | Engineers Representative
D1.3.3 | Engineer's inspections | H | Inspection report | Enginer's inspection for pipe, concrete pre pour, pre sealing | As required | Inspection | Email |  | Engineers Representative
C1.18 | Surface Reinstatement | H | Engineer's Approval | Mark out the trench including overcuts | Prior to surfacing | Inspection | Email |  | Engineers Representative
|  | H | NDM testing | Provide NDM test results for AP65 and AP40 layers | Prior to surfacing | Testing | Test records |  | Engineers Representative
7.0 Close out documentation
C1.13 | As-built | H | Ensure as-built data recorded and submitted | Red pen markup drawing | Prior to PCC application | Submission | Asbuilt plans |  | Engineers Representative
| PS3 submission | H | Producer statement for construction to be supplied to client | As per schedule 6 3910:2013 | Prior to PCC application | Submission | Email of notice |  | Engineers Representative
| WCN and CAR close out | H | To be submitted at completion of works | Submission to ICC of completion of works in road corridor and close out of CAR | Prior to PCC application | Submission | PS3 document |  | Engineers Representative
| QA documents submitted | H | All required documents submitted throughout and at conclusion of project | All connection sheets, weld logs, NDM results, destructive testing weld reports, encountered services sheets, construction photographs, any outstanding H&S or non conformance reporting | Prior to PCC application | Submission | Various |  | Engineers Representative
Comments:
Accepted By :_____________________________________________ |  |  | Sub-contractor | Accepted By :_____________________________________________ |  | Project Manager |  | Accepted By :_____________________________________________ |  |  |  | Quality Manager
Signature:_____________________________ |  |  |  | Signature:________________________________________________ |  |  |  | Signature:________________________________________________