## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | 1.0 Pre-construction / 2.0 Pre Commencement checks | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 1.0 Pre-construction / 2.0 Pre Commencement checks
section | 1.0 Pre-construction - 1.0 General
checkpoint | D1.5 - Pre-work site inspection/Existing asset assessment
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Carry out inspection and video existing assets and condition throughout work areas.
label | Detail - Existing asset assessment completed
label | Frequency - Pre-Construction
label | Inspection / Test Method - Inspection
label | Verification Records - Copy on file
label | Signatory - Engineers Representative
section | 1.0 Pre-construction - 2.0 Project Plans
checkpoint | D1.19 - Contract Programme
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The Contractor shall submit to the Engineer an appropriately detailed programme for approval.
label | Inspection / Test Method - Submission
label | Verification Records - Approved Contract Programme
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3 - Site Management plan
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer to accept the CMP prior to any work commencing on site
label | Detail - CMP including safety, quality and environmental plans submitted for approval
label | Frequency - Prior to any work commencing on site
label | Inspection / Test Method - Submission
label | Verification Records - NTC
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.7 - Traffic management Plan
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Approved by road controlling authority
label | Detail - Traffic Management Plan to be approved Pre-construction
label | Frequency - Pre-Construction
label | Verification Records - TMP on file
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.6 - Heritage Authority induction
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Heritage induction to be completed
label | Detail - All personnel who are undertaking work are required to be present at archaeological induction
label | Frequency - Pre-Construction
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Inspection Test plans
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Approved by the Engineer
label | Detail - The ITP is a Contractor-generated document that outlines the specific inspection and testing requirements used by the Engineer’s Representative to monitor the Contractor’s quality.
label | Frequency - Pre-Construction
label | Verification Records - NTC,Copy on file
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.11 - Residents notification
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Enginer approved letter distributed 48hrs prior to construction commencing.
label | Detail - Residents notifications completed
label | Verification Records - Letter on file
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.7 - Customer and Stakeholder Communication Management Plan
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer to accept Customer and Stakeholder Communication Management Plan
label | Inspection / Test Method - Submission
label | Verification Records - Approved CMP
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
section | 1.0 Pre-construction - 3.0 Service Location/Potholing
checkpoint | D1.8 - Service Plans
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - All Service Plans onsite and understood by all
label | Detail - Apply for BeforeUDig, contact anyone not on BeforeUDig
label | Frequency - Pre-Construction
label | Inspection / Test Method - Witness
label | Verification Records - Plans Onsite & Signed ITP
label | Signatory - Site Engineer
checkpoint | D1.8 - Service Location Investigation Completed
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Complete the service locate with the authorised people
label | Detail - Inform Engineer about any significant clash
label | Frequency - Pre-Construction
label | Inspection / Test Method - Witness
label | Verification Records - Plans Onsite & Signed ITP
label | Signatory - Engineers Representative
section | 2.0 Pre Commencement checks - 4.0 Material checks
checkpoint | D1.29.3 - AP 65 Tests
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - one initially
label | Inspection / Test Method - Testing
label | Verification Records - Test result
label | Standard - NZS 4407:1991
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.29.3 - AP 65 Tests
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase MDD
label | Frequency - one initially
label | Inspection / Test Method - Testing
label | Verification Records - Test result
label | Standard - NZS 4407:1991
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.29.4 - AP 40 Tests
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP40 Basecourse particle size and sand equivalent
label | Frequency - one initially
label | Inspection / Test Method - Testing
label | Verification Records - Test result
label | Standard - NZS 4407:1991
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.29.4 - AP 40 Tests
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP40 Basecourse MDD
label | Frequency - one initially
label | Inspection / Test Method - Testing
label | Verification Records - Test result
label | Standard - NZS 4407:1991
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.5.3 - Butt Weld joint
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Butt weld samples to be tested by independant laboratory
label | Detail - Should meet the requiremnts of AS/NZS 2033, the PIPA guidelines and the manufacturer's specifications.
label | Frequency - 1 test weld from first 100m and 1 from last 100m and 1 weld test for every 50 weld
label | Inspection / Test Method - Testing
label | Verification Records - Test result
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checklist | 3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm) | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm)
section | 3.0 Salford Street - Layard Street to Cruickshank Crescent (DN180mm)
checkpoint | Link in at intersection of Layard Street and Salford Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail A in sheet 15 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Layard Street and Salford Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x6)
label | Detail - As per detail A in sheet 15 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD LAYARD VALVE CH16 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD LAYARD VALVE CH16 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD LAYARD VALVE CH16 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#107 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#108 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#111 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#112 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#115 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#116 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#117 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH1 at CH 90 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH1 at CH 90 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH1 at CH 90 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#121 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#125 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of High Street and Salford Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail B in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of High Street and Salford Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail B in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD HIGH VALVE CH127 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD HIGH VALVE CH127 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD HIGH VALVE CH127 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#127 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#131 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#133 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#132 Salford Street needs confirmation
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - CONFIRMATION REQUIRED
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D5.5 - Fire Hydrant SALFORDFH2 at CH 175 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH2 at CH 175 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH2 at CH 175 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#137 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#141 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#143 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Terrace Street and Salford Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail B in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Terrace Street and Salford Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail B in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#147 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD TERRACE VALVE CH237 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD TERRACE VALVE CH237 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve SALFORD TERRACE VALVE CH237 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#151 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#202 Terrace Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house on Salford Street needs confirmation between 202 Terrace Street and 154 Salford Steet
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - CONFIRMATION REQUIRED
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#153 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#154 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#157 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house on Salford Street needs confirmation between 154 and 156 Salford Steet
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - CONFIRMATION REQUIRED
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#156 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH3 at CH293 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH3 at CH293 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH3 at CH293 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#161 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house on Salford Street needs confirmation between 156 and 162 Salford Steet
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - CONFIRMATION REQUIRED
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#162 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Lamond Street East and Salford Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail C in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Lamond Street East and Salford Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail C in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Cruickshank Crescent and Salford Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail B in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Cruickshank Crescent and Salford Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail B in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D2.7 - Trenching and excavation
label | ACTION (W, M, H) - M
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - Daily
label | Inspection / Test Method - Inspection
label | Verification Records - RCP and digging checklist
label | Standard - NZS 4407
label | Signatory - Site Engineer
checkpoint | D2.9.1 - Pressure testing & disinfection (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
label | Detail - pressure testing of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - AS/NZS 2566:2 Section 6.3
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.9.1 - Pressure testing & disinfection (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Detail - Disinfection of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Engineer's inspections
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Inspection report
label | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
label | Frequency - As required
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer's Approval
label | Detail - Mark out the trench including overcuts
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NDM testing
label | Detail - Provide NDM test results for AP65 and AP40 layers
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checklist | 4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm) | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm)
section | 4.0 Salford Street and Moana Street - Cruickshank Crescent to Wilton Street (DN180mm)
checkpoint | D5.4.2 - Isolation Valve CRUICKSHANK VALVE CH358 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve CRUICKSHANK VALVE CH358 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve CRUICKSHANK VALVE CH358 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#178 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH4 at CH397 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH4 at CH397 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant SALFORDFH4 at CH397 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#182 Salford Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#192 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#188 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#8 Sommerset Lane
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#185 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house on Sommerset Lane needs confirmation at #8
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - CONFIRMATION REQUIRED
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#1 Sommerset Lane
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH1 at CH512 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH1 at CH512 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH1 at CH512 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#183 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#177 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#171 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#176 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#165 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#174 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house on Moana Street needs confirmation at #172
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - CONFIRMATION REQUIRED
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#170 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#163 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#162 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#159 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#158 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#154 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH2 at CH647 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH2 at CH647 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH2 at CH647 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#150 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#151 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house on Moana Street needs confirmation at #151 - potential duplicate
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#145 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#146 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#141 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#142 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#138 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH3 at CH725 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH3 at CH725 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant MOANAFH3 at CH725 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON CH748 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON CH748 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve MOANA-WILTON CH748 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Moana Street and Wilton Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail D in sheet 15 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Moana Street and Wilton Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x3)
label | Detail - As per detail D in sheet 15 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D2.7 - Trenching and excavation
label | ACTION (W, M, H) - M
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - Daily
label | Inspection / Test Method - Inspection
label | Verification Records - RCP and digging checklist
label | Standard - NZS 4407
label | Signatory - Site Engineer
checkpoint | D2.9.1 - Pressure testing & disinfection (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
label | Detail - pressure testing of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - AS/NZS 2566:2 Section 6.3
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.9.1 - Pressure testing & disinfection (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Detail - Disinfection of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Engineer's inspections
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Inspection report
label | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
label | Frequency - As required
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer's Approval
label | Detail - Mark out the trench including overcuts
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NDM testing
label | Detail - Provide NDM test results for AP65 and AP40 layers
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checklist | 5.0 Wilton Street - Layard Street to Moana Street (DN125mm) | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 5.0 Wilton Street - Layard Street to Moana Street (DN125mm)
section | 5.0 Wilton Street - Layard Street to Moana Street (DN125mm)
checkpoint | Link in at intersection of Layard and Wilton Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail M in sheet 15 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Layard and Wilton Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail M in sheet 15 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-LAYARD CH14 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-LAYARD CH14 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-LAYARD CH14 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#126 Layard Street needs confirmation
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#125 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#131 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#128 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH01 at CH83 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH01 at CH83 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH01 at CH83 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#37 High Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#41 High Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Wilton Street and High Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail E in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Wilton Street and High Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x1)
label | Detail - As per detail E in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Removal of existing cross and reinstated with straight through pipe at SW corner of Wilton Street and High Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
label | Detail - As per typical details sheet 18
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4130
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-HIGH CH125 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-HIGH CH125 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-HIGH CH125 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#40 High Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#143 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#147 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH02 at CH179 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH02 at CH179 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH02 at CH179 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#150 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#149 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Wilton Street andTerrace Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail F in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Wilton Street andTerrace Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x1)
label | Detail - As per detail F in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Removal of existing tees (2) and reinstated with straight through pipe and associated bends/thrust protection at SW corner of Wilton Street and High Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
label | Detail - As per detail L in sheet 16 and typical details sheet 18
label | Frequency - per connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4130
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-TERRACE CH235 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-TERRACE CH235 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-TERRACE CH235 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#159 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#162 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#166 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#165 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH03 at CH294 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH03 at CH294 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH03 at CH294 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#167 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#170 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#175 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Wilton Street and Lamond Street West (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail G in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Wilton Street and Lamond Street West (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail G in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve LAMOND-WILTON (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve LAMOND-WILTON (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve LAMOND-WILTON (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#177 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-LAMOND CH347 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-LAMOND CH347 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WILTON-LAMOND CH347 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#180 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#181 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#184 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH04 at CH387 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH04 at CH387 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WILTON FH04 at CH387 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#185 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#188 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#189 Wilton Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#133 Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D2.7 - Trenching and excavation
label | ACTION (W, M, H) - M
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - Daily
label | Inspection / Test Method - Inspection
label | Verification Records - RCP and digging checklist
label | Standard - NZS 4407
label | Signatory - Site Engineer
checkpoint | D2.9.1 - Pressure testing & disinfection (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
label | Detail - pressure testing of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - AS/NZS 2566:2 Section 6.3
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.9.1 - Pressure testing & disinfection (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Detail - Disinfection of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Engineer's inspections
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Inspection report
label | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
label | Frequency - As required
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer's Approval
label | Detail - Mark out the trench including overcuts
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NDM testing
label | Detail - Provide NDM test results for AP65 and AP40 layers
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checklist | 6.0 Waihopai Street - Layard Street to Moana Street (DN180mm) | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 6.0 Waihopai Street - Layard Street to Moana Street (DN180mm)
section | 6.0 Waihopai Street - Layard Street to Moana Street (DN180mm)
checkpoint | Link in at intersection of Layard and Waihopai Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail H in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Layard and Waihopai Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail H in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Removal of existing teeand bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Layard and Waihopai Streets
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
label | Detail - As per detail L in sheet 16 and typical details sheet 18
label | Frequency - per connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4130
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAYARD CH15 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAYARD CH15 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAYARD CH15 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#90 Layard Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#92 Layard Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#4 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#7 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#8 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#18 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH01 at CH90 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH01 at CH90 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH01 at CH90 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and High Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail I in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and High Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail I in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#11 Waihopai Street needs confirmation
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Engineers Representative
checkpoint | D8.3, D8.4 - Lateral connection to house no#22 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-HIGH CH126 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-HIGH CH126 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-HIGH CH126 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#26 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#25 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#29 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH02 at CH178 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH02 at CH178 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH02 at CH178 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#30 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#38 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#33 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai and Terrace Streets (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail J in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai and Terrace Streets (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail J in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Capping of existing tees to blank abandoned ends. Intersection of Waihopai and Terrace Streets
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Tee ends blanked and thrust protected
label | Detail - As per typical details in sheet 18
label | Frequency - per connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4130
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-TERRACE CH238 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-TERRACE CH238 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-TERRACE CH238 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#42 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#46 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#52 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH03 at CH285 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH03 at CH285 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH03 at CH285 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#53 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#54 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#58 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and Lamond Street West (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail I in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and Lamond Street West (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail I in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#60 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAMOND CH347 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAMOND CH347 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-LAMOND CH347 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#62 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#64 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#71 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#66 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#70 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH04 at CH393 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Hydrant outlet is between 200mm & 400mm from the finished ground level
label | Detail - The fire hydrant should be installed in accordance with the standard drawing details in sheet 17 fig.W1. section 3 of NZS 4522.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH04 at CH393 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D5.5 - Fire Hydrant WAIHOPAI FH04 at CH393 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Paint marking, RRPM and Hydrant marker
label | Detail - Hydrant paint markings as per NZS4501:1972 and as per detail W18, marker post as per detail W11
label | Frequency - Per each hydrant
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - NZS 4522
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#75 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#74 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D8.3, D8.4 - Lateral connection to house no#78 Waihopai Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - The min depth of the connection 700mm in the road and 300mm to 375mm below the GL at the boundary to the top of the toby, to be checked and witnessed by site rep.
label | Detail - As per fig.W20 of sheet 17 and specifications in D8.3 and D8.4
label | Frequency - Per each connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4129
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-MOANA CH438 (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Spindle height to be max 600mm from surface
label | Detail - The valve should be installed in accordance with the standard drawing details in sheet 17 fig.W4 & W9
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-MOANA CH438 (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust wall installed
label | Detail - Thrust wall constructed as per fig.W9 of page 17 of the drawings
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | D5.4.2 - Isolation Valve WAIHOPAI-MOANA CH438 (3)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Surface box finish
label | Detail - cast iron valve box to be flush with the finished surface level.
label | Frequency - Per each valve
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and Moana Street (1)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Manifold bolts to be torqued to manufacture's specification, to be checked and witnessed by the Site representative before backfilling.
label | Detail - PE to DI connection to be done as per the detail K in sheet 16 of the drawing
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Link in at intersection of Waihopai Street and Moana Street (2)
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Thrust protection to be constructed (x2)
label | Detail - As per detail K in sheet 16 and typical details as per sheet 18
label | Frequency - Before backfilling
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Signatory - Site Engineer
checkpoint | Removal of existing tee and bends and reinstated with straight through pipe and associated bends/thrust protection at intersection of Waihopai Street and Moana Street
label | ACTION (W, M, H) - W
label | Conformance Criteria (What's Required) - Pipe reinstated through old line and thrust protected
label | Detail - As per detail L in sheet 16 and typical details sheet 18
label | Frequency - per connection
label | Inspection / Test Method - Inspection
label | Verification Records - Photos
label | Standard - AS/NZS 4130
label | Signatory - Site Engineer
checkpoint | D2.7 - Trenching and excavation
label | ACTION (W, M, H) - M
label | Conformance Criteria (What's Required) - In accordance with NZS 4407
label | Detail - AP65 Subbase particle size and sand equivalent
label | Frequency - Daily
label | Inspection / Test Method - Inspection
label | Verification Records - RCP and digging checklist
label | Standard - NZS 4407
label | Signatory - Site Engineer
checkpoint | D2.9.1 - Pressure testing & disinfection (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - AS/NZS 2566:2 Section 6.3
label | Detail - pressure testing of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - AS/NZS 2566:2 Section 6.3
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D2.9.1 - Pressure testing & disinfection (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Detail - Disinfection of the new PE main
label | Frequency - Prior to link in
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Standard - NZS 4404:2004 Appendix C, AS/NZS 2566:2 Section 7
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | D1.3.3 - Engineer's inspections
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Inspection report
label | Detail - Enginer's inspection for pipe, concrete pre pour, pre sealing
label | Frequency - As required
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (1)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Engineer's Approval
label | Detail - Mark out the trench including overcuts
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Inspection
label | Verification Records - Email
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | C1.18 - Surface Reinstatement (2)
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - NDM testing
label | Detail - Provide NDM test results for AP65 and AP40 layers
label | Frequency - Prior to surfacing
label | Inspection / Test Method - Testing
label | Verification Records - Test records
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checklist | 7.0 Close out documentation | itp |  |  |  |  | ITP - Salford, Moana, Wilton, Waihopai Streets - 7.0 Close out documentation
section | 7.0 Close out documentation
checkpoint | C1.13 - As-built
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Ensure as-built data recorded and submitted
label | Detail - Red pen markup drawing
label | Frequency - Prior to PCC application
label | Inspection / Test Method - Submission
label | Verification Records - Asbuilt plans
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | PS3 submission
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - Producer statement for construction to be supplied to client
label | Detail - As per schedule 6 3910:2013
label | Frequency - Prior to PCC application
label | Inspection / Test Method - Submission
label | Verification Records - Email of notice
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | WCN and CAR close out
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - To be submitted at completion of works
label | Detail - Submission to ICC of completion of works in road corridor and close out of CAR
label | Frequency - Prior to PCC application
label | Inspection / Test Method - Submission
label | Verification Records - PS3 document
label | Signatory - Engineers Representative
holdpoint | HOLD POINT
checkpoint | QA documents submitted
label | ACTION (W, M, H) - H
label | Conformance Criteria (What's Required) - All required documents submitted throughout and at conclusion of project
label | Detail - All connection sheets, weld logs, NDM results, destructive testing weld reports, encountered services sheets, construction photographs, any outstanding H&S or non conformance reporting
label | Frequency - Prior to PCC application
label | Inspection / Test Method - Submission
label | Verification Records - Various
label | Signatory - Engineers Representative
holdpoint | HOLD POINT