## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-277-RAIL-CPD-Track Formation - General Fill
ITP Description: |  | Track Formation - General Fill
Project: |  | Calder Park Drive
Discipline (e.g. CIV/STR/RAIL: |  | RAIL
Revision Number: |  | 0
Revision Date: |  | 2025-05-08
ITP created by: |  | Jake Argentaro
ITP approved for use by: |  | Pradeep Talasila
Special Notes to ConQA Team : |  | ITP to be used at Calder Park Drive Project Only
Inspection & Test Plan - Track Formation - General Fill
|  |  | Document Title: ITP-277-RAIL-CPD-Track Formation - General Fill | [5 empty] | Revision: | 0
[9 empty] | Date: | 2025-05-08
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Drawing Pack - Rail Track and Civil | MRP-DPK-080-00-CPW-0063-0 Rail Track & Civil Drawings - Calder Park Drive | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Metro Engineering Specifications - Earthworks & Formation Specification | L1-CHE-SPE-178 (VERSION 3) | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Metro Engineering Specifications - Earthworks & Formation Standard | L1-CHE-STD-029 (VERSION 4) | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Australian Standard - Methods of testing soils for engineering purposes | AS 1289 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | General Fill Material Conformance (1 of 2) | L1-CHE-SPE-178 - Clause 5.10.1. Australian Standard - AS1289 | General Fill shall consist of suitable material that shall be compacted to a minimum characteristic value of density ratio 98% Refer to AS1289 for tests Enter: Teambinder Material Approval number | Visual Review Test | Once, for each material type - prior to works commencement | HP | PE/Nominated authority | Material approval in TeamBinder This ITP Signed Off
2.2 | General Fill Material Conformance (2 of 2) | L1-CHE-SPE-178 - Clause 5.10.4.1. Table 1 AS 1289 | General fill shall comply with the criteria listed in Table 1 (L1-CHE-SPE-178 - Clause 5.10.4.1.): • Soaked CBR - 3% min nominal • Plasticity Index 9-20% • Dispersion (pin hole dispersity) - ND1/ND2 • Dispersion (Emerson class number of soil) - not to be class 1 or 2 • Collapse strain - to be agreed by MTM geotechnical engineer • Free swell index - 2.5% max. • Soil soluble salt content - 3% • Organic content (dry weight) - 2% max. Refer to AS 1289 for Tests Enter: Teambinder Material Approval number | Visual Review Test | Once, for each material type - prior to works commencement | HP | PE/Nominated authority | Material approval in TeamBinder This ITP Signed Off
3 | Preliminaries - Procedures & Documentation
3.1 | Pre-Commencement of Fill Works | L1-CHE-SPE-178 - Clause 5.12.5. Table 7 AS1289 Tests | The Contractor shall not commence placing any fill on the prepared areas until the area has been reviewed by the Responsible Engineer. | Visual Inspection | Prior to commencement of fill works | HP | SE/PE | This ITP Signed Off MTM representative signoff Attach: Site Photos
4 | Pre-Construction Activities
4.1 | Approval of IFC drawings | MRP-DPK-080-00-CPW-0063-0 Rail Track & Civil Drawings - Calder Park Drive | Approved IFC Drawings | Document review and approval | Prior to works commencing | HP | SE/PE | This ITP Signed Off
4.2 | Survey Set Out | IFC Drawings | Set out pegs in place and clearly mark out limits of works. | Visual Inspection | Prior to commencement of fill works | HP* | SE/PE/SPE | This ITP Signed Off
5 | Construction Activities
5.1 | General Fill Preparation and Installation - For track constructed on embankment (1 of 2) | L1-CHE-SPE-178 - Clause 5.10.3.1. Australian Standard - AS1289 IFC Drawings. | Any surface on which fills are to be constructed shall be proof rolled. All layers of general fill material shall be compacted to a minimum characteristic value of density ratio of 98% (Standard Compaction) Where a layers to be constructed in fill it shall be constructed in uniform thickness not exceeding 200mm lose. • One test per 1000m³ • Volume < 1000m³ atleast one set of tests shall be carried out | Standard Compaction | Each Lot | HP | SE/PE | This ITP Signed Off Attach: Compaction Test Report
5.2 | General Fill Preparation and Installation - For track constructed on embankment (2 of 2) | L1-CHE-SPE-178 - Clause 5.10.3.1. Australian Standard - AS1289 IFC Drawings. | General fill shall comply with the criteria listed in Table 1 (L1-CHE-SPE-178 - Clause 5.10.4.1.): • Soaked CBR - 3% min nominal • Plasticity Index 9-20% • Dispersion (pin hole dispersity) - ND1/ND2 • Dispersion (Emerson class number of soil) - not to be class 1 or 2 • Collapse strain - to be agreed by MTM geotechnical engineer • Free swell index - 2.5% max. • Soil soluble salt content - 3% • Organic content (dry weight) - 2% max. Refer to AS 1289 for Tests • One test per 1000m³ • Volume < 1000m³ atleast one set of tests shall be carried out | Standard Compaction | Each Lot | HP | SE/PE | This ITP Signed Off Attach: Test Report
5.3 | Proof rolling | L1-CHE-SPE-178 - Clause 5.4.1. and Clause 5.10.3.1. | Proof roll as per L1-CHE-SPE-178 - Clause 5.10.3.1. | Proof roll | Each Lot | HP | SE/PE | This ITP Signed Off MTM representative Signoff Attach: Site Photos
6 | Post-Construction Activities
6.1 | General Fill Finishing and Tolerances - For track constructed on embankment / Survey Conformance | L1-CHE-SPE-178 - Clause 5.10.6.1. | General fill on embankments shall be installed within +/- 40mm of approved design surface level | Document Review | Each Lot | IP | SE/Surveyor | This ITP Signed Off Attach: Survey Conformance Report
6.2 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP* | SE/PE/SPE | This ITP Signed Off
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /