## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Service Penetrations to Rigid Air Barriers |  |  |  |  | Yes | Service Penetrations to Rigid Air Barriers | 00d43dc0-d7b0-4689-9305-4ad788700d95
checkpoint-status |  |  | checkpoint | All pipes should be sealed with caulk, a gap between the pipe and air barrier should be between 3-8mm
checkpoint-status |  |  | checkpoint | Ducts are sealed with caulking and backing rods for gaps under 35mm. Gaps over 35mm is sealed with rubber gaskets or flashing with caulking. All seals on duct penetrations require photographic evident particularly the top seal and be signed off.
checkpoint-status |  |  | checkpoint | Cables penetrations are sealed with caulking.
button | c33e580f-7c0b-5822-bb4a-e7c093abcab4 |  | button | Caulking material should be applied between cables before packing the bundle, a minimum of 2 cable ties should be tightly applied between 5 and 10mm apart to minimise movement where the caulking material is applied. | Yes,No
button | 1f3846fc-5ce8-5fca-b245-89ceb90159f9 |  | button | Bundling of cables should be limited to 8 cables. | Yes,No
button | 5d56a83e-8383-5532-b187-38ef1bcc67ca |  | button | Spacer (backing rods) with a minimum size of 5mm should be placed between cable bundles. | Yes,No
checkpoint-status |  |  | checkpoint | Cable trays are expected to be treated similar to fire/smoke penetration which the red highlighting the caulking material.
checklist-sectioned |  |  | checklist | SVR: |  |  |  |  | Yes | Engineer Site Visit Report | 02963c06-15b7-4667-a33c-9941bd9ea40e
checkpoint-group |  |  | section | Site Visit Report
checkpoint-status |  |  | checkpoint | SVR Attached
text | 2bf6224d-212d-4c05-8d20-702627eeda57 |  | textbox | SVR No.
folder-normal |  | Not allowed as a child of checklist-sectioned. | folder-normal | Follow-Up Action(s)
checkpoint-group |  |  | section | Close-Out
checkpoint-status |  |  | checkpoint | SVR Closed-Out
checklist-flat |  |  | checklist | Structural Steel |  |  |  |  | Yes | Structural Steel | 0344b58a-23f5-4c88-878d-254a4916d845
checkpoint-status |  |  | checkpoint | Steel inspected on arrival, checked and correct and no significant damage
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Correct location and orientation
checkpoint-status |  |  | checkpoint | All drypacking and grouting completed , reviewed and approved to meet required specifications
checkpoint-status |  |  | checkpoint | General photos / comments / observations during install
checklist-flat |  |  | checklist | Fill Checklist |  |  |  |  | Yes | Fill Checklist | 08b9130c-0cce-4e3b-8078-4778c402b400
checkpoint-no-status |  |  | checkpoint | Fill
text | ed2d81c1-3532-539e-9cd3-a8df329e6038 |  | textbox | Zone / Level / Grid(s) recorded
checkpoint-status |  |  | checkpoint | Sub-grade inspected by engineer and approved for fill
checkpoint-status |  |  | checkpoint | Fill layers as per specification
checkpoint-status |  |  | checkpoint | Compaction testing completed and achieved to specification (attach report)
checkpoint-status |  |  | checkpoint | RL Checked by Hawkins
checklist-flat |  |  | checklist | Internal Gutter |  |  |  |  | Yes | Internal Gutter | 096cf461-335f-42e0-98b6-428bf7ee67c3
checkpoint-status |  |  | checkpoint | Timber framing installed as per drawing
checkpoint-status |  |  | checkpoint | Outlet opening done as per drawing
checkpoint-status |  |  | checkpoint | ILD mesh installed
checkpoint-status |  |  | checkpoint | Torch on membrane installed (bottom and side)
checkpoint-status |  |  | checkpoint | ILD test result collected
checkpoint-status |  |  | checkpoint | PIR 50mm glue down + outlet installed
checkpoint-status |  |  | checkpoint | ILD mesh installed
checkpoint-status |  |  | checkpoint | Sarnafil welded correctly
checkpoint-status |  |  | checkpoint | ILD test result collected
checkpoint-status |  |  | checkpoint | Hand over to roof work
checklist-flat |  |  | checklist | CFRP Strengthening |  |  |  |  | Yes | CFRP Strengthening | 0c18fdd6-11bb-42ec-9aa3-6bb911ace434
checkpoint-status |  |  | checkpoint | Has the concrete been prepared
checkpoint-status |  |  | checkpoint | Has the product been installed as per manufacturers requirement
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
button | 2fe50ada-d8e8-5537-9ba1-1ab0238fdbc5 |  | button | Is this an architectural area requiring attention | Yes,No
checklist-sectioned |  |  | checklist | In Ground Water & Gas Mains Checklist |  |  |  |  | Yes | In Ground Water & Gas Mains Checklist | 0c4baa48-5f8a-4d41-b1ab-e9f2e5e0dce3
checkpoint-group |  |  | section | Water mains
checkpoint-status |  |  | checkpoint | All fittings scrapped correctly
checkpoint-status |  |  | checkpoint | Iso used on fittings
checkpoint-status |  |  | checkpoint | Valves fitted correctly
checkpoint-status |  |  | checkpoint | Fittings welded & weld indicator has popped out
checkpoint-status |  |  | checkpoint | Trace wire and ID tape installed
checkpoint-group |  |  | section | Gas main
checkpoint-status |  |  | checkpoint | All fittings scrapped correctly
checkpoint-status |  |  | checkpoint | Iso used on fittings
checkpoint-status |  |  | checkpoint | Valves fitted correctly
checkpoint-status |  |  | checkpoint | Fittings welded & weld indicator has popped out
checkpoint-status |  |  | checkpoint | Trace wire and ID tape installed
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | All open ends capped
checkpoint-status |  |  | checkpoint | Pipework bedded correctly
checkpoint-status |  |  | checkpoint | Tidy work areas
checkpoint-status |  |  | checkpoint | Pressure test pipework
checkpoint-status |  |  | checkpoint | Visual check (for leeks from valves, tees, saddles, etc)
checkpoint-status |  |  | checkpoint | Backfill around pipework with fines
checkpoint-status |  |  | checkpoint | as-built completed and photo
checkpoint-status |  |  | checkpoint | Installers name & date works completed
text | 511ff863-6523-57e8-b023-ae701e8717c1 |  | textbox | Installers name
text | b922ea92-5647-5a8c-924e-bc797e4ed8d0 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Tested by & date
text | acde50fb-2b4e-5c27-95fb-37233c2ed4ac |  | textbox | Tested by:
text | 23111134-c3b4-5553-a508-71edf81331c4 |  | textbox | Date tested:
checkpoint-status |  |  | checkpoint | Council inspector sign off and date
checklist-flat |  |  | checklist | Tanking / Waterproofing Checklist (Audit) |  |  |  |  | Yes | Tanking / Waterproofing Checklist (Audit) | 0c909a29-1e39-4212-b598-d71659722f4c
checkpoint-status |  |  | checkpoint | Preparation / Substrate acceptable
checkpoint-status |  |  | checkpoint | Correct product delivered and checked - approval given to install
checkpoint-status |  |  | checkpoint | Any inspections / observations documented, reviewed and closed out
checkpoint-status |  |  | checkpoint | Trades QA received & attached as applicable
checkpoint-status |  |  | checkpoint | Waterproofing install completed, reviewed and approved to meet required specifications
checklist-flat |  |  | checklist | Manhole Install Checklist |  |  |  |  | Yes | Manhole Install Checklist | 0d55aa9c-c7e9-48de-89fb-e087fdfba78e
checkpoint-status |  |  | checkpoint | Latest construction drawings referenced and followed
text | d488283e-102a-581c-8a30-0ab5d7b5c484 |  | textbox | Drawing & Revision Number
checkpoint-status |  |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status |  |  | checkpoint | Ground Conditions Checked and Acceptable
checkpoint-status |  |  | checkpoint | Bedding depth and material correct (photo required)
checkpoint-status |  |  | checkpoint | Correct manhole size installed to specified Invert Level
checkpoint-status |  |  | checkpoint | Manhole risers & steps installed and joints sealed as specified (photo required)
checkpoint-status |  |  | checkpoint | Manhole benching completed and acceptable (photo required)
checkpoint-status |  |  | checkpoint | Concrete manhole cover installed and sitting correctly with hole covered if required (photo required)
checkpoint-status |  |  | checkpoint | Cast Iron Lid installed and fixed at correct height (photo required)
checkpoint-status |  |  | checkpoint | CCTV test complete
checkpoint-status |  |  | checkpoint | Manhole Installation reviewed and approved (photo required)
checkpoint-status |  |  | checkpoint | Backfill completed & compacted as specified (Photos during backfill required)
checklist-sectioned |  |  | checklist | Ceiling Preline incl High Level Services |  |  |  |  | Yes | Ceiling Preline incl High Level Services | 1397430a-c250-4975-b408-6d3672401e83
checkpoint-group |  |  | section | QA - Plumbing First Fix
checkpoint-status |  |  | checkpoint | Reference Drawings ( add numbers and revisions)
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Consultants Inspection sign off
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Council inspection and testing complete and signed off
checkpoint-status |  |  | checkpoint | Engineer has signed off Seismic restraints
checkpoint-status |  |  | checkpoint | Witness testing of pipework by Hawkins
checkpoint-group |  |  | section | Fire Protection (Sprinklers & Alarms) First Fix
checkpoint-status |  |  | checkpoint | Reference Drawings ( add numbers and revisions)
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Consultant inspection sign off
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Engineer has signed off Seismic restraints
checkpoint-status |  |  | checkpoint | Witness testing of pipework by Hawkins
checkpoint-group |  |  | section | Mechanical Services First Fix
checkpoint-status |  |  | checkpoint | Reference Drawings ( add numbers and revisions)
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | All required testing complete
checkpoint-status |  |  | checkpoint | Engineer has signed off Seismic restraints
checkpoint-status |  |  | checkpoint | Consultant sign off
checkpoint-status |  |  | checkpoint | All ends covered/protected to reduce debris
checkpoint-status |  |  | checkpoint | Witness testing of compliance check by Hawkins
checkpoint-group |  |  | section | Electrical First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All required testing complete
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Consultant sign off
checkpoint-status |  |  | checkpoint | Engineer has signed off Seismic restraints
checkpoint-status |  |  | checkpoint | Witness testing of compliance check by Hawkins
checkpoint-group |  |  | section | Data First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All required testing complete
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Consultant sign off
checkpoint-status |  |  | checkpoint | Engineer has signed off Seismic restraints
checkpoint-status |  |  | checkpoint | Witness testing of compliance check by Hawkins
checkpoint-group |  |  | section | Security First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All required testing complete
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Consultant sign off
checkpoint-status |  |  | checkpoint | Engineer has signed off Seismic restraints
checkpoint-status |  |  | checkpoint | Witness testing of compliance check by Hawkins
checkpoint-group |  |  | section | Rondo Ceiling Grid Installation
checkpoint-status |  |  | checkpoint | Service penetrations mark out completed, checked and acceptable (clashes considered)
checkpoint-status |  |  | checkpoint | Ceiling Grid ( pass when all below ticked)
boolean | 68e7cef0-de8a-5c29-8460-fc52fad1daa9 |  | tickbox | Ceiling height correct
boolean | 74b9a255-4e27-5a78-8ecd-f370ccb73e3a |  | tickbox | Appropriate fixings used and installed as per required specification
boolean | 98f383af-0990-5f7b-8a95-6e5e275ead5c |  | tickbox | Appropriate spacings for respective grid elements
boolean | 70642190-88ae-5cef-aa35-b8f91b909586 |  | tickbox | Perimeter channel/angle installed correctly
boolean | ba858e08-ae3b-51aa-9d03-c4d16db0180e |  | tickbox | All strong backs installed where required to meet specification
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Insulation Prior to Lining
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Insulation pre lining works completed, checked & approved
boolean | 0e8a6528-73d9-5e03-87e2-32322c4873f4 |  | tickbox | Correct product & R value as per specification
boolean | 34066410-3f3f-5290-b2ec-9cf9ed662c9d |  | tickbox | Fitting Snug
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Council Sign Off
checkpoint-status |  |  | checkpoint | Council preline inspection passed
checklist-flat |  |  | checklist | Capping Beam |  |  |  |  | Yes | Capping Beam | 14b13fc1-2127-4c52-b129-b265f7813dc4
checkpoint-status |  |  | checkpoint | Grouted tubes
checklist-flat |  |  | checklist | Base Isolator |  |  |  |  | Yes | Base Isolator | 161037e5-9cdf-4639-a81f-373b64ced9cf
checkpoint-status |  |  | checkpoint | Base Isolator
text | 567df56e-5eb8-598a-9772-d8f4ecf553a7 |  | textbox | Zone / Level / Grid(s) recorded
checkpoint-status |  |  | checkpoint | RL base isolator checked
button | c940c22f-ea8a-5aca-b7db-1ea3416a4105 |  | button | Isolator type | LRB,NRB,PS-A,PS-B,PS-C
checklist-flat |  |  | checklist | Waste Water (Main Line) - Pipeline Installation Checklist |  |  |  |  | Yes | Waste Water (Main Line) - Pipeline Installation Checklist | 1ae92220-2cf5-408a-a227-32db04aa8b7d
checkpoint-status |  |  | checkpoint | Latest construction drawings referenced and followed
text | 0576824c-bf55-57aa-93db-ae0a66f7c091 |  | textbox | Drawing & Revision Number
checkpoint-status |  |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status |  |  | checkpoint | Ground Conditions Checked & Acceptable
checkpoint-status |  |  | checkpoint | Bedding depth and material correct (photo required)
checkpoint-status |  |  | checkpoint | Correct pipe (size, material & class) laid to specified level, grade and jointed as specified
text | 1322c1c4-09e1-5b02-90cd-58367fba65be |  | textbox | Invert Level (upstream manhole)
text | 84585604-45e3-5607-993e-17b04f7a2518 |  | textbox | Invert Level (downstream manhole)
text | 5cc39329-685f-501c-9061-67d65b7fab16 |  | textbox | Design length of pipe (m)
text | a0389f76-fc00-57c7-a811-5df1055df36f |  | textbox | Length of pipe installed (m)
text | 5dead63f-0297-5fec-a43d-20366e51c71d |  | textbox | Grade of Pipe-Line %
checkpoint-status |  |  | checkpoint | Connections to manholes complete and approved (photo required)
checkpoint-status |  |  | checkpoint | Air/water test completed (photo of pressure gauge taken at START & FINISH)
checkpoint-status |  |  | checkpoint | Backfill completed & compacted as specified
checkpoint-status |  |  | checkpoint | Relevant tests, photos & as-built information attached
checklist-flat |  |  | checklist | Envelope - Internal gutter |  |  |  |  | Yes | Envelope - Internal gutter | 1b2ac01f-fe38-48fd-b3cd-3b81c4dbe268
checkpoint-status |  |  | checkpoint | 17mm C-D structural plywood
checkpoint-status |  |  | checkpoint | minimum fall of 1:100 (0.57°)
checkpoint-status |  |  | checkpoint | 5 mm fillets
checkpoint-status |  |  | checkpoint | Locations for outlets and sumps
checkpoint-status |  |  | checkpoint | Correct width and level/depth
checkpoint-status |  |  | checkpoint | General photos, comments and observations during paint application
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checklist-sectioned |  |  | checklist | Water Pump Commissioning |  |  |  |  | Yes | Water Pump Commissioning | 27cc24b1-dc81-41d1-a75b-44d6bed43a13
checkpoint-group |  |  | section | Pumpset manifold
checkpoint-status |  |  | checkpoint | Connections welded correctly
checkpoint-status |  |  | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
checkpoint-status |  |  | checkpoint | Valves fitted correctly
checkpoint-status |  |  | checkpoint | Line strainer fitted between pump & tank
checkpoint-group |  |  | section | Pumps
checkpoint-status |  |  | checkpoint | Pump 1 Startup KPA
checkpoint-status |  |  | checkpoint | Pump 1 kick out pressure KPA
checkpoint-status |  |  | checkpoint | Pump 2 Startup KPA
checkpoint-status |  |  | checkpoint | Pump 2 kick out pressure KPA
checkpoint-status |  |  | checkpoint | Pressure vessel pressure
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Mains water change over
checkpoint-status |  |  | checkpoint | Flow test pump
checkpoint-status |  |  | checkpoint | Pressure tests pipework
checkpoint-status |  |  | checkpoint | Visual check (for leaks from valves, tees, saddles, etc)
checkpoint-status |  |  | checkpoint | Non return valves fitted
checkpoint-status |  |  | checkpoint | Installers name & date works completed
text | dd02a9ec-5a79-5e48-bd50-93eadaff61a9 |  | textbox | Installers name
text | f244b4b0-2f85-5c2c-81cd-e72048946136 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Tested by & date
text | 8654d84f-62de-5ef2-8fb5-d3433b972b2d |  | textbox | Tested by:
text | 7b1c1c37-906e-5f0e-81a1-0248043c3740 |  | textbox | Date tested:
checkpoint-status |  |  | checkpoint | Council inspector sign off and date
checklist-flat |  |  | checklist | Underslab Services Checklist (Audit) |  |  |  |  | Yes | Underslab Services Checklist (Audit) | 2abbebee-0fb3-4060-a384-935b6ae4fe84
checkpoint-status |  |  | checkpoint | Electrical services/ conduits installed, fixed in correct location, backfilled and correct as per design
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Signoff
checkpoint-status |  |  | checkpoint | Hydraulic services installed, fixed in correct location, backfilled and correct as per design
boolean | eff9b4c9-41cc-5151-b668-e3aea52d07b7 |  | tickbox | Storm Water
boolean | b2e855cf-dc5d-5893-8fb7-cbb17617ecea |  | tickbox | Sewer
boolean | ae58a314-a6c1-5e27-a175-bb2dbf001342 |  | tickbox | Water Supply
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Signoff
checkpoint-status |  |  | checkpoint | Gas installed, fixed in correct location, backfilled and correct as per design
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Signoff
checkpoint-status |  |  | checkpoint | Telecommunication/Fibre installed, fixed in correct location, backfilled and correct as per design
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Signoff
checkpoint-status |  |  | checkpoint | Any other relevant services installed, fixed in correct location, backfilled and correct as per design
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Signoff
checkpoint-status |  |  | checkpoint | Any additional observations / attachments
checkpoint-status |  |  | checkpoint | Any relevant inspections carried out and attached - observations documented and closed out
checkpoint-status |  |  | checkpoint | All subfloor services correctly installed to respective area
checklist-flat |  |  | checklist | Connection from Private - Public Checklist |  |  |  |  | Yes | Connection from Private - Public Checklist | 2b66c65e-a23c-4a7c-b134-8ae94fc9a916
checkpoint-status |  |  | checkpoint | Approval to connect given by relevant Authority
text | c2877c84-a07b-509f-b22f-97a8aafd4c71 |  | textbox | EPA number
text | d8abf733-2d30-58ec-96f6-1a96dcb9e267 |  | textbox | Corridor Access Request
checkpoint-status |  |  | checkpoint | Advice notice conditions from relevant Authority received
checkpoint-status |  |  | checkpoint | Work done in accordance with requirements (photos required)
checklist-sectioned |  |  | checklist | Insitu Stitch Joints |  |  |  |  | Yes | Insitu Stitch Joints | 2fba61ab-b997-4d18-9333-f9d136d1ecc0
checkpoint-group |  |  | section | Pour Details
checkpoint-no-status |  |  | checkpoint | Details
text | 1d2003e8-79c0-5174-bdd5-6eaff61d08ca |  | textbox | Area to be poured:
text | 6f8c2c21-806f-5d9b-a45a-441c75fdd3af |  | textbox | Date of pour:
checkpoint-group |  |  | section | Formwork
checkpoint-status |  |  | checkpoint | Formwork braced & fixed correctly
checkpoint-status |  |  | checkpoint | All surfaces correctly prepared (e.g. joints to existing concrete, release agent to formwork etc)
checkpoint-group |  |  | section | Reinforcing
checkpoint-status |  |  | checkpoint | Size and type correct to specification
checkpoint-group |  |  | section | Pre-Pour Completion (Approval to pour)
checkpoint-status |  |  | checkpoint | Engineer inspection completed - any observations / remedial work documented and closed out
checkpoint-status |  |  | checkpoint | All relevant inspections completed and attached
checkpoint-status |  |  | checkpoint | Main contractor inspection completed - Approval given to pour concrete
checkpoint-group |  |  | section | Concrete Supplier Specifics
checkpoint-no-status |  |  | checkpoint | Details
text | 3d1d733f-2d52-5cff-ac7e-961a94ab187c |  | textbox | Supplier Name:
text | aaad4d79-ac26-5d6b-91fe-3f2577858f79 |  | textbox | Specified concrete strength:
text | 5cef97e4-48b0-50a2-abf6-77a9f353b3d1 |  | textbox | Concrete strength ordered:
text | ce351a24-8bc9-592a-b743-ae6143ddab37 |  | textbox | Concrete quantity ordered:
checkpoint-status |  |  | checkpoint | Test blocks booked
checkpoint-status |  |  | checkpoint | All concrete dockets photographed/ attached
checkpoint-group |  |  | section | Post Pour Checks/Sign Off
checkpoint-status |  |  | checkpoint | Any remedial work completed
checkpoint-status |  |  | checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
checklist-flat |  |  | checklist | Waterproofing Checklist |  |  |  |  | Yes | Waterproofing Checklist | 34244357-39de-4652-b867-f48c0dceb79c
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Preparation / Substrate acceptable
checkpoint-status |  |  | checkpoint | Correct product delivered and checked - approval given to install
checkpoint-status |  |  | checkpoint | General photos/comments during install
checkpoint-status |  |  | checkpoint | Any inspections / observations documented, reviewed and closed out
checkpoint-status |  |  | checkpoint | Waterproofing install completed, reviewed and approved to meet required specifications
checklist-sectioned |  |  | checklist | ISN Report: |  |  |  |  | Yes | ISN Report | 368f0a2d-e9ae-46ac-b6a5-d673601baf08
checkpoint-group |  |  | section | Site Visit Report
checkpoint-status |  |  | checkpoint | SVR Attached
text | 2bf6224d-212d-4c05-8d20-702627eeda57 |  | textbox | SVR No.
folder-normal |  | Not allowed as a child of checklist-sectioned. | folder-normal | Follow-Up Action(s)
checkpoint-group |  |  | section | Close-Out
checkpoint-status |  |  | checkpoint | SVR Closed-Out
checklist-flat |  |  | checklist | Timber Framing |  |  |  |  | Yes | Timber Framing | 3c3f2ae3-65da-4aeb-9abf-de5cc036bc01
checkpoint-status |  |  | checkpoint | Dimensions / locations checked and accurate
checkpoint-status |  |  | checkpoint | All frames are square
checkpoint-status |  |  | checkpoint | Frames are straight and level
checkpoint-status |  |  | checkpoint | Fixings are correct including seizmac requirements
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All framing completed correctly within tolerance in respective area
checkpoint-status |  |  | checkpoint | Signed Off
checklist-flat |  |  | checklist | Site Concrete Checklist |  |  |  |  | Yes | Site Concrete Checklist | 3e65946a-d9f9-4b20-bb2b-6e917280ca60
checkpoint-status |  |  | checkpoint | Excavation depth and location checked and correct
checkpoint-status |  |  | checkpoint | Ground conditions acceptable
checkpoint-status |  |  | checkpoint | Concrete specifications checked, correct and delivery docket photographed
checkpoint-status |  |  | checkpoint | Site concrete placed
text | 4d63a2e5-37bf-5496-b4fa-b5b68f82dc43 |  | textbox | Placed by:
checkpoint-status |  |  | checkpoint | Concrete placed to the correct height
checkpoint-status |  |  | checkpoint | Site concrete pour completed and finish acceptable
checklist-flat |  |  | checklist | Underground Services Checklist (Audit) |  |  |  |  | Yes | Underground Services Checklist (Audit) | 44da844f-aac5-403f-8e1c-9896fef1635d
checkpoint-status |  |  | checkpoint | Electrical services/ conduits installed, fixed in correct location, backfilled and correct as per design
checkpoint-status |  |  | checkpoint | Hydraulic services installed, fixed in correct location, backfilled and correct as per design
checkpoint-status |  |  | checkpoint | Gas installed, fixed in correct location, backfilled and correct as per design
checkpoint-status |  |  | checkpoint | Telecommunication/Fibre installed, fixed in correct location, backfilled and correct as per design
checkpoint-status |  |  | checkpoint | Any other relevant services installed, fixed in correct location, backfilled and correct as per design
checkpoint-status |  |  | checkpoint | Any additional observations / attachments
checkpoint-status |  |  | checkpoint | Any relevant inspections carried out and attached - observations documented and closed out
checkpoint-status |  |  | checkpoint | All subfloor services correctly installed to respective area
checklist-sectioned |  |  | checklist | Eye Brow |  |  |  |  | Yes | Eye Brow | 473405f6-f59b-4e34-be1c-900673d31778
checkpoint-group |  |  | section | QC Summary
checkpoint-no-status |  |  | checkpoint | QC Summary
text | 98f0f1e2-bc57-5e47-b447-9ee2d851bac0 |  | textbox | Subcontractor/Supplier
text | 803ae822-c5ee-5c27-8dd9-a550be84f9e1 |  | textbox | Works area
text | 356c968d-c8dc-5126-9a63-a9acdd0a62ad |  | textbox | Drawings reference
text | 441ee782-5edd-5718-a829-1901f613fc02 |  | textbox | Project specification reference
checkpoint-group |  |  | section | Precladding
checkpoint-status |  |  | checkpoint | RAB and timber is dry prior to apply revalshield
label | 6e9ab6ea-ba9c-5f32-8535-749c5c8b0ca4 |  | note | Photos
checkpoint-status |  |  | checkpoint | Revealshield is applied correctly (80mm overlap) and as per drawing
label | 8f10462a-72ea-5c9f-9a9c-c4b270645021 |  | note | Photos
checkpoint-status |  |  | checkpoint | Liquidflash is apply around the window opening andany other location required
label | 6363da32-354a-5aeb-b146-2d214d140777 |  | note | Photos
checkpoint-status |  |  | checkpoint | Sealant and flashing tape is applied ( brackets fixed on RAB/ over the top of pressure bar...)
label | 7ad2ebc6-75ab-5fbb-8f55-5abb016ddc53 |  | note | Photos
checkpoint-group |  |  | section | Eyes brow Cladding
checkpoint-status |  |  | checkpoint | Cleats surveyed and checked
label | 0979ea91-4454-5246-b1ef-203c5abdb1ce |  | note | Photos
checkpoint-status |  |  | checkpoint | Aluminium frame as per shopdrawings
label | 605a589a-675c-5dc8-a720-c5db2168a5ba |  | note | Photos
checkpoint-status |  |  | checkpoint | Aluminium frame plumb and levelled
label | a6bd3307-259b-5ab6-8705-f1057133df86 |  | note | Photos
checkpoint-status |  |  | checkpoint | Induraplate flashing as per drawings
label | 6eef6120-6300-51ca-9122-6889f2acf976 |  | note | Photos
checkpoint-group |  |  | section | Final approvals and holdpoints
checkpoint-status |  |  | checkpoint | Hold point - Sub contractor QA
label | 4078bd1a-9dab-5eb2-981a-0ee4e24370dd |  | note | QA REPORT
holdpoint |  |  | signoff | Company QA Check
checkpoint-status |  |  | checkpoint | Engineer Inspections
label | 95a329b3-bcc0-5f8f-8123-5448f02f0fdd |  | note | SITE REPORTS
checkpoint-status |  |  | checkpoint | Council Inspections
label | 257595df-030d-5a4d-9eeb-b9d9e2452c33 |  | note | INSPECTION REPORT
checklist-flat |  |  | checklist | Asbestos Removal Checklist |  |  |  |  | Yes | Asbestos Removal Checklist | 47a094a7-cebc-4e3f-80f7-913324ad225f
checkpoint-status |  |  | checkpoint | Initial Environment/Planning Asbestos report attached
checkpoint-status |  |  | checkpoint | Asbestos Removal approved to commence (all pre-commencement considerations allowed for)
checkpoint-status |  |  | checkpoint | Attach relevant asbestos removal photos (Label all photos with relevant location)
checkpoint-status |  |  | checkpoint | Independent asbestos report completed and attached
checkpoint-status |  |  | checkpoint | Trade contractor QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Any remedial requirements actioned and completed / closed out
checkpoint-status |  |  | checkpoint | All asbestos removed and approval given to progress with work
checklist-flat |  |  | checklist | Civil - Sanitary Sewer |  |  |  |  | Yes | Civil - Sanitary Sewer | 4db08abb-c08b-4125-baed-699b2c45e719
checkpoint-status |  |  | checkpoint | Location details and relevant mark ups attached
checkpoint-status |  |  | checkpoint | Consultant inspection completed as required
checkpoint-status |  |  | checkpoint | Council Inspection completed as required
checkpoint-status |  |  | checkpoint | Invert levels recorded
checkpoint-status |  |  | checkpoint | Invert levels as per design
checkpoint-status |  |  | checkpoint | Received QA from Subcontractor?
checkpoint-status |  |  | checkpoint | As Built drawings received
checkpoint-status |  |  | checkpoint | CCTV Survey
checkpoint-status |  |  | checkpoint | Certificates provided
checkpoint-status |  |  | checkpoint | Installation record photos
checkpoint-status |  |  | checkpoint | Foul Installation completed
checkpoint-status |  |  | checkpoint | Any onsite changes documented (Attach marked up drawings, etc)
checklist-flat |  |  | checklist | Description/Number: |  |  |  |  | Yes | ISN Follow Up Action | 4ecac9a3-994c-4f28-b83b-5ae35da7bced
checkpoint-status |  |  | checkpoint | Follow-Up Action completed
text | ddf14301-8239-5b3b-951b-d5fa379a59cd |  | textbox | Specific Location:
text | 91c806c7-c985-559e-94d6-00a2b29bd0fd |  | textbox | Detail:
text | f17daeb2-6b36-59f2-add1-159d86b7a239 |  | textbox | Action Required:
holdpoint |  |  | signoff | Request Review
checklist-flat |  |  | checklist | Ceiling Postline |  |  |  |  | Yes | Ceiling Postline | 5231d811-39b5-4a95-b5b8-91f3f6ab9b91
checkpoint-status |  |  | checkpoint | Correct linings installed as per linings plan
checkpoint-status |  |  | checkpoint | Fixings as per specification including if glue required
checkpoint-status |  |  | checkpoint | Service penetrations cut out as per architecture RCP
checkpoint-status |  |  | checkpoint | Any ceiling hatches installed & fixed correctly
checkpoint-status |  |  | checkpoint | Ceiling approved for stopping
checkpoint-status |  |  | checkpoint | Stopping light check complete ready for paint
checklist-sectioned |  |  | checklist | Demolition Checklist |  |  |  |  | Yes | Demolition Checklist | 533bdaae-6b18-4af9-950e-c1874295b53c
checkpoint-group |  |  | section | Pre Demolition QA
checkpoint-status |  |  | checkpoint | Traffic management in place (attach TMP)
checkpoint-status |  |  | checkpoint | NVMP completed and attached
checkpoint-status |  |  | checkpoint | Attach any other relevant pre start documentation
checkpoint-status |  |  | checkpoint | All relevant services isolated
boolean | c68b2ad1-4346-5f70-9898-8dac1f06586b |  | tickbox | Power isolated
boolean | 9e1fda30-3b84-5b21-8514-68842798c727 |  | tickbox | Waste/storm water isolated
boolean | 8f58c372-c618-5edb-9f7f-2dbb5ef09b76 |  | tickbox | Gas isolated
boolean | 9026cdef-992c-5c17-bfec-fd9d56d98a21 |  | tickbox | Telecommunication/Fibre isolated
boolean | e64d7ac0-2529-585b-b8a4-fad555a99b74 |  | tickbox | Any other relevant services isolated
text | 4228de12-c9ad-51bc-b3e8-6707bd155240 |  | textbox | Specify which other services were isolated
checkpoint-status |  |  | checkpoint | General Photos of controls (attach and label)
checkpoint-status |  |  | checkpoint | All pre demolition QA completed and approval given to commence demolition
checkpoint-group |  |  | section | Demolition QA
checkpoint-status |  |  | checkpoint | Prior to demolition, all pre start checks have been completed
checkpoint-status |  |  | checkpoint | General photos and observations of demo (attached and labelled)
checkpoint-group |  |  | section | Demolition Complete
checkpoint-status |  |  | checkpoint | All rubbish/debris removed and area left clean and tidy
checkpoint-status |  |  | checkpoint | Trade Contractor QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | All demolition works completed, checked and approved
checklist-flat |  |  | checklist | Intumescent Painting Checklist |  |  |  |  | Yes | Intumescent Painting Checklist | 578e5fb3-c48a-44e4-b0c3-260b4efc0269
checkpoint-status |  |  | checkpoint | Steel Erection completed and approval given to apply Intumescent Paint
checkpoint-status |  |  | checkpoint | Paint specifications and product checked
checkpoint-status |  |  | checkpoint | Paint applied using correct methodology
checkpoint-status |  |  | checkpoint | General photos, comments and observations during paint application
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Paint application complete - area inspected, checked and correct to required specification
checklist-flat |  |  | checklist | Backfill Checklist |  |  |  |  | Yes | Backfill Checklist | 5b9f438f-c1de-4e63-a188-742908209859
checkpoint-status |  |  | checkpoint | Backfill methodology and material confirmed
checkpoint-status |  |  | checkpoint | Any formwork/ debris removed from area
checkpoint-status |  |  | checkpoint | Any waterproofing/ drainage / service requirements completed and inspected
checkpoint-status |  |  | checkpoint | Approval given to commence backfill - attach any other relevant inspections and observations closed out
checkpoint-status |  |  | checkpoint | General photos and observations during backfill
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Backfill completed correctly and heights checked/ correct - desired compaction achieved
checklist-sectioned |  |  | checklist | Concrete Pour Checklist (Self Perform) |  |  |  |  | Yes | Concrete Pour Checklist (Self Perform) | 612e926c-bce9-4f0f-8faa-fb3e43064a34
checkpoint-group |  |  | section | Pour Details
checkpoint-no-status |  |  | checkpoint | Pour Details:
text | 56535b3e-d0a7-5921-adfc-f8c02e5c2a96 |  | textbox | Area to be poured:
text | a13f129e-ab15-58c3-b2ea-f102f4655927 |  | textbox | Date of pour:
checkpoint-status |  |  | checkpoint | Latest drawings available, checked and referenced
checkpoint-group |  |  | section | Formwork and Embedded Items
checkpoint-status |  |  | checkpoint | Formwork - location, height, falls and dimensions checked and accurate
checkpoint-status |  |  | checkpoint | Service penetrations formed correctly and locations checked/correct
checkpoint-status |  |  | checkpoint | All surfaces correctly prepared (e.g. joints to existing concrete, release agent to formwork etc)
checkpoint-status |  |  | checkpoint | Any control joints/ stop ends installed accurately and correctly braced
checkpoint-group |  |  | section | Reinforcing
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Sign Off
checkpoint-status |  |  | checkpoint | Size and type correct to specification
checkpoint-status |  |  | checkpoint | Reinforcing spacing and location correct
checkpoint-status |  |  | checkpoint | Specified covers checked/correct
checkpoint-status |  |  | checkpoint | Splice laps checked/correct
checkpoint-status |  |  | checkpoint | All couplers installed correctly
checkpoint-status |  |  | checkpoint | Any starter bars are installed correctly (location, size and spacing )
checkpoint-status |  |  | checkpoint | Any additional items installed/ completed (trimmer bars etc) and excess reinforcing removed
checkpoint-status |  |  | checkpoint | Welding certificates sited and attached
checkpoint-status |  |  | checkpoint | Mill certificate reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Reinforcing installed correctly to specification and ready for concrete to be placed
checkpoint-group |  |  | section | Pre-Pour Completion (Approval to pour)
checkpoint-status |  |  | checkpoint | Any waterproofing elements have been correctly installed and checked
checkpoint-status |  |  | checkpoint | Any relevant service requirements completed (locations checked and accurate)
checkpoint-status |  |  | checkpoint | Engineer inspection completed - any observations / remedial work documented and closed out
checkpoint-status |  |  | checkpoint | All relevant inspections completed and attached
checkpoint-status |  |  | checkpoint | Main contractor inspection completed - Approval given to pour concrete
checkpoint-group |  |  | section | Concrete Supplier Specifics
checkpoint-no-status |  |  | checkpoint | Concrete Supplier Specifics:
text | 4f39b43a-f59b-591f-a22e-def2e43c795f |  | textbox | Supplier Name:
text | 74ff00be-21af-5944-858e-8b549bbcb90c |  | textbox | Specified concrete strength:
text | e99293c8-715e-5ecb-ab91-81453b575302 |  | textbox | Concrete strength ordered:
text | 0d971149-5263-5e2a-b3ee-90464604b481 |  | textbox | Concrete quantity ordered:
checkpoint-status |  |  | checkpoint | Test blocks booked
checkpoint-status |  |  | checkpoint | All concrete dockets photographed/ attached
checkpoint-status |  |  | checkpoint | Concrete strength test reports attached and required concrete strength achieved
checkpoint-group |  |  | section | Concrete Distribution
checkpoint-status |  |  | checkpoint | General distribution photos, documents and observations attached
checkpoint-status |  |  | checkpoint | All concrete distributed correctly (area left clean and tidy)
checkpoint-group |  |  | section | Placement Method
checkpoint-status |  |  | checkpoint | Placement methodology confirmed and necessary plant and equipment on site
checkpoint-status |  |  | checkpoint | Heights and falls checked/confirmed before placement
button | 1cf85b65-9ecb-5aec-863e-753b0f2266f5 |  | button | Is the cover correct to specification | Yes, No
checkpoint-status |  |  | checkpoint | Heights and falls checked/ confirmed after placement
checkpoint-status |  |  | checkpoint | Any curing compound applied correctly
checkpoint-status |  |  | checkpoint | Concrete placement completed - specified level of finish achieved
checkpoint-status |  |  | checkpoint | Area left clean and tidy
checkpoint-group |  |  | section | Post Pour Checks/Sign Off
checkpoint-status |  |  | checkpoint | Any remedial work completed
checkpoint-status |  |  | checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
checklist-flat |  |  | checklist | Description/Number: |  |  |  |  | Yes | Engineer Follow Up Action | 66bf98fc-2aca-4032-a7f9-6f5ab8a7f23c
checkpoint-status |  |  | checkpoint | Follow-Up Action completed
text | ddf14301-8239-5b3b-951b-d5fa379a59cd |  | textbox | Specific Location:
text | 91c806c7-c985-559e-94d6-00a2b29bd0fd |  | textbox | Detail:
text | f17daeb2-6b36-59f2-add1-159d86b7a239 |  | textbox | Action Required:
holdpoint |  |  | signoff | Request Review
checklist-flat |  |  | checklist | Intumescent Painting |  |  |  |  | Yes | Intumescent Painting Checklist (v2) | 6d2517ca-cbf3-4317-a70a-4f60e556be32
checkpoint-status |  |  | checkpoint | Steel Erection completed and approval given to apply Intumescent Paint
checkpoint-status |  |  | checkpoint | Paint specifications and product checked
checkpoint-status |  |  | checkpoint | Paint applied using correct methodology
checkpoint-status |  |  | checkpoint | Positector readings uploaded
checkpoint-status |  |  | checkpoint | General photos, comments and observations during paint application
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Paint application complete - area inspected, checked and correct to required specification
checklist-sectioned |  |  | checklist | Aluminium Joinery / Glazing |  |  |  |  | Yes | Aluminium Joinery / Glazing | 6d40dce0-7da9-4033-8992-a41a96db9481
checkpoint-group |  |  | section | Joinery Install
checkpoint-status |  |  | checkpoint | Opening approved (ready for install)
checkpoint-status |  |  | checkpoint | Joinery in correct location
checkpoint-status |  |  | checkpoint | Appropriate fixings installed
checkpoint-status |  |  | checkpoint | Any air/ weather seals completed
checkpoint-status |  |  | checkpoint | Appropriate external flashings installed and sealed
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Inspection completed and joinery install completed as per specification
checkpoint-group |  |  | section | Final Inspection/Sign Off
checkpoint-status |  |  | checkpoint | Install completed, reviewed and approved
checkpoint-status |  |  | checkpoint | Item checked, functioning and damage free
checklist-flat |  |  | checklist | Grouting Precast Panels |  |  |  |  | Yes | Grouting Precast Panels | 6e503a83-6c9b-4e59-9f20-6e251e8f8ab1
checkpoint-status |  |  | checkpoint | Dry pack completed?
checkpoint-status |  |  | checkpoint | Pumped used?
checkpoint-status |  |  | checkpoint | Grout Used: Mapei SP (If different add in comments)
text | 268c4ed9-f86e-5e94-ae28-ea378f3a095d |  | textbox | Number of bags of grout used
checkpoint-status |  |  | checkpoint | Is the grout mixed properly? (3.0 to 3.4 Litres of Water per bag)
text | e1be3ca8-6bb5-5675-a621-83a588c2e185 |  | textbox | Number of grout tubes in panel
text | 1745a689-f647-53de-a683-96ecd30fc592 |  | textbox | Duration of pumping the whole panel
checkpoint-status |  |  | checkpoint | Did grout came out of top of dross tube?
checkpoint-status |  |  | checkpoint | No blow outs
checklist-sectioned |  |  | checklist | Nu Wall Cladding |  |  |  |  | Yes | Nu Wall Cladding | 7c895ed4-f1a1-4649-97b6-de9f78ef24e3
checkpoint-group |  |  | section | QC Summary
checkpoint-no-status |  |  | checkpoint | QC Summary
text | b788dc77-8f2e-56e7-ba1a-5c2779e36611 |  | textbox | Subcontractor/Supplier
text | e0f364de-b553-56cd-838e-4376a3c888a2 |  | textbox | Works area
text | 5a6bbcb7-08d1-5d04-8cdf-9f781f243cf6 |  | textbox | Drawings reference
text | 0ec5cd9f-d79d-5eb6-9030-0cfd4f90fe6e |  | textbox | Project specification reference
checkpoint-group |  |  | section | Precladding
checkpoint-status |  |  | checkpoint | RAB and timber is dry prior to apply revealshield
label | d428cdad-4895-5648-a3f4-b332175d6819 |  | note | Photos
checkpoint-status |  |  | checkpoint | Revealshield is applied correctly (80mm overlap) and as per drawing
label | a23f1fe9-795c-59c0-964e-b4f7889eb032 |  | note | Photos
checkpoint-status |  |  | checkpoint | Liquidflash is apply around the window opening andany other location required
label | 12f16471-76bb-53c5-929d-85bf18234763 |  | note | Photos
checkpoint-status |  |  | checkpoint | Sealant and flashing tape is applied ( brackets fixed on RAB/ over the top of pressure bar...)
label | c4dc960c-6c9a-5484-af17-5cffed30c4b4 |  | note | Photos
checkpoint-group |  |  | section | Cladding - Nu Wall
checkpoint-status |  |  | checkpoint | Façade bottom flashing detail installed (equal angle/ steel angle/ vermin/J flashing..)
label | f4a984fa-7527-57fe-93a2-9b91d926fec6 |  | note | Photos
checkpoint-status |  |  | checkpoint | Aluminum batten installed as per spec (600mm/enough fixing/location on windows sides)
label | 4ac384b7-a950-5902-b560-dce0eb0c47c5 |  | note | Photos
checkpoint-status |  |  | checkpoint | Fixings installed as per product installation guide
label | 134a3e91-3894-55d0-9a92-2f9a29853994 |  | note | Photos
button | 0dc1a7b3-6e37-5213-ad33-deeb49604dd6 |  | button | Flashing tapes installed as per installation guide | Timber,Concrete,Steel
label | b3170e02-a2d7-59ad-a4ab-fd708124cf1f |  | note | Photos
checkpoint-status |  |  | checkpoint | Seismic movement join in correctly
label | ebed63aa-9efb-5e1e-bf1e-331c9a5b3fc8 |  | note | Photos
checkpoint-status |  |  | checkpoint | Check colour and type of Nu wall
label | af2a4e6e-6b1f-5a3c-a27c-9bfa6f860f58 |  | note | Photos
checkpoint-status |  |  | checkpoint | Vertical sheet flashings installed
label | b9c61898-8679-51b2-8829-523ff3876ad5 |  | note | Photos
checkpoint-status |  |  | checkpoint | Interstorey flashing/ head flashing/ sill flashing installed correctly - with soaker and sealant
label | 59b11c5b-c721-51e9-a103-0f33837a12b0 |  | note | Photos
checkpoint-status |  |  | checkpoint | Corners flashing if required on
checkpoint-status |  |  | checkpoint | Windows jamb cap align with vertical jointer cap -detail 5-A330
checkpoint-status |  |  | checkpoint | Flashing tape over flashing (head flashing, interstorey flashing)
label | 153a33f1-60e5-58d8-a7d8-a7187b0d6d87 |  | note | Photos
checkpoint-status |  |  | checkpoint | Top flashing detail complete with flashing tape over it
checkpoint-status |  |  | checkpoint | Is it complete and tightly fitted
label | 2560df36-3e6b-5fd7-bda1-39a80880603c |  | note | Photos
checkpoint-group |  |  | section | Services
checkpoint-status |  |  | checkpoint | Check if services penetrating the RAB are required in this location
label | d7e52687-954f-5735-856f-a4d3b93772a0 |  | note | Photos
checkpoint-status |  |  | checkpoint | Security services installed to correct locations
label | 1183022c-c75c-566a-af9f-4386d191d1a5 |  | note | Photos
checkpoint-status |  |  | checkpoint | Plumbing services installed to correct locations
label | a6bf809b-1f3c-5e33-9fdb-d0e9ec6f7d2c |  | note | Photos
checkpoint-status |  |  | checkpoint | Fire services installed to correct loctions
label | 0deb001d-8e9d-5f01-b39b-7a7c07ea168d |  | note | Photos
checkpoint-status |  |  | checkpoint | Lighting and power services installed to correct locations
label | 71e8717b-0930-5c87-8aae-88f367cfe51c |  | note | Photos
checkpoint-status |  |  | checkpoint | Mechanical services installed to correct locations
checkpoint-group |  |  | section | Final approvals and holdpoints
checkpoint-status |  |  | checkpoint | Hold point - Sub contractor QA
label | 5324250e-4be7-5675-b916-5b35624d3fa1 |  | note | QA REPORT
holdpoint |  |  | signoff | Company QA Check
checkpoint-status |  |  | checkpoint | Engineer Inspections
label | d1010b87-f397-5ff8-950f-26fb2c0a8146 |  | note | SITE REPORTS
checkpoint-status |  |  | checkpoint | Council Inspections
label | 692c7767-d92e-5079-b1c2-a17f1f4cbbb6 |  | note | INSPECTION REPORT
checklist-flat |  |  | checklist | Watermain - Pipeline Installation Checklist |  |  |  |  | Yes | Watermain - Pipeline Installation Checklist | 7c8dfb97-74de-4dee-9dd4-54030d369789
checkpoint-status |  |  | checkpoint | Latest construction drawings referenced and followed
text | d9771d09-b06f-5465-97d3-685850b7ffa2 |  | textbox | Drawing & Revision Number
checkpoint-status |  |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status |  |  | checkpoint | Ground Conditions Checked & Acceptable
checkpoint-status |  |  | checkpoint | Bedding depth and material correct (photo required)
checkpoint-status |  |  | checkpoint | Correct pipe (size, material & class) laid to specified level, grade and jointed as specified
text | 747d5e18-13d5-5ff3-95ab-d90e6ad13d64 |  | textbox | Design length of pipe (m)
text | c28370f9-338c-5349-8fec-5c2178b5696b |  | textbox | Length of pipe installed (m)
checkpoint-status |  |  | checkpoint | Connections complete and approved (photo required)
checkpoint-status |  |  | checkpoint | Relevant test completed (photos required)
checkpoint-status |  |  | checkpoint | Backfill completed & compacted as specified
checkpoint-status |  |  | checkpoint | Relevant tests, photos & as-built information attached
checklist-sectioned |  |  | checklist | Shroud & Finns |  |  |  |  | Yes | Shroud & Finns | 84756185-a6f0-4b7d-8d4f-167485e06b84
checkpoint-group |  |  | section | QC Summary
checkpoint-no-status |  |  | checkpoint | QC Summary
text | be104312-4d2a-51a0-8c7d-1ad0579fedee |  | textbox | Subcontractor/Supplier
text | b6af4c2d-eba7-5b36-8877-e37351b5ff3b |  | textbox | Works area
text | 5e7f15d0-df69-5613-a9be-c9d03a93af1e |  | textbox | Drawings reference
text | 18c041d2-d8a1-5cc7-8944-fcd1ddca78e8 |  | textbox | Project specification reference
checkpoint-group |  |  | section | Precladding
checkpoint-status |  |  | checkpoint | RAB and timber is dry prior to apply revalshield
label | b297b1c9-30ea-5a9c-996e-e54823979439 |  | note | Photos
checkpoint-status |  |  | checkpoint | Revealshield is applied correctly (80mm overlap) and as per drawing
label | 24c2e58b-209d-5d2f-b202-6c5e575cc83c |  | note | Photos
checkpoint-status |  |  | checkpoint | Liquidflash is apply around the window opening andany other location required
label | 95b055ef-ae39-5db6-a80e-8883a437d1da |  | note | Photos
checkpoint-status |  |  | checkpoint | Sealant and flashing tape is applied ( brackets fixed on RAB/ over the top of pressure bar...)
label | cd9ef285-d527-5c5e-b1e5-60193b2a9003 |  | note | Photos
checkpoint-group |  |  | section | Shroud
checkpoint-status |  |  | checkpoint | Brackets in and leveled
label | 1f9c9cb1-da79-5819-a0cb-f0d356ec756d |  | note | Photos
checkpoint-status |  |  | checkpoint | Brackets setout correct
label | c8a6878f-8039-584b-9129-a4253f4b7493 |  | note | Photos
checkpoint-status |  |  | checkpoint | Anodised Frost Ultra black check
label | a1b27ded-062f-51ac-9eb3-7e4802e85d55 |  | note | Photos
checkpoint-status |  |  | checkpoint | Bottom and top shroud leveled
label | 82827932-7e41-5520-bc61-50beec232d34 |  | note | Photos
checkpoint-status |  |  | checkpoint | Side shroud plumb
label | 254ea561-b604-5243-ba5c-65ef5af80bc4 |  | note | Photos
checkpoint-status |  |  | checkpoint | Fixing as per drawings
label | c0248300-5186-54e8-b60e-46852ed3e6b0 |  | note | Photos
checkpoint-status |  |  | checkpoint | Join, gap, notch, all detail as per drawings
label | 11224243-61f8-58c0-a2b7-eada85f714fc |  | note | Photos
checkpoint-group |  |  | section | Finns
checkpoint-status |  |  | checkpoint | Brackets in
label | 32a03a7e-af9f-52c0-9b5c-de899ff0099f |  | note | Photos
checkpoint-status |  |  | checkpoint | Anodised Frost Ultra black check
label | 99654c42-a4d9-51a3-bede-6fc476eb0b38 |  | note | Photos
checkpoint-status |  |  | checkpoint | Fines installed as per drawings (lengh, gap, fixing detail )
label | 62afadae-5f35-508c-b9a5-a4e7cb9fea4a |  | note | Photos
checkpoint-status |  |  | checkpoint | Fixing as per drawings
label | ebfda595-e827-5af3-8d19-4847a32bc66c |  | note | Photos
checkpoint-group |  |  | section | Final approvals and holdpoints
checkpoint-status |  |  | checkpoint | Hold point - Sub contractor QA
label | e1eefd4d-4216-5240-a9a2-0fc3c55837aa |  | note | QA REPORT
holdpoint |  |  | signoff | Company QA Check
checkpoint-status |  |  | checkpoint | Engineer Inspections
label | 60a8c94f-1dec-5cf5-bd4a-1d6a6da442c7 |  | note | SITE REPORTS
checkpoint-status |  |  | checkpoint | Council Inspections
label | 8e2de418-acd0-57e8-ac3e-bdb5ae259190 |  | note | INSPECTION REPORT
checklist-sectioned |  |  | checklist | Curtain Walls |  |  |  |  | Yes | Curtain Walls | 85dd7367-9870-46ab-903c-f24291be3426
checkpoint-group |  |  | section | Pre-construction
checkpoint-status |  |  | checkpoint | Inspected and accepted the work area and surfaces ready to commence work
checkpoint-status |  |  | checkpoint | Confirmed site storage requirements, packaging and preservation
checkpoint-group |  |  | section | Opening Handover
checkpoint-status |  |  | checkpoint | Visual check of opening is completed
checkpoint-status |  |  | checkpoint | Steel flat plates or sill have been installed correctly
checkpoint-status |  |  | checkpoint | Trade inspected and opening handed over
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Stud welds completed in the area
checkpoint-status |  |  | checkpoint | Brackets installed and welded off
checkpoint-status |  |  | checkpoint | Curtain wall panel installed correctly
checkpoint-status |  |  | checkpoint | 150mm depth rockwool fire insulation installed with 33% compression with 50mm LG zed clips at 600mm centers
checkpoint-status |  |  | checkpoint | Hilti CFS-SP Sil silicone based joint sealant spray min 15mm overlap with 2mm min film thickness
checkpoint-status |  |  | checkpoint | 1.2mm THK continuous galvanised pressing on top of HILTI spray
checkpoint-status |  |  | checkpoint | Aluminum flashing installed and sealed with silicone
checkpoint-group |  |  | section | Airtightness
checkpoint-status |  |  | checkpoint | Top and bottom of all mullions capped and sealed
checkpoint-status |  |  | checkpoint | Smoke seals are sealed with a light coloured caulk
checkpoint-status |  |  | checkpoint | Beware of smoke seals near columns where the installers are restricted in applying caulk
checkpoint-group |  |  | section | Completion
checkpoint-status |  |  | checkpoint | Removal of temporary fixings, spacers & packers
checkpoint-status |  |  | checkpoint | Panel cleaned to remove installation marks
checkpoint-status |  |  | checkpoint | Panel surface are defects free
checkpoint-group |  |  | section | Final Inspection
checkpoint-status |  |  | checkpoint | All defects complete and “signed off”
checkpoint-status |  |  | checkpoint | Issued Façade Maintenance Manuals, service agreements & all warrantees and guarantees
checkpoint-group |  |  | section | Subcontractor Sign Off
checkpoint-status |  |  | checkpoint | Subcontractor Sign Off
checklist-flat |  |  | checklist | Flooring |  |  |  |  | Yes | Flooring | 88d090ae-0b7c-4c6c-ac5b-e46cb473bff6
checkpoint-status |  |  | checkpoint | Floor substrate clean, dry, ready for finishes
checkpoint-status |  |  | checkpoint | Finishes as per architectural plans
checkpoint-status |  |  | checkpoint | Trim thresholds junction as per detail
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checklist-flat |  |  | checklist | Detailed Excavation Checklist |  |  |  |  | Yes | Detailed Excavation Checklist | 8b22d857-1852-4c8a-813b-b93a7c88ee80
checkpoint-status |  |  | checkpoint | Location accurate
checkpoint-status |  |  | checkpoint | Depth correct (allow for site concrete if required)
checkpoint-status |  |  | checkpoint | Width correct (allow for boxing if required)
checkpoint-status |  |  | checkpoint | Any relevant excavation for services is completed and accurate
checkpoint-status |  |  | checkpoint | Excess Material Cleaned up and removed as required
checkpoint-status |  |  | checkpoint | Detailed excavation completed, reviewed and approved
checklist-flat |  |  | checklist | Drypacking and Grouting |  |  |  |  | Yes | Drypacking and Grouting | 96925b15-9f06-4bd6-a2cf-f61bb79d3943
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Preparation / Substrate acceptable
checkpoint-status |  |  | checkpoint | Installed as per installation requirements
checkpoint-status |  |  | checkpoint | General photos/comments during install
checkpoint-status |  |  | checkpoint | Any inspections / observations documented, reviewed and closed out
checkpoint-status |  |  | checkpoint | All drypacking and grouting completed , reviewed and approved to meet required specifications
checklist-flat |  |  | checklist | Envelope - Parapet |  |  |  |  | Yes | Envelope - Parapet | 982fe59e-2662-49c6-af41-6218a5de4418
checkpoint-status |  |  | checkpoint | Structural stee level and in correct location
checkpoint-status |  |  | checkpoint | Dry packing complete
checkpoint-status |  |  | checkpoint | Timber/DPC adequately fixed to framing
checkpoint-status |  |  | checkpoint | Timber framing @ 400 c/c
checkpoint-status |  |  | checkpoint | Ply correctly fixed (21mm H3.2)
checkpoint-status |  |  | checkpoint | Insulation correctly installed
checkpoint-status |  |  | checkpoint | Curtain wall bracket checked
checkpoint-status |  |  | checkpoint | Curtain wall checked
checkpoint-status |  |  | checkpoint | Photograph curtain wall junctions
checkpoint-status |  |  | checkpoint | Steel top plate (parapet build up)
checkpoint-status |  |  | checkpoint | Parapet ply installed (21mm H3.2)
checkpoint-status |  |  | checkpoint | EDPM installed to parapet
checkpoint-status |  |  | checkpoint | Integrity of the EPDM airseals. All corner junctions must be photographed and signed off
checkpoint-status |  |  | checkpoint | The connection between the EPDM airseal and the EQUUS SOPREMA DUOTHERM warm roof cap sheet requires sign off.
checkpoint-status |  |  | checkpoint | Membrane installed to EPDM (check laps and junctions 150mm to roofing)
checkpoint-status |  |  | checkpoint | Integrity of the membrane to the EPDM. All corner junctions must be photographed and signed off
checkpoint-status |  |  | checkpoint | Cap flashing installed
checklist-flat |  |  | checklist | Slab Penetration(s) Checklist |  |  |  |  | Yes | Slab Penetration(s) Checklist | 98bdb711-2ed1-4b0a-9944-41e98ad67662
checkpoint-status |  |  | checkpoint | Area clear and ready for work (accessible & acceptable)
boolean | 92ac45ae-a442-5eb2-9c2e-c3207c3808b4 |  | tickbox | Grid lines marked out available
label | ef78a869-d58d-5412-a786-b884bb776e9a |  | note | Any issues "Fail" and send report to Kalmar
checkpoint-status |  |  | checkpoint | Slab Penetration(s) Completed
label | a4bcf11b-6fd1-5554-9ae3-31db62b3ed5e |  | note | Select "PASS" once all slab penetrations are installed, double checked & mark up/photos attached
text | 0d381cb7-eb55-5922-b304-6d4860703247 |  | textbox | Drawing number used for set out
text | 82e56c06-85c6-5b93-ae25-d0860c2594a0 |  | textbox | Penetration sizes
text | 47e5f953-fb7c-5373-9ff4-db4a469d815e |  | textbox | Total number of penetrations installed
boolean | 18d88df0-f248-5057-8a14-72ca9ae3e33b |  | tickbox | Measurements double checked
boolean | 56a54457-a49e-5d3c-a1de-2a5dda535758 |  | tickbox | Marked up drawing attached
checklist-flat |  |  | checklist | Shotcrete Fill Works Checklist |  |  |  |  | Yes | Shotcrete Fill Works Checklist | 9a209efb-31eb-4d67-864d-38849fd15c70
checkpoint-status |  |  | checkpoint | Specified the cut upper or lower cut and position (grid lines)
checkpoint-status |  |  | checkpoint | Imported fill material checked either GAP65 hardfill-HOROKIWI or RM65 hardfill-Winstones belmont
checkpoint-status |  |  | checkpoint | Every 500mm layer plateform checked
checkpoint-status |  |  | checkpoint | Compaction test with Mats check and passed
checkpoint-status |  |  | checkpoint | As built location of the cut confirmed
checkpoint-status |  |  | checkpoint | As built the slope either 40deg or 60deg
checkpoint-status |  |  | checkpoint | Progress photos
checklist-flat |  |  | checklist | Bore Drain Checklist |  |  |  |  | Yes | Bore Drain Checklist | 9baf8235-8c5a-48a6-8670-3b7e4a48268d
checkpoint-status |  |  | checkpoint | Set out confirmed
checkpoint-status |  |  | checkpoint | Coordinate with pile locations
checkpoint-status |  |  | checkpoint | General photos, comments and observations during drilling
checklist-flat |  |  | checklist | Ground Anchor Checklist |  |  |  |  | Yes | Ground Anchor Checklist | 9ecbef25-39ec-42d9-8101-eda57339d4ac
checkpoint-status |  |  | checkpoint | Set out confirmed
checkpoint-status |  |  | checkpoint | Drilling angle confirmed
checkpoint-status |  |  | checkpoint | Coordinate with pile locations
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Load testing complete
checkpoint-status |  |  | checkpoint | General photos, comments and observations during drilling
checklist-flat |  |  | checklist | Roof Decks |  |  |  |  | Yes | Roof Decks | a4cb475c-0923-48bb-bef2-31d38d5a125d
checkpoint-status |  |  | checkpoint | Safety mesh and cavity batten installed correctly
checkpoint-status |  |  | checkpoint | Outside box gutter with eave flashing installed - if required
checkpoint-status |  |  | checkpoint | Covertek 407 on safety mesh installed as per drawing
checkpoint-status |  |  | checkpoint | Revealshield/ flashing tape dressed over covertek as per drawing
checkpoint-status |  |  | checkpoint | Eco foam closure strip installed
checkpoint-status |  |  | checkpoint | Roof metal decking sheet installed and screwed correctly & colorcote – Off white checked
checkpoint-status |  |  | checkpoint | Side flashing 0.55BMT coil coated steel installed & colorcote - off white
checkpoint-status |  |  | checkpoint | Flashing tape over Apron flashing - Installed
checkpoint-status |  |  | checkpoint | No damage, scratches - hand over to next trade approved
checklist-sectioned |  |  | checklist | Sumner Schist Stone Cladding |  |  |  |  | Yes | Sumner Schist Stone Cladding | ac5a1afd-4a3a-416c-953c-cf97f02e9788
checkpoint-group |  |  | section | QC Summary
checkpoint-no-status |  |  | checkpoint | QC Summary
text | 82b1d8e1-a124-5fa3-af99-c39da9e4b998 |  | textbox | Subcontractor/Supplier
text | a18d1c32-200e-58f0-b024-fce23ef020a3 |  | textbox | Works area
text | 99f32d87-d469-58a0-839e-af7901638a6f |  | textbox | Drawings reference
text | d1deadd2-7ebc-5562-9e7b-79f395c23f86 |  | textbox | Project specification reference
checkpoint-group |  |  | section | Precladding
checkpoint-status |  |  | checkpoint | RAB and timber is dry prior to apply revalshield
label | d7809b79-4225-52b4-bc9b-c02385554aef |  | note | Photos
checkpoint-status |  |  | checkpoint | Revealshield is applied correctly (80mm overlap) and as per drawing
label | 35575107-3f69-5513-b1de-48f359c610fb |  | note | Photos
checkpoint-status |  |  | checkpoint | Liquidflash is apply around the window opening andany other location required
label | ed08d027-f9d1-5c23-8c29-45c8aca4b512 |  | note | Photos
checkpoint-status |  |  | checkpoint | Sealant and flashing tape is applied ( brackets fixed on RAB/ over the top of pressure bar...)
label | f53749aa-3a8e-53f8-9e82-f28a19a8fccc |  | note | Photos
checkpoint-group |  |  | section | Sumner Schist - Stone Cladding
checkpoint-status |  |  | checkpoint | Installation of Cavity Batten as per drawing
label | d039d756-1603-574a-9535-a293dc187a17 |  | note | Photos
checkpoint-status |  |  | checkpoint | Movement join as per drawing and set out
label | 3d9e790e-d130-5534-81d7-0b9aa050234a |  | note | Photos
checkpoint-status |  |  | checkpoint | Sumner schist 9mm board installed as per manual
label | fdddc186-4d25-5987-bdcc-27f3ae6a068f |  | note | Photos
checkpoint-status |  |  | checkpoint | Sumner stone primer and stone installed as per specification
label | c7234151-4561-5c13-8aa9-8f3b1d8ce474 |  | note | Photos
checkpoint-status |  |  | checkpoint | Backing rod/ sealant applied
label | 3c840c97-fa2f-5a98-9f33-6de82e801f0d |  | note | Photos
checkpoint-status |  |  | checkpoint | Windows sill checked
label | 6a7a0b74-87f6-5b40-8fa8-567e0fe2bd11 |  | note | Photos
checkpoint-status |  |  | checkpoint | Connection to ground checked
label | b1d3c83d-243d-5265-9652-43193ad0200d |  | note | Photos
checkpoint-group |  |  | section | Services
checkpoint-status |  |  | checkpoint | Check if services penetrating the RAB are required in this location
label | 689ef172-7833-58fe-87d9-21463820f731 |  | note | Photos
checkpoint-status |  |  | checkpoint | Security services installed to correct locations
label | 7677586a-7404-5963-af95-68e8ab732a98 |  | note | Photos
checkpoint-status |  |  | checkpoint | Plumbing services installed to correct locations
label | 92729d83-25ef-5507-b69f-51390bf7be01 |  | note | Photos
checkpoint-status |  |  | checkpoint | Fire services installed to correct loctions
label | ce3cb479-40db-59b9-a5c4-c95f0c1a7606 |  | note | Photos
checkpoint-status |  |  | checkpoint | Lighting and power services installed to correct locations
label | 2529d919-4c0e-59cd-b631-c64bfbefcda6 |  | note | Photos
checkpoint-status |  |  | checkpoint | Mechanical services installed to correct locations
label | 82a1c704-3a75-5207-9775-755c062bc714 |  | note | Photos
checkpoint-group |  |  | section | Final approvals and holdpoints
checkpoint-status |  |  | checkpoint | Hold point - Sub contractor QA
label | a89ab464-9871-572c-80c8-6782340a5875 |  | note | QA REPORT
holdpoint |  |  | signoff | Company QA Check
checkpoint-status |  |  | checkpoint | Engineer Inspections
label | d59f0d2d-88b0-55fb-8331-7107df8cb175 |  | note | SITE REPORTS
checkpoint-status |  |  | checkpoint | Council Inspections
label | 3652b802-6089-5e9d-859b-d12738fb7c26 |  | note | INSPECTION REPORT
checklist-flat |  |  | checklist | Grouting Checklist |  |  |  |  | Yes | Grouting Checklist | b0179418-bc04-4424-bfff-68d97253f7ea
checkpoint-status |  |  | checkpoint | Dry pack completed?
checkpoint-status |  |  | checkpoint | Pumped used?
checkpoint-status |  |  | checkpoint | Grout Used: Mapei SP (If different add in comments)
text | 93cdd564-7873-50ad-a6ea-b748040d5270 |  | textbox | Number of bags of grout used
checkpoint-status |  |  | checkpoint | Is the grout mixed properly? (3.0 to 3.4 Litres of Water per bag)
text | ecd64d6e-531d-5263-9781-a4b1eb8c8644 |  | textbox | Number of grout tubes in panel
text | 399d2858-213f-5223-92f5-3e5aff18d5db |  | textbox | Duration of pumping the whole panel
checkpoint-status |  |  | checkpoint | Did grout came out of top of dross tube?
checkpoint-status |  |  | checkpoint | No blow outs
checklist-flat |  |  | checklist | Site Establishment Checklist |  |  |  |  | Yes | Site Establishment Checklist | b0c4bf3d-b0a1-4b47-b50c-3b4685de828c
checkpoint-status |  |  | checkpoint | Any relevant dilapidation requirements captured
checkpoint-status |  |  | checkpoint | Attach relevant site establishment photos/ documents
checkpoint-status |  |  | checkpoint | Appropriate isolation of site (hoardings / fencing)
checkpoint-status |  |  | checkpoint | Sufficient & Appropriate site/H&S signage erected
checkpoint-status |  |  | checkpoint | Site establishment completed
checklist-flat |  |  | checklist | Envelope - Warm roof |  |  |  |  | Yes | Envelope - Warm roof | b1bfe9dd-d924-466a-b7e9-eb6232461b82
checkpoint-status |  |  | checkpoint | Substrate clear of debris (no sharp edges/ air pockets)
checkpoint-status |  |  | checkpoint | Vapour barrier installed (up parapet)
checkpoint-status |  |  | checkpoint | PIR insulation (brick pattern, tight joint)
checkpoint-status |  |  | checkpoint | Cement board (Perma base Dek correct fixing)
checkpoint-status |  |  | checkpoint | Soprema Sopradere quick primer
checkpoint-status |  |  | checkpoint | Membrane installed (80mm min lap)
checkpoint-status |  |  | checkpoint | Duo Capsheet installed
checkpoint-status |  |  | checkpoint | Internal gutters (ply installed, lap of membrane and capsheet into drain)
checkpoint-status |  |  | checkpoint | Seal around drain
checklist-flat |  |  | checklist | Final Sign Off |  |  |  |  | Yes | Final Sign Off | b4ac42ea-5913-401c-8068-7ef79c4b6af7
checkpoint-status |  |  | checkpoint | Doors Installed including drop down seals if applicable
checkpoint-status |  |  | checkpoint | Hardware as per approved schedule
checkpoint-status |  |  | checkpoint | Architraves and skirtings installed
checkpoint-status |  |  | checkpoint | Electrical Power/Lighting second fix installed
checkpoint-status |  |  | checkpoint | Sprinkler/Alarm second fix installed
checkpoint-status |  |  | checkpoint | Security second fix installed
checkpoint-status |  |  | checkpoint | Data second fix installed
checkpoint-status |  |  | checkpoint | HVAC second fix installed
checkpoint-status |  |  | checkpoint | Floor finishes installed as per architectural plan
checkpoint-status |  |  | checkpoint | Paint correct colour
checkpoint-status |  |  | checkpoint | Door signage installed
checkpoint-status |  |  | checkpoint | Manifestations on glazing
checkpoint-status |  |  | checkpoint | Joinery installed correctly
checklist-sectioned |  |  | checklist | Envelope - Sills |  |  |  |  | Yes | Envelope - Sills | bc0cef08-3ee9-4cd5-9b7c-a6f6b373f0db
checkpoint-group |  |  | section | Sills
checkpoint-status |  |  | checkpoint | No sharp edges
checkpoint-status |  |  | checkpoint | Substrate applied (membrane applied)
checkpoint-status |  |  | checkpoint | Sill try to be sealed (check for backing rod and sealant)
checkpoint-status |  |  | checkpoint | Sill tray fixed at correct centres
checkpoint-status |  |  | checkpoint | Check workmanship of junctions and seals
checkpoint-status |  |  | checkpoint | Check lap of membrane
checkpoint-group |  |  | section | Airtightness
checkpoint-status |  |  | checkpoint | All unexposed caulking should use light colour caulk (eg, Light gray, or white)
checkpoint-status |  |  | checkpoint | Check corner junctions for quality. (Typically, the lab test only covers typical panels.) Particularly without factory made corners.
checkpoint-status |  |  | checkpoint | Mounting brackets sealed to the slab with caulking, tolerance slots should also be sealed
checklist-sectioned |  |  | checklist | Concrete Pour |  |  |  |  | Yes | Concrete Pour | bc4ad00e-4303-4b81-a547-e78b6cc2d3f9
checkpoint-group |  |  | section | Formwork and Embedded Items
checkpoint-status |  |  | checkpoint | Latest drawings available, checked and referenced
text | 38ed2830-3628-57c7-887b-5ac519a19c13 |  | textbox | Grid Line
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Grids and RLs clearly marked for reference
checkpoint-status |  |  | checkpoint | Formwork - location, height, falls and dimensions checked and accurate
checkpoint-status |  |  | checkpoint | Formwork sufficiently fixed and braced (incl any propping)
checkpoint-status |  |  | checkpoint | Shear studs installed as-per shop drawings & check ring test
checkpoint-status |  |  | checkpoint | Any rebates/ nibs / cast in items are correctly positioned, sized and appropriately fixed in place
checkpoint-status |  |  | checkpoint | Service penetrations formed correctly and locations checked/correct
checkpoint-status |  |  | checkpoint | All surfaces correctly prepared (e.g joints to exisiting concrete, release agent to formwork etc)
checkpoint-status |  |  | checkpoint | Any control joints/ stop ends installed accurately and correctly braced
checkpoint-status |  |  | checkpoint | Any additional formwork photos and observations
checkpoint-status |  |  | checkpoint | All formwork elements completed and ready for concrete pour ( excess debris removed )
checkpoint-group |  |  | section | Reinforcing
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Size and type correct to specification
checkpoint-status |  |  | checkpoint | Reinforcing spacing and location correct
checkpoint-status |  |  | checkpoint | Specified covers checked/correct
checkpoint-status |  |  | checkpoint | Splice laps checked/correct
checkpoint-status |  |  | checkpoint | Any starter bars are installed correctly (location, size and spacing )
checkpoint-status |  |  | checkpoint | Any additional items installed/ completed (trimmer bars etc) and excess reinforcing removed
checkpoint-status |  |  | checkpoint | Reinforcing installed correctly to specification and ready for concrete to be placed
checkpoint-group |  |  | section | Pre-Pour Completion (Approval to pour)
checkpoint-status |  |  | checkpoint | Engineer inspection completed - any observations / remedial work documented and closed out
checkpoint-status |  |  | checkpoint | Council inspection completed and attached
checkpoint-status |  |  | checkpoint | All relevant inspections completed and attached
checkpoint-status |  |  | checkpoint | Main contractor inspection completed - Approval given to pour concrete
checkpoint-status |  |  | checkpoint | Heights and falls checked/confirmed before placement
button | 9c03fa07-0113-54c7-b57c-a794f6ecaf35 |  | button | Is the cover correct to specification | Yes,No
checkpoint-status |  |  | checkpoint | General photos and observations of concrete placement attached
checkpoint-group |  |  | section | Pour / Post-Pour Checks/Sign Off
checkpoint-status |  |  | checkpoint | Concrete checked on arrival & correct (slump, MPa etc)
checkpoint-status |  |  | checkpoint | Heights and falls checked/ confirmed after placement
checkpoint-status |  |  | checkpoint | Any curing compound applied correctly
checkpoint-status |  |  | checkpoint | Concrete surface to specifications
checkpoint-status |  |  | checkpoint | Area left clean and tidy
checkpoint-status |  |  | checkpoint | Any remedial work completed
checkpoint-status |  |  | checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
checklist-sectioned |  |  | checklist | Core Water Checklist |  |  |  |  | Yes | Core Water Checklist | bd67627c-844c-4e68-b2e1-d8272b8a1014
checkpoint-group |  |  | section | Cold water main
checkpoint-status |  |  | checkpoint | Connections brazed correctly
checkpoint-status |  |  | checkpoint | Clip Spacing to manufacturer's specs horizontal/ vertical
checkpoint-status |  |  | checkpoint | Valves fitted correctly
checkpoint-group |  |  | section | Hot water main
checkpoint-status |  |  | checkpoint | Connections welded correctly
checkpoint-status |  |  | checkpoint | Clip spacing to manufacturer's specs horizontal/ vertical
checkpoint-status |  |  | checkpoint | Expansion allowed for
checkpoint-status |  |  | checkpoint | Lagging installed and neat
checkpoint-status |  |  | checkpoint | Valves fitted correctly
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Open ends of riser capped for testing
checkpoint-status |  |  | checkpoint | Checked for crossovers
checkpoint-status |  |  | checkpoint | Tidy work areas
checkpoint-status |  |  | checkpoint | Allowance for expansion
checkpoint-status |  |  | checkpoint | Pressure test to 1500kpa for 30mins
checkpoint-status |  |  | checkpoint | Visual check (for leeks from valves, tees, saddles, etc)
checkpoint-status |  |  | checkpoint | Seismic bracing for pipework longitude and latitude
checkpoint-status |  |  | checkpoint | Lateral labelling of pipework backflow devices fitted
checkpoint-status |  |  | checkpoint | Pre Line Inspection Passed
checkpoint-status |  |  | checkpoint | Installers name & date works completed
text | 6167ad08-2200-5b1a-abfa-28d57fb211ec |  | textbox | Installers name
text | b112e53f-1734-5c06-a984-5f530544a185 |  | textbox | Date:
checkpoint-status |  |  | checkpoint | Tested by & date
text | 5f0e8bb2-7a8b-5cb3-a094-b678f15d8ac2 |  | textbox | Tested by:
text | 3bf8abc6-5efb-5643-aa08-ee47ad07a141 |  | textbox | Date tested:
checkpoint-status |  |  | checkpoint | Council inspector sign off and date
checklist-flat |  |  | checklist | Service Location / Isolation Checklist |  |  |  |  | Yes | Service Location / Isolation Checklist | be81f86d-25e9-4d97-8c41-d2d21f166aae
checkpoint-status |  |  | checkpoint | Power located/Isolated
checkpoint-status |  |  | checkpoint | Hydraulic services located/isolated
checkpoint-status |  |  | checkpoint | Gas located/isolated
checkpoint-status |  |  | checkpoint | Telecommunication/Fibre located/isolated
checkpoint-status |  |  | checkpoint | Any other relevant services located/ isolated
checkpoint-status |  |  | checkpoint | All Services located/ isolated (Pass once all services are located/isolated)
checklist-flat |  |  | checklist | Envelope - Anchors |  |  |  |  | Yes | Envelope - Anchors | bffcaf95-6906-4bd6-90b3-174b902e3e1b
checkpoint-status |  |  | checkpoint | Installed as per drwg
checkpoint-status |  |  | checkpoint | sealed/waterproofed
checkpoint-status |  |  | checkpoint | General photos, comments and observations during paint application
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checklist-sectioned |  |  | checklist | Wall Preline |  |  |  |  | Yes | Wall Preline | c562b382-c53a-47b1-93fd-b0eea059984f
checkpoint-group |  |  | section | Interior Framing
checkpoint-status |  |  | checkpoint | Reference Drawings ( add numbers and revisions)
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All framing setout correctly & surveyed in respective area
boolean | c5461e37-9dd3-5471-9ca6-290d56001b84 |  | tickbox | Spot checks on frames for square
boolean | 77546d39-aa58-5b0d-bd28-c7ff65566f29 |  | tickbox | Spot checks on frame level
boolean | aabbc6a5-b4ba-5559-87e0-08bb26e4882e |  | tickbox | Fixings are correct including seismic requirements
boolean | dffceefc-1ab2-5a28-89ac-70d17825a1e7 |  | tickbox | Service Nogs installed
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Plumbing Walls First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Plumbing install First fix complete - checks done based on elevations of current drawings
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Council inspection and testing complete and signed off
checkpoint-group |  |  | section | Fire Protection Walls (Alarms) First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | First Fix checks with Subcontractor (alarms)
checkpoint-status |  |  | checkpoint | All required 1st fix testing complete
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Mechanical Services Wall First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | First Fix checks with subcontractor
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Electrical Wall First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | First Fix checks with Subcontractor
checkpoint-status |  |  | checkpoint | All required first fix testing complete
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Data Wall First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All required first fix completed
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Security Wall First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All required first fix completed
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | AV Wall First Fix
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | All required first fix completed
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Insulation/Acoustic
checkpoint-status |  |  | checkpoint | Trades QA received, reviewed, attached and approved
checkpoint-status |  |  | checkpoint | Spot checks on correct product
checkpoint-status |  |  | checkpoint | Spot checks on correct R value
checkpoint-status |  |  | checkpoint | Fitting Snug
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-group |  |  | section | Council Sign Off
checkpoint-status |  |  | checkpoint | Council preline inspection passed
checklist-sectioned |  |  | checklist | Sewer - Pipeline Installation Checklist |  |  |  |  | Yes | Sewer - Pipeline Installation Checklist | cad3db28-e69f-4b8d-a89b-1879bda61257
checkpoint-group |  |  | section | Pipe Laying
checkpoint-status |  |  | checkpoint | Latest consented drawings
text | 4bfc2356-d3c7-5325-8343-74829401697c |  | textbox | Drawing Ref No.
checkpoint-status |  |  | checkpoint | Setout completed checked and accurate
checkpoint-status |  |  | checkpoint | Excavation Accurate - Location & Depth
checkpoint-status |  |  | checkpoint | Ground Conditions Checked & Acceptable
checkpoint-status |  |  | checkpoint | Bedding depth and material correct
checkpoint-status |  |  | checkpoint | Correct pipe laid to specified level and grade (all joints sealed correctly as specified)
text | 4eff6175-3e51-5242-a8d6-8f3165d591f9 |  | textbox | Start Invert
text | e83881f6-9fcb-59d4-96e6-030379dc5dd2 |  | textbox | Finish Invert
text | 2b41fb9c-94ab-5bc2-8ba8-8e6e8d185c67 |  | textbox | Grade of Pre-Line %
text | 556d13b9-5ec1-5802-87d9-cf882d30c35f |  | textbox | Product Type
checkpoint-status |  |  | checkpoint | Install Tests completed, reviewed & approved
text | e16e8c3e-d542-530f-bbfd-d3ecc002b835 |  | textbox | Local Authority Inspection Passed
text | eb29c5b5-5de9-550b-b3c8-126dae4da9bd |  | textbox | Name of inspector
text | 2741e0fa-9820-5443-84ec-3b14d2719cde |  | textbox | Date
checkpoint-status |  |  | checkpoint | Pipe Laying Completed
boolean | 71bc27c3-4a6f-56a5-93df-2e7335126e09 |  | tickbox | Bedding Sound
boolean | d10c6e2e-9818-5101-830e-bc1ecebc900f |  | tickbox | Soil Removed
boolean | 35940f5a-1be8-5d58-a833-d45566a4dce0 |  | tickbox | Trench Compacted
boolean | a1f79508-53db-5bc0-a173-a1a2c088296b |  | tickbox | Hard Filled
checkpoint-status |  |  | checkpoint | Connections to manholes complete and approved
checkpoint-status |  |  | checkpoint | Air Test Complete
checkpoint-group |  |  | section | Backfill
checkpoint-status |  |  | checkpoint | Backfill methodology and material confirmed
checkpoint-status |  |  | checkpoint | Any formwork/ debris removed from area
checkpoint-status |  |  | checkpoint | Any waterproofing/ drainage / service requirements completed and inspected
checkpoint-status |  |  | checkpoint | Approval given to commence backfill - attach any other relevant inspections and observations closed out
checkpoint-status |  |  | checkpoint | General photos and observations during backfill
checkpoint-status |  |  | checkpoint | Backfill completed correctly and heights checked/ correct
checklist-sectioned |  |  | checklist | Blockwork Checklist |  |  |  |  | Yes | Blockwork Checklist | d0ad75e6-94a7-4aa1-9a1a-2cc41c1c7e41
checkpoint-group |  |  | section | Blockwork Setout/Pre Start QA
checkpoint-status |  |  | checkpoint | Grids available for reference and base of wall marked accurately
checkpoint-status |  |  | checkpoint | RL reference/TOW confirmed
checkpoint-status |  |  | checkpoint | Starter bars correct (location, length and strength)
checkpoint-status |  |  | checkpoint | Concrete/footing clean, tidy and level (ready for first course)
checkpoint-status |  |  | checkpoint | Blockwork reinforcing steel delivered correct and accessible (Attach photos of respective reinforcing docket)
checkpoint-status |  |  | checkpoint | Any additional pre start observations
checkpoint-status |  |  | checkpoint | Correct blocks delivered, checked & accessible
checkpoint-status |  |  | checkpoint | Latest drawings available, checked and referenced
text | 9aedf9df-f3d9-565a-8c91-170ce02767bf |  | textbox | Relevant drawings & revisions for reference:
checkpoint-status |  |  | checkpoint | Approval given to start laying blockwork
checkpoint-group |  |  | section | Blockwall Prepour
checkpoint-status |  |  | checkpoint | Base of wall in correct location
checkpoint-status |  |  | checkpoint | Horizontal reinforcing installed correctly (centres/ size / splicing etc)
checkpoint-status |  |  | checkpoint | Ties / Control joints installed as required
checkpoint-status |  |  | checkpoint | Vertical reinforcing installed as required with appropriate splice laps & secure
checkpoint-status |  |  | checkpoint | Openings checked and correct - location, height and width
checkpoint-status |  |  | checkpoint | Washouts correct/openings covered correctly and wall braced adequately (if required)
checkpoint-status |  |  | checkpoint | Any additional observations/ inspections attached
checkpoint-status |  |  | checkpoint | Wall built within tolerance - straight, level and to the correct height (Approval to pour)
checkpoint-group |  |  | section | Blockwall Pour
checkpoint-status |  |  | checkpoint | Any remedial work completed/observations closed out and approval given to pour
checkpoint-status |  |  | checkpoint | Concrete specifications checked and correct - delivery docket(s) photographed
checkpoint-status |  |  | checkpoint | General photos and any additional observations
checkpoint-status |  |  | checkpoint | All blocks filled to correct height
checkpoint-status |  |  | checkpoint | Starter bars in centre of block if applicable
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Any concrete spillage/splatter cleaned up
checkpoint-status |  |  | checkpoint | Blockwork wall(s) complete to required specification
checklist-flat |  |  | checklist | Bulk Excavation Checklist |  |  |  |  | Yes | Bulk Excavation Checklist | d1e6dcbd-9035-4246-a487-a507729876ec
checkpoint-status |  |  | checkpoint | Excavation depth determined using appropriate RL's
checkpoint-status |  |  | checkpoint | Confirm location and isolation of relevant services
checkpoint-status |  |  | checkpoint | General excavation documentation and photos attached
checkpoint-status |  |  | checkpoint | Any batters formed correctly
checkpoint-status |  |  | checkpoint | Any trenches/ pits / hazardous areas appropriately isolated
checkpoint-status |  |  | checkpoint | Any soft spots identified and appropriate remedial completed
checkpoint-status |  |  | checkpoint | Any hardfill/ blinding installed correctly to required specification
checkpoint-status |  |  | checkpoint | Relevant inspections completed and attached and any observations recorded and closed out
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Excavation completed - Correct locations and RL's achieved
checklist-flat |  |  | checklist | Civil - Storm Checklist |  |  |  |  | Yes | Civil - Storm Checklist | d210e3cd-e249-46d1-9239-5f19665a62a9
checkpoint-status |  |  | checkpoint | Location details and relevant mark ups attached
text | a9663646-22e9-5ab0-9117-3cae71fd1015 |  | textbox | Location
checkpoint-status |  |  | checkpoint | Consultant inspection completed as required
checkpoint-status |  |  | checkpoint | Council Inspection completed as required
checkpoint-status |  |  | checkpoint | Invert levels recorded
checkpoint-status |  |  | checkpoint | Invert levels as per design
text | 8e93c404-a12c-589c-be44-16a75a010538 |  | textbox | Invert Levels
checkpoint-status |  |  | checkpoint | Received QA from Subcontractor?
checkpoint-status |  |  | checkpoint | As Built drawings received
checkpoint-status |  |  | checkpoint | CCTV Survey
checkpoint-status |  |  | checkpoint | Certificates provided
checkpoint-status |  |  | checkpoint | Installation record photos
checkpoint-status |  |  | checkpoint | Storm Installation completed
checklist-flat |  |  | checklist | Timber Framing (Audit) |  |  |  |  | Yes | Timber Framing (Audit) | d34a6ee9-b3b5-4fee-b3c7-753bed17516f
checkpoint-status |  |  | checkpoint | Approval given to install timber framing
checkpoint-status |  |  | checkpoint | Dimensions / locations checked and accurate
checkpoint-status |  |  | checkpoint | All frames are square
checkpoint-status |  |  | checkpoint | Frames are straight and level
checkpoint-status |  |  | checkpoint | Fixings are correct
checkpoint-status |  |  | checkpoint | Any bracing requirements installed
checkpoint-status |  |  | checkpoint | Any additional photos, comments and observations
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
holdpoint |  |  | signoff | Raise Remedial / Request trades QA / Signoff
checkpoint-status |  |  | checkpoint | All framing completed correctly within tolerance in respective area
checklist-flat |  |  | checklist | Screw Piling Checklist |  |  |  |  | Yes | Screw Piling Checklist | d718ba31-adcc-4c6c-86e5-6ef77e629807
checkpoint-status |  |  | checkpoint | As-Built location confirmed (allowable tolerance 75mm)
checkpoint-status |  |  | checkpoint | Verticality checked
checkpoint-status |  |  | checkpoint | Concrete specification checked (concrete docket supplied)
checkpoint-status |  |  | checkpoint | Rebar installed (if required)
checkpoint-status |  |  | checkpoint | Lattey QA Received (As per requirements of Section 1.23 Piling Specification)
checkpoint-status |  |  | checkpoint | Cut off RL checked
checkpoint-status |  |  | checkpoint | Excess pile removed and disposed off
checkpoint-status |  |  | checkpoint | Progress photos
checklist-flat |  |  | checklist | Setout / Surveying Checklist |  |  |  |  | Yes | Setout / Surveying Checklist | d8e05b65-fdff-4a50-9855-06f28ed15d82
checkpoint-status |  |  | checkpoint | Any RL's setout are correct, labelled and photographed
checkpoint-status |  |  | checkpoint | Any grid setout are correct, labelled and photographed
checkpoint-status |  |  | checkpoint | Any other relevant setout/ survey documentation attached
checkpoint-status |  |  | checkpoint | Survey work completed, checked and accurate
checklist-sectioned |  |  | checklist | Blockwork |  |  |  |  | Yes | Blockwork Checklist (v2) | e4b9c7ee-8870-4c41-b3a2-cc7fb2bc3a88
checkpoint-group |  |  | section | Pre-Pour Checks
checkpoint-status |  |  | checkpoint | Location Recorded
text | c6b3003e-12bb-5a3f-a33b-6a2695174083 |  | textbox | Zone / Level / Grid(s) recorded
checkpoint-status |  |  | checkpoint | Starter bars: correct size, length, position, clean
checkpoint-status |  |  | checkpoint | Control joints/construction joints/expansion joints are located and provided
checkpoint-status |  |  | checkpoint | Penetrations/embedded items - Overall Pass
button | 69c350e2-acfe-5928-af96-5064d05ccd50 |  | button | Penetrations located and formed/allowed for (i.e openings, services penetrations) | Yes,No
button | c975308f-77c2-53af-a94e-67c25a734e2a |  | button | Embedded items (i.e anchor bolts etc) are correct and at the correct location | Yes,No
checkpoint-status |  |  | checkpoint | Blockwork specification and quality - Overall Pass
button | a81b2842-74b2-5721-9338-b10780fd928b |  | button | Block type, quality, moisture content, finish | Yes,No
button | e9d2e354-41df-5702-b23d-46b79837be25 |  | button | Mortar condition, specification, finish | Yes,No
button | 2d0caad4-19c6-5df0-9dcf-4980f5ff779e |  | button | Course type, square cuts, aligned | Yes,No
button | 9b170f2a-551e-5e62-96d9-68e90a0bae62 |  | button | Cleanout ports provided | Yes,No
button | 92589475-e797-53b9-bbc8-1ae3299d5e7a |  | button | Debris and droppings removed | Yes,No
checkpoint-status |  |  | checkpoint | Reinforcement - Overall Pass
button | 320f9775-11ea-5c37-b3b1-59c5e10d1851 |  | button | Bars: Correct location, quantity, diameter, grade, spacing, | Yes,No
button | feeee03c-ada9-54c4-a0ac-277a4fa64a6f |  | button | Reinforcement is clean and securely tied Laps and bends correct | Yes,No
button | c18e2e6e-0e95-5a3c-ab82-69ec7b75320d |  | button | Lintel and trimmer reinforcing above and around openings and penetrations etc | Yes,No
button | 3a3d09e3-c3ed-58ba-91fb-3e3927fe3db5 |  | button | Control joint reinforcing, dowel bars, tape provided | Yes,No
button | 806949f2-0e04-5976-a528-14a7c568a699 |  | button | Bond beam reinforcing provided at the top of wall | Yes,No
button | baf76fae-f016-50ed-9a14-b83b859887ae |  | button | Earthing bars present where required, including cable connections | Yes,No
button | 18c49ded-2a86-546e-a58b-da68f462387b |  | button | Grout compressive strength, condition and admixtures (20MPa min., 5mm - 12mm agg.) | Yes,No
checkpoint-status |  |  | checkpoint | Engineer informed of pour (see consultant folder and ensure observations are closed out)
holdpoint |  |  | signoff | All inspectors comments addressed
checkpoint-group |  |  | section | Pour /Post Pour
checkpoint-status |  |  | checkpoint | General photos/comments/observations during placement
checkpoint-status |  |  | checkpoint | Trades QA received & complete
button | 7e14b639-2ca0-5d82-a0d4-ee64b677e48b |  | button | Grout dockets & test cylinder results recorded | Yes,No
checklist-flat |  |  | checklist | Profile Metal Checklist |  |  |  |  | Yes | Profile Metal Checklist | e530d7b6-fecc-404e-bb41-90e4d6aca4d2
checkpoint-status |  |  | checkpoint | Product checked and correct as per specification
checkpoint-status |  |  | checkpoint | All prestart checks completed and approval given to install
checkpoint-status |  |  | checkpoint | General photos, comments and observations during install
checkpoint-status |  |  | checkpoint | Relevant Services considered, checked and approved where applicable
checkpoint-status |  |  | checkpoint | All cladding elements completed, checked and approved as per specifications
holdpoint |  |  | signoff | Request Signoff
checklist-flat |  |  | checklist | Stormwater (Main Line) - Pipeline Installation Checklist |  |  |  |  | Yes | Stormwater (Main Line) - Pipeline Installation Checklist | ed88ea71-769f-4d21-8b37-50b3078a1090
checkpoint-status |  |  | checkpoint | Latest construction drawings referenced and followed
text | 43e0b328-f62c-5cf6-8840-61e8bfff2e9d |  | textbox | Drawing & Revision Number
checkpoint-status |  |  | checkpoint | Setout & Excavation completed checked and accurate
checkpoint-status |  |  | checkpoint | Ground conditions checked & acceptable
checkpoint-status |  |  | checkpoint | Bedding depth and material correct (photo required)
checkpoint-status |  |  | checkpoint | Correct pipe (size, material & class) laid to specified level, grade and jointed as specified
text | a88d30e5-931b-56d4-854a-088a42f71017 |  | textbox | Invert Level (upstream manhole)
text | 01d5e3cb-1513-5cb3-98e3-8cb50bdb6e34 |  | textbox | Invert Level (downstream manhole)
text | 103e1aeb-ff8c-5fb2-a83b-86a602ff8caf |  | textbox | Design length of pipe (m)
text | c9b1f200-4f0f-5414-8a3c-3f18c2d5f325 |  | textbox | Length of pipe installed (m)
text | c1f37624-0125-54d0-ac57-0a748cbf5434 |  | textbox | Grade of Pipe-Line %
checkpoint-status |  |  | checkpoint | Connections to manholes complete and approved (photo required)
checkpoint-status |  |  | checkpoint | Backfill completed & compacted as specified (Photos during backfill required)
checkpoint-status |  |  | checkpoint | Relevant tests, photos & as-built information provided
checklist-flat |  |  | checklist | Precast Panel Installation Checklist |  |  |  |  | Yes | Precast Panel Installation Checklist | f075f1ff-d168-4952-aa55-2a725e7e9fd5
checkpoint-status |  |  | checkpoint | Inspected on arrival and damage free
checkpoint-status |  |  | checkpoint | Installed in correct location
checkpoint-status |  |  | checkpoint | Adequately braced
checkpoint-status |  |  | checkpoint | Grout sleeves correctly grouted
checkpoint-status |  |  | checkpoint | Panel install complete (checked location & level)
checklist-flat |  |  | checklist | Walls Postline |  |  |  |  | Yes | Walls Postline | f21a05d6-e610-459e-b5c9-903642eeeb38
checkpoint-status |  |  | checkpoint | Correct linings installed as per linings plan
checkpoint-status |  |  | checkpoint | Bracing fixings installed correctly as per requirements
checkpoint-status |  |  | checkpoint | Linings cut out for flush boxes neat and tidy
checkpoint-status |  |  | checkpoint | All screws installed flush
checkpoint-status |  |  | checkpoint | Wall approved for stopping
checkpoint-status |  |  | checkpoint | Stopping light check complete ready for paint
checklist-sectioned |  |  | checklist | Spanlok Cladding |  |  |  |  | Yes | Spanlok Cladding | f28fd8a2-e4a3-4a96-8fe5-523091602d1f
checkpoint-group |  |  | section | QC Summary
checkpoint-no-status |  |  | checkpoint | QC Summary
text | 217a0ac7-32e7-5823-9f50-08b5cde24042 |  | textbox | Subcontractor/Supplier
text | 2c375605-e35d-51ed-a449-a5f84fae8d50 |  | textbox | Works area
text | caac1df2-74fb-57aa-b189-9f584b109712 |  | textbox | Drawings reference
text | 05caea43-9de6-5180-a20c-652e4861cbe4 |  | textbox | Project specification reference
checkpoint-group |  |  | section | Precladding
checkpoint-status |  |  | checkpoint | RAB and timber is dry prior to apply revalshield
checkpoint-status |  |  | checkpoint | Revealshield is applied correctly (80mm overlap) and as per drawing
checkpoint-status |  |  | checkpoint | Liquidflash is apply around the window opening andany other location required
checkpoint-status |  |  | checkpoint | Sealant and flashing tape is applied ( brackets fixed on RAB/ over the top of pressure bar...)
checkpoint-group |  |  | section | Spanlok
checkpoint-status |  |  | checkpoint | Façade bottom flashing detail installed (equal angle/ steel angle/ vermin..)
label | 7b131631-515c-5181-ab50-0d20712ed1f6 |  | note | Photos
checkpoint-status |  |  | checkpoint | Timber batten + castellated cavity batten (James hardie)
label | 36f3bd62-b0bd-56a6-844c-21d15868eb1e |  | note | Photos
checkpoint-status |  |  | checkpoint | PVC stripes over timber batten
label | 68c4b63c-8136-5b5a-8898-d84b7abbaa84 |  | note | Photos
checkpoint-status |  |  | checkpoint | Shroud brackets on if required
label | 3d49858e-055d-571d-ab4c-59c578ba97c2 |  | note | Photos
checkpoint-status |  |  | checkpoint | Horizontal fixing plate on
label | 6209ed1f-57d0-5ca1-9abb-576230ebc373 |  | note | Photos
checkpoint-status |  |  | checkpoint | Spanlok sheet plumb and leveled (10mm gap over the head flashing))
label | b170e69c-8832-558c-b81b-d5baeca39610 |  | note | Photos
checkpoint-status |  |  | checkpoint | Sill flashing installed correctly
label | c174aae9-62f9-5d22-94d6-4534ed08a831 |  | note | Photos
checkpoint-status |  |  | checkpoint | Is it complete and tightly fitted
label | 943fcb18-f0b6-56ba-8824-4f2b5b0fb044 |  | note | Photos
checkpoint-group |  |  | section | Services
checkpoint-status |  |  | checkpoint | Check if services penetrating the RAB are required in this location
label | d96c25af-dac3-5d3e-82d6-bd5023b42de4 |  | note | Photos
checkpoint-status |  |  | checkpoint | Security services installed to correct locations
label | e510a0fe-17fe-57e6-ba1e-df4fd213bdd7 |  | note | Photos
checkpoint-status |  |  | checkpoint | Plumbing services installed to correct locations
label | f19be9ce-e142-5d79-ab86-7e78057e7236 |  | note | Photos
checkpoint-status |  |  | checkpoint | Fire services installed to correct loctions
label | dc123978-6318-57f2-8780-bcfa014e5e2b |  | note | Photos
checkpoint-status |  |  | checkpoint | Lighting and power services installed to correct locations
label | 9adf994e-5a98-50fb-ae60-ad6a2d576ef1 |  | note | Photos
checkpoint-status |  |  | checkpoint | Mechanical services installed to correct locations
label | 1a7fa40e-f2d2-514d-bfd9-9cbcbd388851 |  | note | Photos
checkpoint-group |  |  | section | Final approvals and holdpoints
checkpoint-status |  |  | checkpoint | Hold point - Sub contractor QA
label | 2c1d1940-c9df-5950-90f5-d55db202c580 |  | note | QA REPORT
holdpoint |  |  | signoff | Company QA Check
checkpoint-status |  |  | checkpoint | Engineer Inspections
label | 64f6674e-1e53-50b0-ab6c-6f7ccd59bd74 |  | note | SITE REPORTS
checkpoint-status |  |  | checkpoint | Council Inspections
label | a7dcefb6-fd05-56b1-8f87-10d4c6599be5 |  | note | INSPECTION REPORT
checklist-flat |  |  | checklist | Retaining Wall Checklist |  |  |  |  | Yes | Retaining Wall Checklist | f4a8dded-3356-4ea2-aa22-c8841ed67b2c
checkpoint-status |  |  | checkpoint | Retaining wall(s) setout/heights confirmed
checkpoint-status |  |  | checkpoint | Area prepared - Excavation depths and location of wall checked and correct
checkpoint-status |  |  | checkpoint | General install photos and observations attached
checkpoint-status |  |  | checkpoint | Correct materials used and installed using appropriate methodology
checkpoint-status |  |  | checkpoint | All relevant services / waterproofing elements completed, checked and approved prior to backfill
checkpoint-status |  |  | checkpoint | Backfill completed - correct materials and compaction methodology used - specified compaction achieved
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Additional observations/ inspections attached and all remedial items closed out
checkpoint-status |  |  | checkpoint | Retaining wall completed to required specifications
checklist-flat |  |  | checklist | Framing |  |  |  |  | Yes | Framing | f6ca7bd9-7c48-43e1-9e71-6e5dc8b19e90
checkpoint-status |  |  | checkpoint | Timber complies with spec for type and grade
checkpoint-status |  |  | checkpoint | Timber gauge sizing correct
checkpoint-status |  |  | checkpoint | Timber to steel fixings
checkpoint-status |  |  | checkpoint | Setting out as per architectural drawings
checkpoint-status |  |  | checkpoint | Dampcourse installed
checkpoint-status |  |  | checkpoint | Top plate hardware install (every 600mm/80mm from slab edge)
checkpoint-status |  |  | checkpoint | Special and service nogs complete
checkpoint-status |  |  | checkpoint | Stud centres
checkpoint-status |  |  | checkpoint | Nog centres, level and ridged
checkpoint-status |  |  | checkpoint | Floor fixings - Holding down bolts
checkpoint-status |  |  | checkpoint | Seismic joint frame correct
checkpoint-status |  |  | checkpoint | Additional blocking Nuwall
checkpoint-status |  |  | checkpoint | Additional blocking spanlok
checkpoint-status |  |  | checkpoint | Additional blocking INSOL (shrouds/fine)
checklist-flat |  |  | checklist | Piling Checklist |  |  |  |  | Yes | Piling Checklist | fca17410-a8a2-4a3b-9a4e-db712d48278a
checkpoint-status |  |  | checkpoint | Piles setout, surveyed and clearly marked
text | f32dd7a4-7547-5f08-8b2e-ac1e3768a8d3 |  | textbox | Pile number:
checkpoint-status |  |  | checkpoint | Accurate RL confirmed for piling reference
checkpoint-status |  |  | checkpoint | Acceptable site conditions and access for piling rig
checkpoint-status |  |  | checkpoint | Additional photos/ observations / reports attached
checkpoint-status |  |  | checkpoint | Approval given to commence piling
boolean | e21be132-dd8b-5785-a442-59f37b8a632a |  | tickbox | approval given to dig
boolean | fd57fd8d-7472-5383-a984-5d7bc988929f |  | tickbox | relevant services identified and isolated / clearly marked
boolean | a9acba67-e05d-5cc0-8ea7-1d8568425bd8 |  | tickbox | relevant information communicated to piling trade
boolean | 6979b4f2-384f-53cf-a6ac-d704b8598bcf |  | tickbox | any environmental requirements considered and enacted
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Relevant inspections completed and attached - any observations recorded and closed out
checkpoint-status |  |  | checkpoint | Piling spoil removed and work area left clean and tidy
checkpoint-status |  |  | checkpoint | Any additional completion/handover documents completed and attached
checkpoint-status |  |  | checkpoint | All piles completed (locations and heights checked and correct within tolerance)
checklist-sectioned |  |  | checklist | Structure - Concrete Pour - Modified (NB: Only to be used upon Approval by PM) |  |  |  |  | Yes | Structure - Concrete Pour - Modified (NB: Only to be used upon Approval by PM) | fef52d92-5033-4ba2-a442-1d071d0ded72
checkpoint-group |  |  | section | Formwork and Embedded Items
checkpoint-status |  |  | checkpoint | Latest drawings available, checked and referenced
checkpoint-status |  |  | checkpoint | Any additional formwork photos and observations
checkpoint-status |  |  | checkpoint | All formwork elements completed and ready for concrete pour ( excess debris removed )
checkpoint-group |  |  | section | Reinforcing
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Verified Size and type correct to specification
checkpoint-status |  |  | checkpoint | Any additional photos and observations
checkpoint-group |  |  | section | Pre-Pour Completion (Approval to pour)
checkpoint-status |  |  | checkpoint | Heights and falls checked/confirmed before placement
button | 0334b2ac-ef0f-5536-8223-5026b0478c50 |  | button | Is the cover correct to specification | Yes,No
checkpoint-status |  |  | checkpoint | Engineer inspection completed - any observations / remedial work documented and closed out
checkpoint-status |  |  | checkpoint | Main contractor inspection completed - Approval given to pour concrete
checkpoint-status |  |  | checkpoint | General photos and observations of concrete placement attached
checkpoint-group |  |  | section | Pour / Post-Pour Checks/Sign Off
checkpoint-status |  |  | checkpoint | Concrete checked on arrival & correct (slump, MPa, approved mix, etc)
checkpoint-status |  |  | checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
checkpoint-status |  |  | checkpoint | Concrete surface to specifications
checkpoint-status |  |  | checkpoint | Concrete results 7D & 28D Passed
checkpoint-status |  |  | checkpoint | Trades QA received, attached, reviewed and approved
checkpoint-status |  |  | checkpoint | Any remedial work completed