## Structures
ConQA Team Notes:
Document Title: |  | OHLE-ITP-CAT5-OHLE STRUCTURE INSTALLATION
ITP Description: |  | OHLE Structures
Discipline (e.g. CIV/STR/RAIL: |  | STR
Revision Number: |  | 1
Revision Date: |  | 2023-05-09
ITP prepared by:
ITP approved for use by: |  | Cat5 Rail
Special Notes to ConQA Team : |  | ITP to be used in Brunt Rd & Camms Rd Only
Inspection & Test Plan - OHLE Structures Installation
|  |  | Document No.: OHLE-ITP-CAT5-OHLE Structure Installation | [6 empty] | Revision: | 1
[10 empty] | Date: | 2023-05-09
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Responsible person | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Overhead Line Electrification | L1-CHE-STD-011(1) MEST 000002-02(1) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Structure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway | VRIOGS 001 AS 4100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Electrical Networks Standard Electrical Networks Principles and Performance | L1-CHE-STD-015(1) MEST 000002-06(1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Track Bonding for Signaling and Traction Return Current | L1-CHE-STD-016(1) MEST 000002-05(1) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | Procure materials. What materials? Has to be specific, one line item for each material. Materials to be in accordance with IFC design drawings and relevant MTM Standards. | Relevant MTM Standards and AS, etc | To ensure materials are manufactured/fabricated as per IFC design drawings/MTM design range. Material Approval Form to ba raised in TB prior to use on site. | Document Review | Once for each supplier, prior to works start | HP | MRPA | MRPA | This ITP Signed Off
2.2 | Materials delivered/collected to stores/Site. | Contractor - Site Material Control procedure. Cat5 Material received -Brunt and Camms Tracking sheet | Ensure materials are delivered/collected as required. Certificates of Conformity provided by MRPA | Document Review | Once for each supplier, prior to works start | IP | MRPA Issue CAT5 Receive | MRPA | This ITP Signed Off
3 | Preliminaries - Procedures & Documentation
3.1 | Produce Work Package Plan | Work Package Plan WAP_BR_184 | Submission of Work Package Plan and MRPA approval and acceptance. Ensure work is carried out in a safe manner. | Document Review | Prior to Works Start In accordance with MTM Standards | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4 | Pre-construction Activities
4.1 | Approval of IFC drawings | Contractor Design Management procedure. Enter document no. here | Ensure correct and most recent revision of IFC design drawings are used for construction. | Document/ Drawings Review | Prior to Works and at regular intervals. TBC in accordance with MTM Standards | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4.2 | Lifting operations | Contractor - Permit to Lift Control procedure. Contractor - Site Material Control Cat5 -LP-01 | Ensure all plant and equipment are operating within their SWL limits. Permit to lift to be generated and signed off by Appointed Person. | Visual Document Review | Each plant and equipment prior to works start. TBC in accordance with MTM Standards | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4.3 | Task Specfic Permits | Working at height permit. Hot works Permit,Permit to dig. Enter document nos. here | Ensure all task and activities have relevent permits issued and received. Task Permits to be generated and signed off by appointed person. Task specific documents - MTM to issue permit to enter/Isolation permits etc. | Visual Document Review | Each Task prior to works start. TBC in accordance with MTM Standards | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
4.4 | Pre-Installation check | IFC wiring layouts, IFC cross sections and BOQ. Engineering Drawings Management Policy (IFC/AsBuilt) L1-CHE-MAN-001 | Ensure that foundation holding down bolts match steelwork dimensions. Supervision checking to ensurethat equipment is installed correctly. Check sheets, relevant red pen drawing,site delap report to be attached. | Visual Document Review | Each Task prior to works start. TBC in accordance with MTM Standards | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
4.5 | Foundation Coordinates |  | Ensure Complience with structure gauge clearances defined within MTM Spec. Foundation ITP'S and As Built Coordinates accepted and provided As built documents - provided by MRPA. | Visual Document Review | Prior to Works Start TBC in accordance with MTM Standards | HP | MRPA | MRPA | This ITP Signed Off
5 | Construction Activities
5.1 | Erection of Steelwork | IFC wiring layouts, cross sections and BOQ. Enter document nos. here and Relevant MTM Standards and AS, etc | Ensure the safe installation of the correct steel to the correct orientation as per IFC design drawings/MTM design range. Supervision / checking to ensure that equipment is installed correctly. Attach Check sheets, relevant drawings & BOQ. | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.2 | Setting or rake / tightening of bolts | IFC wiring layouts, cross sections and design drawings. Enter document nos. here and Relevant MTM Standards and AS, etc | Ensure the correct installation (prior to the application of loads) torequired rake as per IFC design drawings-MTM design spec. Supervision / checking to ensure that equipment is installed correctly. Attach Check sheets, relevant drawings & designdrawings. | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6 | Post-construction Activities
6.1 | Defects/Temporary Works | IFC wiring layouts, cross sections and design drawings. Enter document nos. here and Relevant MTM Standards and AS, etc | Ensure all Defects/Temporary works are capture and closed out correctly. Defect list to be provided at the end of Occo identifing planned work to recifiy Attach Design mark up, Defect list, temporary bond register, and approved TW design | Document Review Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6.2 | Relevant documentation readily available. (As-built Survey) | As built drawings and check sheets to accordance to MTM Design spec. Enter document nos. here and Relevant MTM Standards and AS, etc | Ensure delivery of relevant documentation to client. As built drawings and check sheets.CAT5/OHLE/CHK001 check sheets. Attach As built drawings and CAT5/OHLE/CHK001 check sheets. | Document Review Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6.3 | Non-conformance Report (NCR) Closure | MTM Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /

## BWA
ConQA Team Notes:
Document Title: |  | OHLE-ITP-CAT5-ITP-OHLE BWA INSTALLATION
ITP Description: |  | OHLE BWA
Discipline (e.g. CIV/STR/RAIL/OHLE: |  | OHLE
Revision Number: |  | 1
Revision Date: |  | 2023-05-09
ITP prepared by: |  | Richard Johnson
ITP approved for use by: |  | Andrew Pitts
Special Notes to ConQA Team : |  | ITP to be used in Brunt Rd & Camms Rd Only
Inspection & Test Plan - OHLE BWA Installation
|  |  | Document No.:OHLE-ITP-CAT5-ITP-OHLE BWA INSTALLATION | [6 empty] | Revision: | 1
[10 empty] | Date: | 2023-05-09
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Responsible person | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Overhead Line Electrification | L1-CHE-STD-011(1) MEST 000002-02(1) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Structure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway | VRIOGS 001 AS 4100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Electrical Networks Standard Electrical Networks Principles and Performance | L1-CHE-STD-015(1) MEST 000002-06(1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | Procure materials. What materials? Has to be specific, one line item for each material. Materials to be in accordance with IFC design drawings and relevant MTM Standards. | Relevant MTM Standards and AS, etc | To ensure materials are manufactured/fabricated as per IFC design drawings/MTM design range. Material Approval Form to be raised in TB prior to use on site. | Document Review | Once for each supplier, prior to works start | HP | MRPA | MRPA | This ITP Signed Off
2.2 | Materials delivered/collected to stores/Site. | Contractor - Site Material Control procedure. Cat5 Material received -Brunt and Camms Tracking sheet | Ensure materials are delivered/collected as required. Certificates of Conformity provided by MRPA | Document Review | Once for each supplier, prior to works start | IP | MRPA Issue CAT5 Receive | MRPA | This ITP Signed Off
3 | Preliminaries - Procedures & Documentation
3.1 | Produce Work Package Plan | Work Package Plan WAP_BR_184 | Submission of Work Package Plan and MRPA approval and acceptance. Ensure work is carried out in a safe manner. | Document Review | Prior to Works Start TBC in accordance with MTM Standards | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4 | Pre-construction Activities
4.1 | Approval of IFC drawings | Contractor Design Management procedure. Enter document no. here | Ensure correct and most recent revision of IFC design drawings are used for construction. | Document/ Drawings Review | Prior to Works and at regular intervals. TBC in accordance with MTM Standards | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4.2 | Lifting operations | Contractor - Permit to Lift Control procedure. Contractor - Site Material Control Cat5 -LP-01 | Ensure all plant and equipment are operating within their SWL limits. Permit to lift to be generated and signed off by Appointed Person. | Visual Document Review | Each plant and equipment prior to works start. TBC in accordance with MTM Standards | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4.3 | Task Specific Permits | Working at height permit. Hot works Permit, Permit to dig. BWA Installation methodology | Ensure all task and activities have relevant permits issued and received. Task Permits to be generated and signed off by appointed person. Task specific documents - MTM to issue permit to enter/Isolation permits etc. | Visual Document Review | Each Task prior to works start. TBC in accordance with MTM Standards | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
4.4 | Pre-Installation check | IFC wiring layouts, IFC cross sections and BOQ. Engineering Drawings Management Policy (IFC/As-built) L1-CHE-MAN-001 | Ensure that locations matches most relevant IFC drawings | Visual Document Review | Each Task prior to works start. TBC in accordance with MTM Standards | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5 | Construction Activities
5.1 | Install BWA at correct location | Overhead Line Electrification L1-CHE-STD-011(1) MEST 000002-02(1) | Ensure that the BWA is set correctly as per IFC design drawing/MTM design range, fit for the passage of trains. | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.2 | Check all fittings are secure. | Manufacturers torque settings | Ensure that the BWA is set correctly and fit for the passage of trains as per IFC design drawing/MTM design range. Engineer checking to ensure that the equipment is installed correctly to IFC design drawing/MTM design range. | Measure Visual | Each OHLE BWA structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.3 | Installation of wire supports at the correct height and stagger. | Install as per design drawings. | Supervision checking to ensure that equipment is installed correctly. | Measure Visual | Each OHLE BWA structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.4 | Check wire follows correct route. | Install as per design drawings. | Engineer checking to ensure that equipment is installed correctly. | Visual | Each OHLE BWA structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.5 | Install to correct tension. | Install as per design, use span/ambient temp. tension charts. | Engineer checking to ensure that equipment is installed correctly. | Measure Visual | Prior termination | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6 | Post-construction Activities
6.1 | Defects/Temporary Works | IFC wiring layouts, cross sections and design drawings. | Ensure all Defects/Temporary works are capture and closed out correctly. Defect list to be provided at the end of Occo identifying planned work to rectify Attach Design mark up, Defect list, temporary bond register, and approved TW design | Document Review Visual | Each Anchor Termination | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6.2 | Relevant documentation readily available. (As-built Survey) | As built drawings and check sheets to accordance to MTM Design spec. | Ensure delivery of relevant documentation to client. As built drawings and check sheets.CAT5/OHLE/CHK/003 check sheets. . | Document Review Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6.3 | Non-conformance Report (NCR) Closure | MTM Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /

## OHLE
ConQA Team Notes:
Document Title: |  | ITP-107-RAIL-SSB-OHLE Installation
ITP Description: |  | OHLE Installation
Discipline (e.g. CIV/STR/RAIL) |  | RAIL
Revision Number: |  | 0
Revision Date: |  | 2023-06-26
ITP prepared by: |  | Nikhil Siram
ITP approved for use by:
Special Notes to ConQA Team : |  | ITP to be used in Station Street, Beaconsfield LXRP
Inspection & Test Plan - OHLE Installation
|  |  | ITP-107-RAIL-SSB-OHLE Installation | [6 empty] | Revision: | 0
[10 empty] | Date: | 2023-06-26
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Responsible person | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Overhead Line Electrification | L1-CHE-STD-011(1) MEST 000002-02(1) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Structure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway | VRIOGS 001 AS 4100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Electrical Networks Standard Electrical Networks Principles and Performance | L1-CHE-STD-015(1) MEST 000002-06(1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Fabrication of Steelwork | VicRoads Section 630 January 2023 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.5 | Electrical Networks Standard Electrical Networks Principles and Performance | Structural Steel Work - Fabrication and Erection | N/A | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | Structural Steel Components and Fasteners | IFC Drawings | Fabricator is required to provide the Manufacturer's Data Record (MDR) for each component. • Typically this consists of but not limited to: i. Completed fabrication ITP ii. Weld Procedure Specifications iii. Weld Procedure Qualifications iv. Welder Qualifications v. Material Certificates vi. Coating certificate(s) vii. Non-destructive Testing (NDT) Reports (if any) viii. As-built Drawings to demonstrate compliance with dimensional tolerances of structural steel • Bolts, nuts and washers for Property Class 4.6 bolting shall be supplied in accordance with AS 1111 and AS 1112 • Bolts, nuts and washers for Property Class 8.8 bolting shall be supplied in accordance with AS/NZS 1252. • All bolts nuts and washers are hot-dipped galvanized. Collate: Structural Steel Quality Assurance Documentation. Attach: Collated QA documents in ConQA | Document review | Where applicable/ Each element | HP | PE | MRPA Engineer | This ITP Signed Off
2.2 | Bolted Connections Using Direct Tension Indicators (DTIs) | AS4100 Clause 15.2.5.3 (a), AS5131 Clause 8.5.7 (a) | Direct tension indicators (DTIs) shall not be used unless approved by the Nominated Authority and accompanied by: i. technical data sheet or information on the product | Document Review | Where applicable/ Each element | HP | PE | MRPA Engineer | This ITP Signed Off
2.3 | Overhead Wiring Small Parts Steel and conductor wires | Relevant MTM Standard Drawings | Overheading Wiring Small Parts Steel to be procured as detailed in the drawings and as per relevant MTM Standard Drawings. • Deliveries are to be inspected to match the purchase order Attach: Purchase order/Delivery dockets/Certificate of conformity | Visual Insoection and measurement | Upon delivery | IP | PE | MRPA | This ITP Signed Off
2.4 | Grout | IFC drawings | All grout under base plates shall be CONBEXTRA C or equivalent as approved. Approved grout to be Flowable shrinkage compensated with minimum 50 Mpa compressive strength. Enter: Teambinder Material Approval number | Document Review | Where applicable/ Each element | HP | PE | MRPA | This ITP/ Material Approval
3 | Preliminaries - Procedures & Documentation
3.1 | Installation Methodology & Works Method Statement | AS5131 Clause 11.2.3 | Details of how the Structural & Architectural Steel will be Installed will need to be privided including the following: – Transported to site; – Handled on site; – Installation Procedure (subcontracor ITP's); Submission of Work Package Plan and MRPA approval and acceptance. Enter: WAP number | Document Review | Prior to Works Start | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4 | Pre-construction Activities
4.1 | Approval of IFC drawings | Contractor Design Management procedure. | Ensure correct and most recent revision of IFC design drawings are used for construction. | Document/ Drawings Review | Prior to Works and at regular intervals. | HP | MRPA/ CAT5 | MRPA/CAT5 Engineer | This ITP Signed Off
4.2 | Cantilever assembled. | Cantilever assembled as per IFC design. | Relevant checks followed and adhered to-Cantilever Fabrication Check sheet. | Visual Document Review | Each Task prior to works start. | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5 | Construction Activities
5.1 | Mast Installation | Overhead Line Electrification L1-CHE-STD-011(1) MEST 000002-02(1) | Work instructions in accordance to IFC design | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.2 | Cantilever installed. | Overhead Line Electrification L1-CHE-STD-011(1) MEST 000002-02(1) | Work instructions in accordance to IFC design | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.3 | Bearing type Joints TB Friction type joints TF | IFC Drawings | BOLTS DESIGNATED TB & TF ARE TENSIONED AS PER AS 5131 and Table 8.5.6 – Bolt mark ups (in case of partial tensionening) should be visible for inspection – DTI squirts are to be visible for inspection | Visual | Where applicable/ Each element | IP | PE | MRPA/CAT5 Engineer | This ITP Signed Off
5.4 | Install SPS to correct height / position relative to track | Design drawings, IFC cross sections &S tructure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway | Ensure SPS is installed as per IFC design drawings/MTM design range. Supervision / checking to ensure that equipment is installed correctly. | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.5 | Cantilever checked once installed. | Cantilever checked as per IFC design drawings/MTM design range.Completed check sheet.CAT5/OHLE/CHK002 | Supervision checking to ensure that equipment is installed correctly. | Measure Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.6 | Base Plate Grout | IFC Drawings | Grout to be mixed as per manufacturer TDS. • Grout to be poured under base plate as per IFC drawings. Grout over pour is to be 6mm and cover area with Nom 50mm offset around the base plate. | Visual | Where applicable/ Each element | IP | PE | MRPA/CAT5 Engineer | This ITP Signed Off
5.7 | Installation of wire supports at the correct height and stagger | Install as per design | Engineer checking to ensure that equipment is installed correctly. | Visual | Each OHLE BWA Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
5.8 | Install to correct tension | Install as per design | Engineer checking to ensure that equipment is installed correctly. | Visual | Prioir termination | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6 | Post-construction Activities
6.1 | Defects/Temporary Works | IFC wiring layouts, cross sections and design drawings. | Ensure all Defects/Temporary works are capture and closed out correctly. Defect list to be provided at the end of Occo identifying planned work to rectify Attach Design mark up, Defect list, temporary bond register, and approved TW design | Document Review Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6.2 | Relevant documentation readily available. (As-built Survey) | As built drawings and check sheets to accordance to MTM Design spec. | Ensure delivery of relevant documentation to client. As built drawings and check sheets.CAT5/OHLE/CHK/002 check sheets. . | Document Review Visual | Each OHLE Structure | IP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
6.3 | Non-conformance Report (NCR) Closure | MTM Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP | CAT5/ MRPA | MRPA/CAT5 Engineer | This ITP Signed Off
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /