## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-107-RAIL-SSB-OHLE Installation | itp |  |  |  |  | ITP-107-RAIL-SSB-OHLE Installation Rev 0
section | Referenced Documentation
checkpoint | Referenced Documentation
label | Document Title: ITP-107-RAIL-SSB-OHLE Installation
label | ITP Description: OHLE Installation
label | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | Discipline (e.g. CIV/STR/RAIL): RAIL
label | Revision Number: 0
label | Revision Date: 26/06/2023
label | ITP created by: Nikhil Siram
label | 1.1 Overhead Line Electrification
label | Reference: L1-CHE-STD-011(1) MEST 000002-02(1)
label | 1.2 Structure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway
label | Reference: VRIOGS 001 AS 4100
label | 1.3 Electrical Networks Standard Electrical Networks Principles and Performance
label | Reference: L1-CHE-STD-015(1) MEST 000002-06(1
label | 1.4 Fabrication of Steelwork
label | Reference: VicRoads Section 630 January 2023
label | 1.5 Electrical Networks Standard Electrical Networks Principles and Performance
label | Reference: Structural Steel Work - Fabrication and Erection
section | Preliminaries - Materials
checkpoint | 2.1 Structural Steel Components and Fasteners
label | REFERENCE: IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Fabricator is required to provide the Manufacturer's Data Record (MDR) for each component.
label | ○ Typically this consists of but not limited to:
label | i. Completed fabrication ITP
label | ii. Weld Procedure Specifications
label | iii. Weld Procedure Qualifications
label | iv. Welder Qualifications
label | v. Material Certificates
label | vi. Coating certificate(s)
label | vii. Non-destructive Testing (NDT) Reports (if any)
label | viii. As-built Drawings to demonstrate compliance with dimensional tolerances of structural steel
label | ○ Bolts, nuts and washers for Property Class 4.6 bolting shall be supplied in accordance with AS 1111 and AS 1112
label | ○ Bolts, nuts and washers for Property Class 8.8 bolting shall be supplied in accordance with AS/NZS 1252.
label | ○ All bolts nuts and washers are hot-dipped galvanized.
label | Collate: Structural Steel Quality Assurance Documentation.
label | Attach: Collated QA documents in ConQA
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Where applicable/ Each element
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: PE
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON:
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 Bolted Connections Using Direct Tension Indicators (DTIs)
label | REFERENCE: AS4100 Clause 15.2.5.3 (a), AS5131 Clause 8.5.7 (a)
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Direct tension indicators (DTIs) shall not be used unless approved by the Nominated Authority and accompanied by:
label | i. technical data sheet or information on the product
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Where applicable/ Each element
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: PE
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 Overhead Wiring Small Parts Steel and conductor wires
label | REFERENCE: Relevant MTM Standard Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Overheading Wiring Small Parts Steel to be procured as detailed in the drawings and as per relevant MTM Standard Drawings.
label | ○ Deliveries are to be inspected to match the purchase order
label | Attach: Purchase order/Delivery dockets/Certificate of conformity
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual Inspection and measurement
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Upon delivery
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: PE
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 2.4 Grout
label | REFERENCE: IFC drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: All grout under base plates shall be CONBEXTRA C or equivalent as approved. Approved grout to be Flowable shrinkage compensated with minimum 50 Mpa compressive strength.
textbox | Enter: Teambinder Material Approval number
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Where applicable/ Each element
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: PE
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP/ Material Approval
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | Preliminaries - Procedures & Documentation
checkpoint | 3.1 Installation Methodology & Works Method Statement
label | REFERENCE: AS5131 Clause 11.2.3
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Details of how the Structural & Architectural Steel will be Installed will need to be privided including the following:
label | – Transported to site;
label | – Handled on site;
label | – Installation Procedure (subcontracor ITP's);
label | ○ Submission of Work Package Plan and MRPA approval and acceptance.
textbox | Enter: WAP number
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Prior to Works Start
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: MRPA/CAT5
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | Pre-construction Activities
checkpoint | 4.1 Approval of IFC drawings
label | REFERENCE: Contractor Design Management procedure.
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure correct and most recent revision of IFC design drawings are used for construction.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document/Drawings Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Prior to Works and at regular intervals.
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: MRPA/CAT5
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 Cantilever assembled.
label | REFERENCE: Cantilever assembled as per IFC design.
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Relevant checks followed and adhered to-Cantilever Fabrication Check sheet.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual, Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each Task prior to works start.
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
section | Construction Activities
checkpoint | 5.1 Mast Installation
label | REFERENCE: Overhead Line Electrification L1-CHE-STD-011(1) MEST 000002-02(1)
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Work instructions in accordance to IFC design
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure, Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.2 Cantilever installed.
label | REFERENCE: Overhead Line Electrification L1-CHE-STD-011(1) MEST 000002-02(1)
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Work instructions in accordance to IFC design
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure, Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.3 Bearing type Joints TB Friction type joints TF
label | REFERENCE: IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: BOLTS DESIGNATED TB & TF ARE TENSIONED AS PER AS 5131 and Table 8.5.6
label | – Bolt mark ups (in case of partial tensionening) should be visible for inspection
label | – DTI squirts are to be visible for inspection
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Where applicable/ Each element
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: PE
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.4 Install SPS to correct height / position relative to track
label | REFERENCE: Design drawings, IFC cross sections &S tructure Gauge Envelopes – Minimum Clearance for Infrastructure Adjacent to the Railway
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure SPS is installed as per IFC design drawings/MTM design range. Supervision / checking to ensure that equipment is installed correctly.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure, Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.5 Cantilever checked once installed.
label | REFERENCE: Cantilever checked as per IFC design drawings/MTM design range. Completed check sheet. CAT5/OHLE/CHK002
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Supervision checking to ensure that equipment is installed correctly.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Measure, Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.6 Base Plate Grout
label | REFERENCE: IFC Drawings
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Grout to be mixed as per manufacturer TDS.
label | ○ Grout to be poured under base plate as per IFC drawings. Grout over pour is to be 6mm and cover area with Nom 50mm offset around the base plate.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Where applicable/ Each element
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: PE
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.7 Installation of wire supports at the correct height and stagger
label | REFERENCE: Install as per design
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Engineer checking to ensure that equipment is installed correctly.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE BWA Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 5.8 Install to correct tension
label | REFERENCE: Install as per design
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Engineer checking to ensure that equipment is installed correctly.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Prior termination
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
section | Post-construction Activities
checkpoint | 6.1 Defects/Temporary Works
label | REFERENCE: IFC wiring layouts, cross sections and design drawings.
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure all Defects/Temporary works are capture and closed out correctly.
label | ○ Defect list to be provided at the end of Occo identifying planned work to rectify
label | ○ Attach Design mark up, Defect list, temporary bond register, and approved TW design
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review, Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 6.2 Relevant documentation readily available. (As-built Survey)
label | REFERENCE: As built drawings and check sheets to accordance to MTM Design spec.
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure delivery of relevant documentation to client. As built drawings and check sheets.CAT5/OHLE/CHK/002 check sheets.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review, Visual
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Each OHLE Structure
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: IP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
checkpoint | 6.3 Non-conformance Report (NCR) Closure
label | REFERENCE: MTM Quality Management Plan
label | – – – – – – – – – – – – – – – – –
label | ACCEPTANCE CRITERIA: Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | – – – – – – – – – – – – – – – – –
label | METHOD: Document Review
label | – – – – – – – – – – – – – – – – –
label | FREQUENCY: Once, prior to closure of this lot / element / Work area
label | – – – – – – – – – – – – – – – – –
label | CATEGORY: HP
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBILITY: CAT5/MRPA
label | – – – – – – – – – – – – – – – – –
label | RESPONSIBLE PERSON: MRPA/CAT5 Engineer
label | – – – – – – – – – – – – – – – – –
label | VERIFYING DOCUMENTS: This ITP Signed Off
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | Name:
text | Position:
date | Date Completed:
holdpoint | Sign ITP