## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CTN-ITP-003 - Service Trenching & Install | itp |  |  |  | Yes | CTN-ITP-003 - Service Trenching & Install
section | 1 - Preliminary Works
checkpoint | 1.1 - Check for correct documentation
label | Frequency: Prior to commencing any activity
label | Acceptance Criteria: Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings
label | – all drawings are the latest revision
label | Reference Documents: Drawings and drawing registers
label | Inspection / Test Method: Visual inspection
label | Record of conformity: This ITP signed off
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency: Prior to commencing any activity
label | Acceptance Criteria: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | Reference Documents: PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection / Test Method: Visual Inspection
label | Record of conformity: This ITP signed off
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 1.3 - Materials
label | Frequency: Per Lot
label | Acceptance Criteria: Bedding sand provided over rock and above conduit
label | • 20mm Class 3 FCR for backfill
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed, Recievable Inspection checklist
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
section | 2 - Construction Works
checkpoint | 2.1 - Survey set-out
label | Frequency: As required
label | Acceptance Criteria: Survey activities undertaken to ensure and validate that all works will meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used.
label | Reference Documents: Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | HP*
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 2.2 - Excavation/Boring & Trenching
label | Frequency: Prior to Backfill
label | Acceptance Criteria: Superintendent to inspect completed tench
label | ○ Depth Requirements:
label | • Where conduits are laid under carriageway pavements, the minimum cover from top of conduit to the pavement surface shall be 600 mm
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Measure
label | Record of conformity: This ITP signed
label | HP
label | Responsibility: Site Engineer
text | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Installation of Conduits
label | Frequency: Prior to installation of conduits
label | Acceptance Criteria: All conduit installation works for electrical wiring and communications cabling shall be carried out by, or under the direct supervision of, appropriately registered and licensed personnel
label | – 100mm bedding sand provided over rock
label | – 150mm bedding sand provided above conduit
label | Reference Documents: C.18, Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed, Subcontractor competencies on salesforce
label | WP
label | Responsibility: Site Engineer / QAV
text | Date Completed:
checkpoint | 2.4 - Back Fill of Trenches
label | Frequency: Each Lot
label | Acceptance Criteria: Place and Compact fill in no greater than 300mm layers
label | – minimum 300mm 20mm Class 3 FCR below pavement/ground level
label | – Where trench passes under load bearing zones maximum 200mm layers
label | – conduits under area to be paved backfilled with select back fill to subgrade level
label | – conduits under area not to be paved backfilled with select fill to 0.4m above top of conduit and common back fill above that
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Measure
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 2.6 - Compaction
label | Frequency: Each Lot
label | Acceptance Criteria: Superintendent to inspect testing and compaction of subgrade
label | • Post compaction falling cone penetrometer >7 blows per 300mm
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | HP
label | Responsibility: Site Engineer
text | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.7 - Compaction
label | Frequency: Once, prior to use of backfill >40mm
label | Acceptance Criteria: Detailed proposals for the compaction of backfill materials of nominal size greater than 40 mm shall be submitted to the superintendent for review before commencing work.
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: Correspondence with superintendent
label | WP
label | Responsibility: Site Engineer / QAV
text | Date Completed:
checkpoint | 2.8 - Installation of marker tape
label | Frequency: Each Lot
label | Acceptance Criteria: Marker tape is to be installed above each line of conduits in all trenches where electrical and communications conduits are provided. When constructed in a shared trench, it must be ensured that the electrical warning tape is on top.
label | Reference Documents: C.19 TC-2204
label | Inspection / Test Method: Visual inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 2.9 - Cable Pits & Pit Lids
label | Frequency: Each Lot
label | Acceptance Criteria: Cable pits constructed and installed as per drawings
label | • Reinforced concrete apron installed around pits that are in an unsealed area
label | • Heavy pit lid provided where pit is located in a road pavement
label | • All pits, junction boxes or terminal pits for electrical purposes shall be watertight
label | • Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
section | 3 - Completion
checkpoint | 3.1 - Cleaning of Site
label | Frequency: Each Lot
label | Acceptance Criteria: Surplus excavated material shall be removed from site. All affected areas shall be restored to similar conditions that existed prior to work.
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Visual inspection
label | Record of conformity: This ITP signed
label | IP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | 3.2 - Recording/As Built
label | Frequency: Each Lot
label | Acceptance Criteria: Installed location and depth of conduits, and location of pits and pedestals, shall be accurately recorded on as-constructed drawings.
label | • Lot Maps shall be completed to show the extent of works for each lot.
label | Reference Documents: C.19, Drawings
label | Inspection / Test Method: Verify
label | Record of conformity: As Built Drawing
label | SCP
label | Responsibility: Site Engineer
text | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
text | Date:
signoff | Sign ITP