## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Wall Closure Checklist 1 Rough In [A]
section | Wall Closure Checklist 1 Rough In
checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schdule
checkpoint | FCU installed as hight as possible with 5% slop tward the drain point
checkpoint | Thermostat control cabling has been installed
checkpoint | Thermostat location is correct as per RCP
checkpoint | Drains have been run to Tundish and does not protrude wall framing
checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect
checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height
checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
checklist | Ceiling Closure Checklist 1 Rough In [B]
section | Air Conditioning:
checkpoint | Air Conditioning
textbox | Inspection Date:
checkpoint | FCUs are installed and other services are not impeding access to fan coil?
checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
checkpoint | Wiring connected to indoor unit electrical box?
checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
section | Ventilation:
checkpoint | Ventilation
textbox | Inspection Date:
checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
checkpoint | All flex are installed and supported by intact load spreaders?
checkpoint | PVC ducts have been hung at correct height and supported by hanging straps
section | Access Panel:
checkpoint | Access Panel
textbox | Inspection Date:
checkpoint | Access Panel location has been marked on floor as per RCP and has been checked
checkpoint | All other other services do not impede access
checklist | Ventilation Checklist Commissioning [G]
section | Ventilation Checklist Commissioning
checkpoint | Fan has been tested and is operational?
checkpoint | Adequate flow has been achieved in bathroom 1?
checkpoint | Adequate flow has been achieved in ensuite?
checkpoint | Adequate flow has been achieved in laundry?
checkpoint | Flexible ducts on the right location and not jammed?
checkpoint | Range hood has been tested and is operational?
checklist | Wall Closure Checklist 2 Rough In [P]
section | Wall Closure Checklist 2 Rough In
checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schdule?
checkpoint | FCU installed as hight as possible with 5% slop tward the drain point?
checkpoint | Thermostat control and zone control cabling has been installed and location is correct?
checkpoint | Drains have been run to Tundish and does not protrude wall framing?
checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect?
checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height?
checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
checklist | Ceiling Closure Checklist 2 Rough In [Q]
section | Air Conditioning:
checkpoint | Air Conditioning
textbox | Inspection Date:
checkpoint | FCU’s are installed and other services are not impeding access to fan coil?
checkpoint | Wiring connected to indoor unit electrical box?
checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
checkpoint | FCU flexible ducts installed and supported by intact load spreader?
checkpoint | Zone motors are installed and connected with junction boxes?
checkpoint | Zone motors is side face?
checkpoint | Supply boxes are installed and supported at correct location in the middle of bulkhead height?
section | Ventilation:
checkpoint | Ventilation
textbox | Inspection Date:
checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
checkpoint | All flex are installed and supported by intact load spreaders?
checkpoint | Flexible ducts on the right location and not jammed?
checkpoint | PVC ducts have been hung at correct height and supported by hanging straps?
section | Access Panel:
checkpoint | Access Panel
textbox | Inspection Date:
checkpoint | Access Panel location has been marked on floor as per RCP and has been checked?
checkpoint | All other other services do not impede access?