## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-024 - Overhead Pole Installation | itp |  |  |  |  | ITP-024 - Overhead Pole Installation
section | Preliminary Works
checkpoint | 1.1 Approval of OHP Layout and Rake
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Check that layout designs satisfy the requirements of the Principal, and drawings are approved for construction.
label | ○ Confirm pole rake bearing and grade.
label | REFERENCE DOCUMENTS: Plan Approved for Construction
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer / Yarra Trams
textbox | Date Completed:
checkpoint | 1.2 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings
label | – all drawings are the latest revision
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.3 Ensure Safety and Environmental Measures
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP.
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.4 Services
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Check DBYD records for any known existing services in the area.
label | ○ Service proving is required to ensure all service locations are known.
label | REFERENCE DOCUMENTS: DBYD Records and Inspection
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed Receival and Inspection Checklist
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.5 Lift Plan
label | FREQUENCY: Prior to pole erection
label | ACCEPTANCE CRITERIA: Ensure a lift plan has been prepared for the lift to mitigate against the risk of lifting the overhead poles near a live overhead power line.
label | REFERENCE DOCUMENTS: WP 02 Cl 3.7
label | INSPECTION/TEST METHOD: Veify
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.6 Pole Type and Quality Conformance
label | FREQUENCY: Each Pole
label | ACCEPTANCE CRITERIA: Principal Supplied Poles and Rag Bolts shall be examined for any damage, corrosion and rust. The materials shall be check for conformance to requirements.
label | ○ Ensure that draw rope is installed prior to pole erection if required and galvanising tags are removed.
label | REFERENCE DOCUMENTS: Contract Drawings, YT Tram Overhead Construction Specification 2013
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed off, Recivable Inspection Checklist
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
section | Construction Works
checkpoint | 2.1 Hole Excavation
label | FREQUENCY: Each Pole
label | ACCEPTANCE CRITERIA: Each hole shall first include a bored hole of uniform diameter throughout the entire depth, 200mm lower than the embedment depth specified on contract drawing.
label | ○ Boring direction shall be in line with specified new pole rake
label | ○ Diameter of the hole shall always be at minimum 100mm greater than the diameter of the pole.
label | REFERENCE DOCUMENTS: Contract Drawings, YT Tram Overhead Construction Specification 2013
label | INSPECTION/TEST METHOD: Inspection/Verify
label | RECORD OF CONFORMITY: This ITP signed off
label | WP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.2 Pole Setting
label | FREQUENCY: Each Pole
label | ACCEPTANCE CRITERIA: Ensure that poles are set as per IFC drawings.
label | REFERENCE DOCUMENTS: Contract Drawings, YT Tram Overhead Construction Specification 2013
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | WP
label | RESPONSIBILITY: Fulton Hogan Foreman
textbox | Date Completed:
checkpoint | 2.3 Pole Rake
label | FREQUENCY: Each Pole
label | ACCEPTANCE CRITERIA: Ensure that poles are set to rake as per IFC drawings.
label | REFERENCE DOCUMENTS: Contract Drawings, YT Tram Overhead Construction Specification 2013
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed off
label | IP
label | RESPONSIBILITY: Fulton Hogan Foreman
textbox | Date Completed:
section | Testing
checkpoint | 3.1 Visual Inspection
label | FREQUENCY: Each pole
label | ACCEPTANCE CRITERIA: Surface of each pole shall be visually inspected for any damage, corrosion or rust before and after erection
label | REFERENCE DOCUMENTS: Contract Drawings, YT Tram Overhead Construction Specification 2013
label | INSPECTION/TEST METHOD: verify
label | RECORD OF CONFORMITY: Visual inspection
label | IP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: