## Master List Templates
Id | Type | Name | Values | Prompting Name
2eb8b747-aac2-4c34-9b7d-f94e1d36f833 | checklist | 1x Shower Tray |  | 1x Shower Tray
9d456cab-3235-4ff6-b7ad-69cf820ff28c | section | Details
21244efe-2dad-4243-8c92-7569afcadfd3 | checkpoint | Shower Tray Installed Level
5e0d76a5-edb4-4515-a1fe-58a234a753bf | checkpoint | Flood Test Shower Tray
aa6479cb-cd6d-429a-b842-810489178275 | checklist | 10) Add Pipework Testsheet |  | Pipework Test sheet
d1980393-ca25-459e-9636-6d0ed0b9ce10 | checkpoint-no-value | Flush – All pipework installs to be flushed for minimum of 2 minutes on full with maximum pressure available.
d8f6afee-178f-5623-9a55-0d7161507f14 | textbox | Duration
4adb10c1-b5bf-59da-9b08-afb7c883e770 | textbox | Free Flowing
a4750f49-3849-42b0-a074-fa8bce13be36 | checkpoint-no-value | Drop Test – Pipework to be subjected to a drop test. No less than 3 drops. Test is used to confirm pipework will withstand environmental extremes.
9865a24f-79e0-5407-a9e6-860c3cf9f860 | textbox | 1st test pressure:
7ae79782-9672-543b-b649-9177461af2b3 | textbox | Duration:
e8b0b3cc-914a-5158-97df-f86114ffadcc | textbox | Rest time:
bd210b68-314e-5c96-8829-4b95be83e345 | textbox | 2nd test pressure:
6978b25b-0412-5d76-b470-3f28968544e1 | textbox | Duration:
7903afa1-e99b-51f4-a619-0c62df00c937 | textbox | Rest time:
90b6d940-5830-5433-9113-28ac537973ac | textbox | 3rd test pressure:
2b8b183e-c90a-5c8a-8914-78f49838c10e | textbox | Rest time:
ee70ed2a-cb8f-540d-a945-e573d4410be9 | textbox | Duration:
97a4c0c6-7c46-4297-ae5f-7d965d4c4944 | checkpoint-no-value | Hydro static test – Pipework to be subjected to a hydrostatic test for no less than 30mins. Record pressure drop if any. Acceptable drops are allowed if within manufacturers allowances.
b3e10a5f-f51f-539b-a48d-2c8a573b1e6c | textbox | Test pressure:
5ae82a22-d264-518d-9c63-7fe2d8331c4c | textbox | Duration:
0c917a2b-fe46-52fe-80a2-893ae0810c2f | textbox | Drop:
b7782ed4-bab3-4af5-8896-91919df6059d | checklist | 25) Add Fire Penetration |  | Label #
2e4d5179-62a3-4a31-ada5-ec768adcec45 | checkpoint-no-value | Has smoke seal been used?
78e9fd5a-7e08-4dac-a15b-915b3a117651 | radio |  | No,Yes
7957aec9-a6c4-498c-bb43-963d3f1473d2 | checkpoint-no-value | What system has been used?
3c7ff7de-4a92-4858-9e83-e004aa1b5423 | tickbox | Collar
1e6aa794-5429-4266-9bac-7bcf08cd789d | tickbox | Wrap
1db1676d-8099-4c10-8211-b286724084dc | tickbox | Other
040c0e22-f74a-41de-8770-cbf20b423db6 | textbox | Please Specify:
1ca1f750-c25b-450e-a7a5-801c2e511fff | checklist | Accessible Shower Bathroom Checklist |  | Accessible Shower Bathroom Checklist
514ae9bd-303c-43c1-b20c-0c9d5b116121 | section | Details
6e640eeb-5296-4a1b-ac85-2a11ac0bcceb | checkpoint | Set-Out Meets Code
a57ea0d0-c959-4940-8dc3-836ed8b50efe | checkpoint | Silicone To Prevent Water Hammer
eae2b5d6-a33d-4989-87dd-3b2702823d0e | checkpoint | Test To 1500Kpa
459d5dcd-2a0c-4694-8499-8f8f81929a93 | checklist | Acoustic Lagging Checklist |  | Acoustic Lagging Checklist
a747a9e8-be46-42a2-b028-b54218fccef3 | section | Details
ea96b98f-7723-4f3f-bc10-065638659051 | checkpoint | Relevant Pipework Lagged
b6d9d6bd-3f1e-436e-85d2-e6d5808645a6 | checkpoint | Lagging Tape Around Joints
352750a8-182f-4003-b0e1-ea8853d83a68 | checkpoint | Blue Strapping And Buckles Every 1 Metre
5a77b5c5-dc2a-4c6f-bfc8-68fb47d37d5d | checkpoint | Pipe Labels After Lagging
0e02bf97-a957-462a-b92e-786792780987 | checklist | Add FF |  | First Fix
501f05b8-22ec-4723-a29f-09be3badc567 | checkpoint | Is the fixture in the right position?
0c454c2f-defb-4352-8675-e57e5c3492b1 | checkpoint | Are pipes coming out the straight?
e2b6fc21-931f-4bb7-b116-838eb58e5111 | checkpoint | Are fixings nogs correct?
e070a2d2-c916-49c1-88b1-070c42deb30e | checkpoint | Has the pipework been tested?
31964b0a-3a2d-47fb-b53b-6ab8ef55b956 | checklist | Add Fit Off |  | Fit Off
c1f80d74-0d56-4aa3-8f9a-6d434cc94f5d | checkpoint | Are all cover flanges installed?
4193bff0-7f4c-4511-9482-efe1de2a8223 | checkpoint | Is fixture stable and installed correctly?
5ad46ee6-f713-49a5-bc13-59d8871d1e0e | checkpoint | Is the fixture free from damage?
4756788b-bf65-46bd-a02d-6498c385a628 | checkpoint | Has the fixture been tested?
0b5543a2-2ae1-4093-98c7-c6e49ef49bee | checklist | Add Potable Water Pressure Test Sheet |  | Pipework Test sheet
c8a2098e-55d7-4369-8e43-fdd395480617 | checkpoint | Photos attached - Pressure gauge and/or flood test
3f37ea2b-93ab-4609-8ddb-252cc7881877 | checkpoint-no-value | Flush – All pipework installs to be flushed for minimum of 2 minutes on full with maximum pressure available.
ed23f1c7-444a-566d-a29e-38119d040174 | textbox | Duration
af7f107f-5d26-5bb5-b450-90b885403dc1 | textbox | Free Flowing
2a0fbd93-0b41-5efc-9f64-8c95da2082b6 | textbox | 1st test pressure:
d61089fa-8b03-5bcb-9454-423481471f3f | textbox | Duration:
a40af1dd-288a-5a3f-bd28-b91dab4b7e9b | textbox | Rest time:
b869faef-f2cc-50f6-be14-98554def90ff | textbox | 2nd test pressure:
e21eb5e2-0c72-5801-9952-d3e63f363764 | textbox | Duration:
0d1273f0-cfa1-57cd-a332-7cd945cda7f0 | textbox | Rest time:
221b8caa-01cf-51c2-8de4-22783743092a | textbox | 3rd test pressure:
4ba39cd5-e00d-5a52-9505-16c05ec085d5 | textbox | Rest time:
896f1d90-6771-53e6-929b-cb0a27bb6c73 | textbox | Duration:
64fe4728-46e1-4dda-a78d-cb797b9fc68a | checkpoint-no-value | Drop Test – Pipework to be subjected to a drop test. No less than 3 drops. Test is used to confirm pipework will withstand environmental extremes.
157384b9-4213-5a75-8b4c-ab40f0ecde8f | textbox | 1st test pressure:
74ecf99f-5463-573c-9dd7-8bacb682479c | textbox | Duration:
5bedd50c-83a3-5534-9466-480ab41fbcc9 | textbox | Rest time:
be3c07fd-aa42-5940-a868-5c5d1c2c2cca | textbox | 2nd test pressure:
f680fd7e-b115-5bd9-9531-d367b4b1fcd8 | textbox | Duration:
54484d8e-65a7-5bc1-be54-c161e8613e3c | textbox | Rest time:
f3e07bac-a8e5-5d27-9f93-7e8a54d3a6f0 | textbox | 3rd test pressure:
d9f5b3a5-dcc9-5d7a-b265-9bbc5af52787 | textbox | Rest time:
254270fc-23cb-5428-8c13-0ca157835e4c | textbox | Duration:
6018fe3e-694d-5b25-9113-b5ea0f3b0d33 | textbox | Test pressure:
8a206918-3dcd-5a14-8da4-cbdb2daa250c | textbox | Duration:
31f0c50d-430b-5c46-8246-c13508f6b98e | textbox | Drop:
8ce0b542-958d-437b-8edb-a38e062646d7 | checkpoint-no-value | Hydro static test – Pipework to be subjected to a hydrostatic test for no less than 30mins. Record pressure drop if any. Acceptable drops are allowed if within manufacturers allowances.
32b429c1-5861-5fa4-9248-ce5fdd30febb | textbox | Test pressure:
ed4a6e75-787d-586b-952c-db6cd2909069 | textbox | Duration:
6519e333-3098-5950-af58-da3c01422704 | textbox | Drop:
cc231d8f-4878-4143-a006-9a20c57006c9 | checklist | Aquatherm Pressure Test Sheet |  | Aquatherm Pressure Test Sheet
5e626c63-9933-4ea9-adbc-8886c94872a6 | checkpoint | Installation Details
93fc2cce-4a6e-4a48-a85b-8e9dac04a136 | button | Type of Installation | Commercial,Domestic
0891b48d-28be-4564-8cd2-765c1aac9253 | dropdown | Type of Pipe: | Aquatherm blue pipe,Aquatherm green pipe,Aquatherm grey pipe,Aquatherm lilac pipe,Aquatherm orange system,Aquatherm red pipe
44d0058f-38ed-4e3c-905f-383f77f9f640 | textbox | Time Testing Started:
25abef4f-adca-4bf1-9248-cc84663ac6f8 | textbox | Time Testing Finished:
dc5a2b5a-de0a-4f63-bc72-a889bd0a74df | textbox | Test Period (minutes):
e6ef9777-906e-424b-8329-626a7151f33d | textbox | Installers #:
f968f898-ef62-4e76-93f9-0773cb6a0a59 | checkpoint | Declaration: I declare that I have installed the above product in accordance with aquatherm specifications with no branding mix
e0cd90ab-c1df-4201-8246-569943f8645a | textbox | Name:
1845f72c-61da-4748-8ea7-a284c3b47d11 | checklist | Balcony - 2nd Fix Checklist |  | Balcony
4ae96957-196b-4c1c-825e-563b46aef006 | section | Details
13cbd098-fdb7-4259-8c90-4f802943a407 | checkpoint | Balcony outlet grate installed
5c165103-1dc0-4db7-8f63-ff40f1b82816 | checkpoint | Balcony overflow grate installed
08c5c209-3511-45f9-88a4-708104c89487 | checkpoint | Downpipe installed level and clipped
9f783318-5e75-453e-bd68-18452255941d | checkpoint | Soffit cover installed
455861b4-076c-4c85-9ea4-b8357c380f00 | checklist | Balcony - Commissioning Checklist |  | Balcony
366a5236-acde-4eb5-b028-f219529ff276 | section | Details
8d213abe-98aa-4398-8438-24383767ccbd | checkpoint | Balcony outlet grate are free of debris
7766d825-c3ec-4e28-862a-836d89d0050d | checklist | Balcony Checklist |  | Balcony Checklist
90435513-a30b-4055-a0e3-7854837cc3fa | section | Details
27354a66-f027-4e33-95a7-c485b4abb12d | checkpoint | Allthrough Installed
849035b7-826c-4043-a6b1-991adf5d4ac1 | checkpoint | Overflow Flange Installed
43f43c2a-bca4-409d-bd67-f0e4046ae10e | checkpoint | Downpipe Flange Installed
e0add3f1-2627-4aca-a978-d4ada5dd2479 | checklist | Bath checklist |  | Bath checklist
0a7f00a6-6664-4ef1-a2f7-7b3fab848cb1 | checkpoint | Nogging for all fixtures
db236d30-556a-49fa-bde4-31d7bc92d622 | checkpoint | Check plan to confirm heights and centres
7161fe16-07d5-420d-89af-6a30aaa27d3a | checkpoint | Check water hammer, Silicone pipes
eb752e00-7147-4b51-a846-68a7c55645e6 | checkpoint | Check drainage waste
d568025c-af33-4b06-b97b-03f65a2e8ab8 | checklist | Bath Checklist |  | Bath Checklist
8fe5fbeb-3964-464c-8a70-c08475aa0f99 | section | Details
baf45f07-1b48-42de-9b16-e991d91923c8 | checkpoint | Nogging for all fixtures
4ca3380e-433e-4efd-b98a-d5520adebece | checkpoint | Check plan to confirm heights and centres
f030e89e-b3c4-44e0-b030-918bf43eb8c1 | checkpoint | Check water hammer, Silicone pipes
ce20edf8-5893-4ca9-b972-4bcd9f256088 | checkpoint | Check drainage waste
a021218d-0082-4b7c-9eb2-733ed56d39ee | checklist | Bathroom - 2nd Fix Checklist |  | Bathroom
f3fe9dea-4e46-4f59-affb-cf8493d73119 | section | WC 2nd Fix
32b73001-4a1f-4901-8b5a-d6d469d6dba0 | checkpoint | WC siliconed
295db18b-f93c-4109-8f98-42cb9de72f04 | checkpoint | WC installation works are completed ( no leaks present and ready for handover )
8f820352-677e-4e7d-8278-97aeb04b90b4 | section | WHB 2nd Fix
c3a9edc7-c144-4f95-92a2-f9c912684de3 | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
5afc97e9-778d-42fe-8cc2-b95f7dc89c65 | checkpoint | Sink mixer flow rate ( confirm flow rate matches products rating )
fb7c44f5-81b8-449f-b9ed-579ffe9ab144 | checkpoint | Sink mixers hot & cold supplies hooked up correctly ( no cross-over )
f585e5a4-1ad0-4faa-83e9-5208b3826a3b | checkpoint | Vanity works are completed ( no leaks present and ready for handover )
295d1354-3534-4971-839a-a8f55796b071 | section | Shower 2nd Fix
6e7772c2-2d4a-436f-8d94-cf5114e67b3d | checkpoint | Shower elbow installed correctly
09d4346f-2f2f-46ab-925e-ea1495e08345 | checkpoint | Shower elbow has silicone between the wall and back of flange
e1377efa-5639-4e81-8a07-1a486a404916 | checkpoint | Shower hand piece and hose installed correctly ( no leaks present and ready for handover )
3b064ea2-e243-4533-93d1-d135db4628e5 | section | Floor Waste Gully 2nd Fix
7991c901-186d-4d96-9b0d-f871cde4a5fb | checkpoint | Tilers have installed the grate correctly
b0d4b4a4-a283-454f-8276-c1d2857e1564 | checkpoint | FWG is clear of any construction debris and drains freely ( plug off and fill sink of fixtures charging FWG, pull plug, and observe water level of trap to ensure it freely drains. Repeat this several times )
ba5f3539-8ce7-434e-8445-b415b53975a8 | checklist | Bathroom - Commissioning Checklist |  | Bathroom
26bfa7b8-0063-42bc-90dd-d1c3311d18cf | section | WC - Commissioning
7db9cd77-e84a-45b8-9fa2-6e1f06f1c36b | checkpoint | WC siliconed
e1858a8c-cd82-4ae9-9f16-c7128ba0c96b | checkpoint | WC installation works are completed ( no leaks present and ready for handover )
bb8283f4-f07b-44c6-bd72-08d508c49ec9 | section | WHB - Commissioning
1b24e1c2-06e9-4d97-8354-6078597a4f31 | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
2361d0e9-47ba-4376-a8a1-866dbc495644 | checkpoint | Sink mixer flow rate ( confirm flow rate matches products rating )
2a6e1c33-4ebb-455d-b3fe-f0601a7f6472 | checkpoint | Basin mixer aerator removed and cleaner of any debris
e5d25c58-3f2b-486a-9297-bf543d1c2d98 | section | Shower - Commissioning
75cfb1b8-c623-4e7a-b288-222c07f0fcc0 | checkpoint | Shower hose filter clear of debris
ba6950e5-7cf5-4759-884c-e5f0b090c4c2 | checklist | Cesspit |  | Cesspit
3e4bf697-2333-4678-9d3b-f1993a8a5235 | section | Details
14351010-2edd-48a0-936f-cd35e1f42a7d | checkpoint | Is the sump set on correct LL
3cdb946c-4504-4cda-ace1-75e6184d0c08 | checkpoint | Installation Process
afa3b8ab-8a28-4279-b800-4d5670620f2b | checkpoint | Council Inspection and As-Built
a20e68e3-7eb9-4a4b-9030-61b18ae528c5 | checklist | Cesspit Checklist |  | Cesspit
494bdc57-4e33-46e9-a62c-0e87c23ca4e0 | checkpoint | Is the sump set on correct LL
526d8dde-c8a8-46d2-90f6-d412dd03cab6 | checkpoint | Installation Process
a7212117-10b5-4a9b-a978-6d427e879dfc | checkpoint | Council Inspection and As-Built
4dcfa55e-0091-4345-b2e2-5072341b4b1e | checklist | Dishwasher |  | Dishwasher
08931c89-0a06-4812-9bc8-df9b602c7c23 | section | Details
d3be7398-e07b-4e9d-b751-56bf90fcc437 | checkpoint | Water and waste connected – attach photo
f883e628-f9a7-4441-a483-fdc5ff7ba91f | checkpoint | Installed level, attach photo
ecdb910c-2f5a-42b2-9d83-366b471d8403 | checklist | Downpipes + Decks Checklist |  | Downpipes + Decks Checklist
e8b800f3-22d8-4ccb-841e-d4bd0dcc6089 | section | Details
7296e3b9-e91e-42a3-9bb8-42408b7bd9d2 | checkpoint | Flanges Installed
de6bea18-6be5-4cf1-826f-3a04a0dc79cb | checkpoint | Domes Installed
736ee5d9-c8d5-4269-a5b1-5eda570c1929 | checkpoint | All Through Installed
8820aea9-e1dc-4319-9be3-a7addee5cc0d | checklist | Drainage Checklist |  | Drainage Checklist
b6a6c946-0d78-48fd-b9cc-8e79852a1eac | checkpoint | Is Pipe Sitting On Bedding
aed47163-32df-4df7-8515-a8e588ab1374 | checkpoint | Is Pipe Installed To Correct Falls On Plan
3f82a26e-85cc-431f-a523-f2d24042e168 | checkpoint | Has Pipe Been Photographed For Q + A
5a0075ce-66ee-45d1-9f69-c525fcf60a35 | checkpoint | Is Pipe Free From Debree
d3f381ba-a5a5-4346-9c4e-cf75ddc0648e | checkpoint | Has Fines Been Installed On Top Of Pipe
25086dd1-bbb7-4f89-9a53-e03323442abf | checklist | Ensuite - 2nd Fix Checklist |  | Ensuite
3473069e-b88a-405b-8b2b-4859d0396b5c | section | WC 2nd Fix
a2e63f15-5a43-4539-9703-4d61f667d8b4 | checkpoint | WC siliconed
17bb45ac-742e-4c52-900d-a9b77e38dd45 | checkpoint | WC installation works are completed ( no leaks present and ready for handover )
ce426cd7-9260-4427-a685-6ca9485ba9d8 | section | WHB 2nd Fix
7bee8630-2bbc-451f-a4f8-667009486126 | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
5414fff6-b7cb-4d18-be45-a38573478651 | checkpoint | Sink mixer flow rate ( confirm flow rate matches products rating )
c4b1a806-6c2b-4793-a975-d3350876f250 | checkpoint | Sink mixers hot & cold supplies hooked up correctly ( no cross-over )
9fd19259-5323-4226-9416-7de2ebf9cba2 | checkpoint | Vanity works are completed ( no leaks present and ready for handover )
1fc1162f-9c57-4598-af80-2a182608a50c | section | Shower 2nd Fix
76c518e7-11db-4b6b-8b3d-f9f02b621186 | checkpoint | Shower elbow installed correctly
dcdff6e5-8084-41c4-abe1-c9ac5c1f8032 | checkpoint | Shower elbow has silicone between the wall and back of flange
22835598-ac5c-44e8-bece-bf5a4318461b | checkpoint | Shower hand piece and hose installed correctly ( no leaks present and ready for handover )
dad8be4c-c40d-4f59-b085-13d4e988d0ba | section | Floor Waste Gully 2nd Fix
fff0901c-fdaf-4d2e-add5-7b6f9528302d | checkpoint | Tilers have installed the grate correctly
4e054149-c6ba-48cb-b8c5-1bbfca851a21 | checkpoint | FWG is clear of any construction debris and drains freely ( plug off and fill sink of fixtures charging FWG, pull plug, and observe water level of trap to ensure it freely drains. Repeat this several times )
8ed91f9b-864a-4009-812d-77ddfc490942 | checklist | Ensuite - Commissioning Checklist |  | Ensuite
5b0740ea-6b29-4aec-86fb-43140e28ebd8 | section | WC - Commissioning
7340e694-4732-449c-85df-1a760fde5310 | checkpoint | WC siliconed
cdd3844b-4533-4493-b286-8b2878db3c89 | checkpoint | WC installation works are completed ( no leaks present and ready for handover )
3c57e70d-1e0a-4309-83f9-6e67e9bc45a1 | section | WHB - Commissioning
d2c0bbc2-974e-4586-82cd-154ecf378efb | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
e86fe56c-db86-4ec6-a6fb-3a63c8543f3c | checkpoint | Sink mixer flow rate ( confirm flow rate matches products rating )
0b09264b-6e19-4e1e-8a9a-ec2975d0fa19 | checkpoint | Basin mixer aerator removed and cleaner of any debris
764e7043-d7f6-4990-877d-54579d61bb98 | section | Shower - Commissioning
99ede956-e3a4-4bdd-8ec0-6b92eefdaaf0 | checkpoint | Shower hose filter clear of debris
ed2353ef-948a-49e3-95de-28e456bd97bf | checklist | Express Plumbing Quality Assurance checks and Commissioning |  | Express Plumbing Quality Assurance checks and Commissioning
0f3c025d-4a9f-4cf1-abb3-288599ba0528 | checkpoint-no-value | Express Plumbing Quality Assurance checks and Commissioning
8cd63223-b1f3-4f34-9910-335b9309577d | note | Express Plumbing uses a online live document system of recording different stages of the construction process through out the build program. With the aid of mobile devices and computers we record with photographic evidence the construction build process, what things look like behind walls and below ground. We follow up these photos with the end product finish and have checkpoints for each fixture to have passed off at each stage so you can be assured of the quality Express Plumbing has archived during your project.
82789061-d20c-448c-bc72-280d357bafaa | note | The system provides a accurate recording of what has happened on site and also provides a means of recording and resolving any defects. During checkpoint sign offs for each fixture a series of questions are asked in relation to the fixture, ie “are the pipes coming out of the wall straight?” or “Has the council inspection been passed?”. If the Express Plumbing site supervisor finds a defect he is able to send a job request immediately to any of his site staff and the repairing staff member is able to take a photo of his repair for the supervisor to approve.
8ecd6366-fa14-4fd0-bd07-51f74df937c9 | note | All dates and time of data entered or altered are recorded next to each question. Our commissioning processes also forms part of this live document with specific fixture questions and photos during the commissioning being recorded i.e. temperature gauge photo of a running hot tap on a basin etc. We are also able to provide our Fire Register through the same system and record locations with the labels and assign a photo of each penetration to that location. We also break down the locations into areas and floors.
de6f5e10-f8f4-436f-a7e4-27ed61710029 | note | As built are also recorded during the project and are loaded into the system before the hole or ceiling is covered in. These can be on request turned into any format you may wish to have these sent to you (there may be additional costs).
f17d3ffd-0b01-489a-92fb-6de7fea2e7ec | note | Express Plumbing supervisor’s are authorised and given access to the specific job they may be running. Access is only given through Web page authorisation from the Express Project Management team. On site teams under the supervisor do not have full access to the system and can only log repairs to defects with in the system. All on site data entry, passing off of fixture, logging of finished works, fire register recording and As built entry may only be preformed by the authorised Express Plumbing Site Supervisor.
34a9eb33-a9be-4cf9-9de4-610933aa9fcb | checkpoint-no-value | QA Hierarchy Flow Chart
f3083c51-d697-4f21-a7e7-216ef499e346 | textbox | Project Manager:
a10cba99-d8df-472c-9941-6d0e90e16089 | textbox | Site Supervisor:
f61c7730-cb04-4122-91d4-98b506629bfa | textbox | Site Defect Repairer:
0e906ed9-d40e-4ac9-a0ac-7fcf34ec4e07 | checklist | Fire Penetration |  | Label #
80b967f8-9a68-4ddd-9018-c6392714a84b | checkpoint-no-value | Has smoke seal been used?
78e9fd5a-7e08-4dac-a15b-915b3a117651 | radio |  | No,Yes
1dfb9a3c-4667-4498-9ed6-deefa5ae8290 | checkpoint-no-value | What system has been used?
3c7ff7de-4a92-4858-9e83-e004aa1b5423 | tickbox | Collar
1e6aa794-5429-4266-9bac-7bcf08cd789d | tickbox | Wrap
1db1676d-8099-4c10-8211-b286724084dc | tickbox | Other
040c0e22-f74a-41de-8770-cbf20b423db6 | textbox | Please Specify:
8aa85385-8c97-4589-b618-93cc57dba6f0 | checklist | First Fix |  | First Fix
23223b68-fcc0-4455-80cb-8dc8ba76f79b | section | Details
87f7cf30-e795-4a3b-9f40-052068d49b92 | checkpoint | Is the correct material used, as specified for the job?
c2ad9842-8446-43a4-95e0-d8568efafc18 | checkpoint | Wing back installed at correct location and height, prior to hardware installation?
10887994-19ff-5ff8-b7af-b086ed5437b1 | note | According to manufacturer specs and architecture design
3a46df18-5f89-49be-9c03-3c4c197b0a67 | checkpoint | Pipework is secured/supported or protected if required
210ab283-a4d3-53a0-b6dc-936d64a9eaa1 | note | Min interval 600mm
100b8580-0119-4ad7-9c1a-6f4bfb0817ce | checkpoint | Is the pipe work tested according to hydrostatics pressure of 1500 kpa for a period of no less than 30 min?
29d9e6e8-81fe-5bb8-bb70-a376230d369a | note | Take picture for proof
94c8f91d-098a-4b92-8f48-11a161d9cdf7 | checkpoint | Waste at correct height and location?
177702f8-a839-5124-98f3-ba25056d1b88 | note | According to fixture manufacturer specs and architecture design
e04b16dd-9563-437b-bfdb-b09171604362 | checkpoint | Additional Comments
a5be3335-f1f4-4c9b-af1c-4c3d4c17abae | checklist | First Fix Checklist |  | First Fix Checklist
3ef0fb46-403d-4f64-8942-097c3de869fc | section | Details
44225b59-0ef4-47d6-b6b9-f215f4a7677b | checkpoint | Nogging For All Fixtures
55f01bee-4410-4ff1-b9f9-b8fc12417b4e | checkpoint | Check Plan To Confirm Heights And Centres
c0fb8807-83e2-4841-be73-bb7cbd957ba2 | checkpoint | Check Water Hammer, Silicone Pipes
c30087e7-e178-4105-83a3-04145b0df4de | checkpoint | Acoustic Lagging
da63679f-058a-477f-92db-e4d5636abe51 | checkpoint | Test All Pipework To 1500Kpa
0fbecbc9-c54c-49c0-a784-b0fb46973bd2 | checklist | Flood Test Sheet |  | Flood Test Sheet
13fadb12-e93e-4252-bd74-6db054d67205 | checkpoint | Flood Test Date
68dc6c58-f370-407b-89ab-886b69f56a39 | checkpoint | Flood Test Duration
d5aa4dbf-c909-4ff1-a8a7-3695981c9bf3 | checkpoint | No sign of water on any joints
bbdd104d-7581-4e59-8176-c115dcbdc501 | checkpoint | No water drop during test
d2373986-6c8e-45c2-b551-332f38602942 | checklist | FWG First Fix Checklist |  | FWG First Fix
337d7a4d-3b91-49f3-ba37-32df096bf080 | checkpoint | Correct Position
23c57d0c-b87c-4361-8c25-70221c1243af | checkpoint | Flange Level
dfaccaa5-2563-4544-a3b8-60d810e3249a | checkpoint | Construction Cap On
85dc5147-7caf-45cd-acef-8cac8ef45248 | checkpoint | Tested
485d96a8-66c7-4620-bf9f-360a8aa4a8ff | checklist | FWG Second Fix Checklist |  | FWG Second Fix
79cb5d8d-10cb-40aa-831a-67f397e265f2 | checkpoint | Has the fixture been fitted correctly
6abc2235-8225-4553-b664-2d1ac88e539d | checkpoint | Has the fixture been tested (add photos)
29297a00-57d9-4ad0-bd7e-7418d925aeb1 | checkpoint | Is the silicone neat and tidy
442263cb-610f-4acc-97bc-9bac99479a77 | checkpoint | Is the fixture free from damage
4378cafb-8bf8-40a2-8aac-43a884cb35bd | checkpoint | Have the lines been flushed
4bc6aabb-0885-4cf3-a8d3-c3d4535cf673 | checkpoint | Is the fixture free from leaks
997ece2e-1445-4d37-8b6d-788c880799c3 | checklist | Gas Checklist |  | Gas Checklist
43b69ee2-12c0-406f-bc34-f4f4f57f59bf | section | Details
69b53aa8-55e1-42cd-881a-995a7e6c00a9 | checkpoint | Pipe Tested To 7Kpa
40672335-0584-4b3a-a7bb-60062d46f314 | checkpoint | Pipe Clearly Labelled Gas
c0b8b1a9-ac05-45d2-8f4f-b0ae1cc9eaa8 | checklist | Hand Basin |  | Hand Basin
aa8244f6-a538-4f8f-a9e2-200832f50758 | checkpoint | Nogs for all Fixing
1ff2383b-7d2f-4d58-8792-78dd7d79ea22 | checkpoint | Check plan to confirm Heights
d84f88b2-ca99-491b-8db9-45f38716b832 | checkpoint | Check Water Hammering, Silicone Pipes
4187745a-6ac5-4599-8611-ab10c07ecee0 | checklist | Hose taps |  | Hose Taps Checklist
660b8e7b-46c2-448d-88ee-e2c6a025ec32 | section | Checks
47444bc1-4d29-4309-8ccd-9286594db43a | checkpoint | Position Correct
faac4ec7-3c40-4064-809f-a96115dcea58 | checkpoint | Pipes coming out of wall straight
301a1d27-7303-4ba2-bc2d-3af6f7cbd62e | checkpoint | Fixings nogs in place
d20fc81c-c550-4e2d-be94-0ca4886f401b | checkpoint | Prevention against waterhammer
103fe4f7-708d-4c41-85e8-02568b4879e4 | checkpoint | All joints watertight and tested
cb7ebe0e-42ed-4ec6-9ae9-550b688415c0 | checkpoint | Has fire rating been completed?
076aca9a-8318-47ef-9efe-3d2ae918e6ce | checklist | Hose Taps Checklist |  | Hose Taps Checklist
1c104346-7dae-4e4a-99fd-8808cc7da0a8 | section | Details
f4704dfb-d7d2-4c15-a247-aba5c50c6226 | checkpoint | Position Correct
1a48e0c3-ee73-44dd-9112-b6aaa92fa394 | checkpoint | Pipes coming out of wall straight
3901f90b-2071-4b3f-a241-5a3ce6c1c35d | checkpoint | Fixings nogs in place
d4306926-6ef1-4061-89a4-6a10d2471e6e | checkpoint | Prevention against waterhammer
904a4cc2-d579-49c2-bb7d-804c228e3ba8 | checkpoint | All joints watertight and tested
ba55324d-7d24-4d99-a51f-d28ffd6d0e04 | checkpoint | Has fire rating been completed?
ef6b5c3b-dc0c-4e73-b3bb-2f80d9c9a03e | checklist | Hot Water Cylinder - 2nd Fix Checklist |  | Hot Water Cylinder
a4402f50-313c-4b5b-9da5-33f199f24ff3 | section | Details
130e7afd-5d4a-402c-a2ca-a6d3b382ef65 | checkpoint | Plinth installed and safe tray connected up
c010afd1-6817-4972-a909-5b6e26ccb924 | checkpoint | Seismic restraints installed for 250Ltr HWC ( 3x strapping and full height vertical blocking )
a2e2beb5-4212-4458-be4d-a7f102caf635 | checkpoint | Valve train installed correctly
45d44aec-ebf9-4ab9-b0ed-4671b77350cf | checkpoint | Safety valve relief lines installed and connected into safe tray TD correctly
6851a616-9990-48bf-9d96-50706a7e9797 | checkpoint | Water supply on and connections checked for leaks and installation is sound
82df402a-8074-422d-a958-41988263f955 | checklist | Hot Water Cylinder - Commissioning Checklist |  | Hot Water Cylinder
3d57b438-fa30-4d63-a94f-ee9c9d06b110 | section | HWC - Commissioning
7e5a0158-ba63-4827-8de6-92b574ffdeef | checkpoint | Tempering valve set to 50°C
0112bb7b-2c7b-4de5-9f25-8981b3f30b06 | checkpoint | TPR and Cold Water Expansion valve drains manually opened to check operation ( relief drains run freely without backing up causing leakage )
676e865a-7669-4d1c-839f-d6b242083383 | checklist | Hot Water Cylinder Checklist |  | Hot Water Cylinder Checklist
2af41e84-55d3-4de7-8728-8bdd6b8b4ea4 | checkpoint | Cold Feed With Isolator
e157aedb-8d15-47d1-8ee5-d9fee2d54095 | checkpoint | Hot And Cold Installed
a1c99102-e00a-448c-8717-a3fb70c89502 | checkpoint | Tundish In
2e224acb-f8cc-4c21-a6c0-b4a32d27dbda | checkpoint | Has Nogs Been Installed For Seismics
58ce7311-6cc7-4ba6-9391-faf40c415da2 | checkpoint | Correct Positioning & Heights
745c8ff0-20bc-4733-bf55-75be0a1a2bcc | checklist | Kitchen - 2nd Fix Checklist |  | Kitchen
33988f5d-a416-4783-b1d6-f7bda8f40975 | section | Details
b5e3102c-1ff7-4d43-9d22-a5bdc53fe6f6 | checkpoint | Kitchen works are completed ( no leaks present and ready for handover )
b2cd014b-c571-4a61-ac25-c4fac6daf265 | checklist | Kitchen - Commissioning Checklist |  | Kitchen
2455acac-f2f2-4d07-9637-afd7413ff7b3 | section | Details
4e1d66ce-0b07-4204-a6fb-a6f5ec7b4cf3 | checkpoint | Kitchen mixer aerator clear of debris
e337ce38-cac3-4caa-b398-415bafe69a27 | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
10c1f572-f286-4e9f-9e5d-2e3121f9ecb6 | checkpoint | Sink mixer flow rate ( confirm flow rate matches products rating )
ec33bf4a-c787-4858-81f1-701e4e149e1c | checkpoint | Sink mixers hot & cold supplies hooked up correctly ( no cross-over )
129f8100-7d7a-446a-81ff-7e5a483a0318 | checkpoint | Dishwasher run through a cycle and leak free
e1373e07-c60d-4196-ab6f-1a8fabb7de27 | checklist | Kitchen Checklist |  | Kitchen Checklist
2d06913e-3f91-4397-8577-58d1d8ffa38b | section | Details
0c0b2b05-06ab-4e2c-94a1-8cfc5cda9d33 | checkpoint | Hot And Cold Water Installed Correct Height
612fc0b6-b07b-423b-a0c0-fb09ba34d602 | checkpoint | Waste Installed Correct Height
b83b0c5f-b295-4561-9a13-6de669cc62d1 | checkpoint | Check Hot And Cold For Crossover
bd011db4-10e6-4275-8a11-d787854141d6 | checkpoint | Tested To 1500Kpa
f72f8ea4-aa05-4366-8e71-96f73bd33762 | checklist | Laundry |  | Laundry
b08f1bd4-77cf-4b81-b19c-067247fd5791 | section | Details
a5e6f50f-6ca0-48b2-8195-c9d2f89c1d3c | checkpoint | Nogs for all Fixing
f04a10ec-8d98-4da5-8adb-47e1f7ef76bb | checkpoint | Check plan to confirm Heights
70751bd6-3847-4e7a-a9ae-1e7b22fe1af9 | checkpoint | Check Water Hammering, Silicone Pipes
8403a94b-c050-45ed-9f0a-37c5001195f9 | checklist | Laundry - Commissioning Checklist |  | Laundry
3024f8f8-708b-4187-b4c1-66639744039a | section | Details
5b5613bd-a22a-4570-a636-b0c07b2d4a86 | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
27293295-d542-41da-8222-cf2a286b7920 | checkpoint | Sink mixers hot & cold supplies hooked up correctly ( no cross-over )
d3081f84-710d-4a97-aa63-1cc55e217e6c | checkpoint | Laundry works are completed ( no leaks present and ready for handover )
844ea86d-a00f-4d89-9aa0-fa40cabea741 | checklist | Laundry Tub - 2nd Fix Checklist |  | Laundry Tub
f191226c-e7ea-49c5-97ac-5d49099128e2 | section | Details
a3e9fa30-6ad7-4c9e-9586-fcfee9f1abac | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
8ebeab49-5547-482c-b266-d6a3f9c61204 | checkpoint | Sink mixers hot & cold supplies hooked up correctly ( no cross-over )
0d6479ef-c024-4c03-afb2-b5f506450d68 | checkpoint | Laundry works are completed ( no leaks present and ready for handover )
d70bd1aa-469d-45cb-9cac-0798c0394f74 | checklist | Manhole Checklist |  | Manhole Checklist
acb7b9fd-9a5c-42d2-9360-60c11a882bfa | section | Details
38b1b062-ce01-4bd1-8c01-f1038f982f8e | checkpoint | Check Existing RL's Of Manhole
608f576a-2343-4fa2-8e75-4e06a9fe62a1 | checkpoint | Check Invert And Grade
d40afc98-865f-4b02-bfbd-14c289db5d77 | checkpoint | Seal Pipe Into Manhole
4124a890-1ae6-4434-8ed5-067d9baf0aa4 | checkpoint | Install Manhole Lid At Finished Height
e66b54b0-053b-4e98-8c92-a52d73e9035d | checkpoint | Benching To Be Complete
6fe6b39d-1cf2-4f2c-8a0c-68d0be25ede1 | checklist | Meter Commissioning Report |  | Meter Commissioning Report
85929bc3-6888-4be6-bb4a-93c5eda0de15 | checkpoint | Is water meter installed according to IFC and is water live?
cac4f757-710a-4f17-9f4f-e12fe4ff9121 | textbox | Water meter reading at handover:
d803dc8a-ecb6-42ce-8759-9378589b3cd1 | textbox | Water meter size:
b8c03996-55b7-41c8-84d5-60a560ab574e | textbox | Water meter asset number:
1c20080e-fca3-41b2-84a0-341f39794071 | textbox | Water meter serial number:
7a55e27a-31af-4252-a831-17193ecdf8f3 | checkpoint | Is gas meter installed according to IFC and is water live?
c2fa59eb-8248-4731-b179-7bda6945f375 | textbox | Gas meter reading at handover:
62725d7b-5058-4062-bab3-2e83930b6601 | textbox | Gas meter size:
553dc1e7-50bc-4834-86f7-69aecf8e12dd | textbox | Gas meter asset number:
ecb1be83-ab77-4686-9441-a0b928525daf | textbox | Gas meter serial number:
2b8db3b4-f326-4c7a-b0f3-547915a1ec77 | checklist | Miscellaneous Test Sheet |  | Miscellaneous Test Sheet
ec269238-ebd3-42d4-85d0-5add4ce6915d | checkpoint | Miscellaneous test sheet
01073ff0-e05a-4a68-8e87-0366a4dfe998 | checklist | Novacoil Checklist |  | Novacoil Checklist
f801030d-3348-4af8-beea-e6d9b3080720 | checkpoint | Are The Heights Set Up Correct
9ec46c09-bf9a-48e2-a585-f7f46623eb33 | checkpoint | 100mm Cover Of Around All The Pipes
1d926fcd-52d6-4a6f-9bac-b133e7940757 | checkpoint | Rodding Points To Be Added In To Surface
a1235306-1602-406e-a894-1b8e609b7d71 | checkpoint | Megaflow Adaptors Installed
ff457fef-aa5c-4574-85fa-4632397ce4c4 | checklist | ORG Checklist |  | ORG Checklist
cdd72e15-bedb-4394-a879-c562d61085f8 | checkpoint | Installed in correct location
148fe040-a82f-4e8d-a3cb-11e36c9a88d8 | checkpoint | Riser level
9dd90fbe-1286-4532-9184-00ca982b6e03 | checkpoint | Is the ORG fixture connection done
1fda1adc-4e43-4e6e-a6e4-bf0906f0ccad | checkpoint | Concrete placed under the gully base
c669cd36-bab5-4709-bfff-e2e146bd306e | checkpoint | Gully dish installed
83ca7832-c4e9-4194-a21f-eea924fca6e2 | checklist | Photos |  | Photos
11881716-d32d-4e98-b218-5de09fe5cbab | checkpoint | Attach Photos
26f02300-68cc-4221-a69d-286c4cfda69c | checklist | Photos & Commissioning |  | Photos & Commissioning
bdad2a2f-7c15-42d2-be94-6ee2d29fc4b0 | section | Details
21999c53-9348-437c-b3f7-fd55a9647846 | checkpoint | Commissioning
e7805f13-3e62-41d5-8873-a030d5812285 | checkpoint | Attach Photo/s
edb2e2e7-345f-4089-9408-9c0233325b7b | checklist | Powder Room - 2nd Fix Checklist |  | Powder Room
4994b5aa-6f9f-4468-a7ef-fae75928dbd2 | section | WC 2nd Fix
499dca7d-7a0e-43c2-8613-822114e30b78 | checkpoint | WC siliconed
cf94621e-e4f5-433e-b4ee-8c94e711dee3 | checkpoint | WC installation works are completed ( no leaks present and ready for handover )
59e95c5c-b5b2-4f33-b384-b879de280c56 | section | WHB 2nd Fix
6899cac8-e8ca-439e-ac0b-373e2b625001 | checkpoint | Sink mixers hot & cold supplies hooked up correctly ( no cross-over )
c87c6b6c-999f-45ac-983e-061c9f0f4947 | checkpoint | Vanity works completed ( no leaks present and ready for handover )
c544d815-f65f-4eff-b6e5-18aee2d542b5 | checklist | Powder Room - Commissioning Checklist |  | Powder Room
bcf8e041-a018-4cc6-a02b-9ab09af6ed69 | section | WC - Commissioning
4a993dba-ed1d-4d0a-8430-6a5ff93daed5 | checkpoint | WC siliconed
17b35364-7890-40bd-8db1-00659661bf01 | checkpoint | WC installation works are completed ( no leaks present and ready for handover )
d39e93dc-802f-4a5f-a74a-d7ada0174d48 | section | WHB - Commissioning
d8965d58-7aae-40cb-862b-eb024b2004a4 | checkpoint | Sink overflow checked ( take video of test showing mixer on and overflow working )
9c52b512-73e9-4d21-8079-490b23812fb9 | checkpoint | Sink mixer flow rate ( confirm flow rate matches products rating )
2ecdfd4c-ab68-44ae-ad5b-666560748c7f | checkpoint | Basin mixer aerator removed and cleaner of any debris
eefe11df-61f8-41d7-b835-2dff64f20894 | checklist | Pressure Testing Checklist |  | Pressure Testing Checklist
76141745-1305-428f-9093-f2d82effdaed | section | Details
f882205e-bd6e-47e5-9423-96245fec2703 | checkpoint | Pump Up To 1500kpa Minimum
78caa1e1-a8ef-44bc-badc-fd3b901fca1b | checkpoint | Take Photos Of Testing
26222c97-a4e9-434d-af52-ce4770d50e15 | checklist | QA Apartment |  | QA Apartment
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
461c13ab-6d05-4ce6-b2ed-206ce64ddf84 | checkpoint | Upload photos or files
05190aa5-afc0-4a85-8d6c-a1d711e5ffe7 | checklist | QA Checklist |  | QA Checklist
f8e4df91-d700-4631-82b2-0a761ca05612 | section | Roof outlet questions
67fe43fb-93ba-49da-8dc6-3f8b5cd874b2 | checkpoint | Is overflow on correct pipe
2eb9c9f3-14a0-4f21-ba6d-f640f281930f | checkpoint | Are clamp rings secure
fbb745ed-d4ab-4626-8f2c-07deb64cb013 | checkpoint | Is gutter free of debris
019773ee-d6f2-4135-aa68-32d4121f2970 | checkpoint | Has pipework been tested ( Insert photo - mandatory for all testing)
f83e98b1-1b7a-444a-a170-8e596948435a | checkpoint | Is pipework secure to outlet
f79c6153-fd6e-4e9f-b977-a4e44fb1a4e7 | checkpoint | Has acoustic lagging been completed
d939ce97-5e51-4867-aa18-368e06fee5fa | checkpoint | Are the pipes labelled correctly
f8ce6944-4935-4913-b8c3-b432356bd68e | section | Vent Questions
ca0fce35-4b55-4e6e-b9e7-87f7da6458c7 | checkpoint | container
41299ec5-1d03-4a09-818c-a1ef85a6adfe | section | General QA
e1b71c93-3b0e-4a96-88ce-643dbeb3ac5d | checkpoint | Pressure Test Sheets
a3fbbb08-4749-4735-8e28-5f08bfc30deb | checkpoint | Downpipes
3d46da30-d618-4a0f-b1a5-8f928adc509e | checkpoint | Service duds
be7ba6c1-7975-492d-a38a-825e49169213 | section | Drainage
36ae3fd5-d5b6-419f-b8ec-a0ca371a7b3d | checkpoint | Are all pipe falling
16305582-6cef-47e6-be40-7f12d92d59ef | checkpoint | All joints secure and tested
0a27bb5b-388d-4841-99df-fe2498c9f292 | checkpoint | Are all upstands labelled
e1356acb-ed5b-4bc8-b270-3b8909af4ee7 | checkpoint | Is backfill complete
df25302d-ab68-429b-9dc2-8da72510fbad | checkpoint | Are all pioe protections in place
6de7c6ff-c513-4a39-90e2-2e5bb84fdd54 | checkpoint | All upstand locations secure
c2d6acfe-c4f4-4977-a883-004661c7a7ad | checkpoint | Has works been signed off by council
b402588e-935a-4441-8f74-f692b1a3d951 | checklist | Second Fix. |  | Second Fix
d8ba3daa-24de-4765-bf9f-6e31b5b2b7a4 | section | Details
ccbecb8f-dc45-4fee-9bc4-2e737237c201 | checkpoint | Is the fixture correctly installed?
10cc93fa-d3f3-50a3-9d55-b9af303bdb7b | note | According to manufacturer specs and architecture design
c2923e18-7012-465b-8167-3fef4738dcef | checkpoint | Is the fixture free of damage?
f670865e-a867-587e-9cd4-01bb05db34c7 | note | Scratches, cracks, chipped areas or stains
f477e0b0-2b1f-47e5-819d-1cbdb7b2a922 | checkpoint | Fixture to be commissioned and checked if any faults require attention
e9505fca-d5f4-5390-842a-43fd8ae27a81 | note | Include leaks
840ff850-25b0-4c23-a8a3-c86687524b74 | checkpoint | Hot water temperature at any sanitary fixture used for disabled bathroom for personal hygiene should not exceed 45 degrees celsius
2d518820-9d42-5d43-b693-4fbb57729829 | note | Accept: kitchen sink min 50 degree celsius - proof with photo
5d29dd10-897c-45d8-86f5-84ea68d5e9e2 | checkpoint | The sanitary fixture siliconing done where required; to be neat and tidy
39e99c5c-29fb-5e78-8f51-4b6f6cab372d | note | Proof with photos
4ec21244-c5a8-488c-9c01-5a2819f7dc78 | checklist | Shower Checklist |  | Shower Checklist
6133e640-f88f-4309-bd32-8965827006f7 | section | Details
1726a2d0-bbbc-469c-b9e6-b515ad181200 | checkpoint | Mixer Sticking Out The Correct Length
c3dcfab0-fe39-46a8-b543-9d40a85c4066 | checkpoint | Mixer Wingback Above 1700 To Prevent Backflow
74278300-18f5-4bdd-bb4e-3358f8940fed | checklist | Stacks + Vents Checklist |  | Stacks + Vents Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
8158c04a-ad96-4798-a823-c6441bfdda0e | checkpoint | Inspection Junction Installed For Testing
b5c83c88-e2a5-4379-8254-0f3386a9485d | checkpoint | Pipe Labels Installed
2be78d64-8fc5-47f2-b2f3-dd1e6d34f7e4 | checkpoint | Mid Level Supports
42d5f588-8194-45fe-80cc-96b4833c20e4 | checkpoint | Write On Test Cap Date Of Test
b63314ef-08b7-4e85-9eb6-0b1cdbcfea24 | checklist | Stand Alone Washing Machine |  | Stand Alone Washing Machine
f8a99d1c-4583-43e4-9488-d9a280153d5b | section | Details
87681c4b-6639-4469-ad07-467eef9990ed | checkpoint | Nogging For All Fixtures
6fa56549-d07b-4259-8eb2-f7a3eba88770 | checkpoint | Check Plan To Confirm Heights And Centres
0de2fa29-2682-4245-b9ab-c1b76467f2ab | checkpoint | Check Water Hammer, Silicone Pipes
7f536846-271f-43a7-9ec3-6299205a840f | checkpoint | Acoustic Lagging
a082bd80-eff5-47ec-b767-b19c45ddeaaa | checkpoint | Test All Pipework To 1500Kpa
743b9dd7-fb61-4e64-8588-02b5903b97b4 | checklist | Storm-Filter |  | Storm-Filter
e2df7ac7-8c1d-4d13-a43e-58c75eae8c7a | section | Details
85ac53bb-5f97-41e1-abf0-3d2a8d6ce928 | checkpoint | Bedding Put In At Correct Height
309a9224-1b83-432b-a8dd-6974e2fe5a29 | checkpoint | Grade Right
19acaf81-e94d-48a1-af5e-fa3364edd9b5 | checkpoint | Check Pipes Is All The Way In
683951d8-55fb-4ff9-af03-ca6f20968757 | checkpoint | As Laid Per Plans
a38e1f9f-ef86-46c0-91b0-597082f366f1 | checkpoint | Filter Clear Of Debris
8ab95003-2f72-43ae-9c0d-4cabe3db78ac | checkpoint | Lid Set To Finished Floor Level
bbaa089a-91de-4b73-9b63-d1eed0533cc9 | checklist | Stormwater Checklist |  | Stormwater Checklist
d39a6fca-8f0f-4440-a898-48944416f3a4 | checkpoint | Relevant Pipework Lagged
787b8ead-c08b-4ba3-abad-5556b5dc36a8 | checkpoint | Lagging Tape Around Joints
45d65ffc-15c3-4c79-b3e8-d55e968a4eaf | checkpoint | Blue Strapping And Buckles Every 1 Metre
d28c1bf8-6253-4f24-b905-c1e8f79080fe | checkpoint | Pipe notes After Lagging
d56e8d89-9a77-4025-986e-8500701dc1a1 | checkpoint | Pipe Tested For Leaks
fd5996e9-cafe-4ca7-85e5-57b1842e2618 | checklist | Supertub |  | Supertub
d035be0c-f3b9-41b0-ad44-e1c41dc2466e | section | Details
b4020090-ba4a-4d9e-8439-c6152c4c555e | checkpoint | Nogging For All Fixtures
f3d3122b-56fa-460a-ad01-a0321ef1d630 | checkpoint | Check Plan To Confirm Heights and Centres
9aa0882f-0710-400d-a940-6e54a6ffbc39 | checkpoint | Check Water Hammer, Silicone Pipes
c5e3cb17-9bcd-45b1-933e-98842e95c7a0 | checkpoint | Acoustic Lagging
8c00d38c-7400-4409-a522-cb5cfde53cf4 | checkpoint | Test All Pipework To 1500Kpa
17451e5c-19e5-45c7-a75e-5ab4ee1afdbf | checklist | Toilet Checklist |  | Toilet Checklist
46d191eb-0ced-429b-83cb-f38f551c2d9d | section | Details
2869c4aa-4fa8-4e4c-9686-136fb29f1d47 | checkpoint | Wingback Installed To Correct Height
d2d1e107-cf07-474b-b2d3-123f621032a5 | checkpoint | Waste Installed Correct Distance From Wall
963d18c1-9352-4eb0-86e8-ea10e4241dac | checklist | Underslab - Water (Rename to required Area) |  | Underslab - Water (Rename to required Area)
5f5c3aa5-6970-44e9-8d2c-35aab6deae6d | section | Details
75c76dcb-687a-4d22-8b1d-23ed05f43b68 | checkpoint | Dimension From Center Of Pipe To Reference Point
faa56579-bdf2-48ec-925b-0f2b2a818055 | checkpoint | Pipe Specification
32362812-3c06-49a5-8caf-b7eaac58a5cd | checkpoint | Is The Installation Compliant To As/Nzs 3500:1
a4aca8f9-df6f-4af6-8447-9aef65453c34 | checkpoint | All Joints Are Crimp And Watertightness
37c2695b-f5a4-4a8f-8f3e-1921f5b8333c | checkpoint | Is The Pipe Protected
04af0874-eb32-5600-af81-2db5eed788a9 | radio | Testing Method | High Pressure Air Test,Water Pressure Test
c0046549-d5e9-450e-8bbb-d0575a08f2da | checkpoint | Any Damage On Pipe
57d708ab-ad30-4b99-9640-129357a697cc | checkpoint | Check For Leak Or Pressure Drop
f8bfc0d2-9cbd-4d63-aae8-044d203b2ebd | checkpoint | Is Stub Straight Or Level Both Side
76862192-1cfa-4ffd-8449-52b724cc0b34 | checkpoint | Council Inspection And As-Built
1c3ddae7-93d9-4eff-a6d4-066937cbf947 | checkpoint | Backfill And All Pipe Covered, Even Protection Sleeves For Concrete
f2c86c75-fbc0-45ef-8e93-5d68f9e4e28c | checklist | Underslung Pvc |  | Underslung Pvc
359ccd89-e90b-4206-b36b-a07f3189fcbd | section | Details
0ca383d9-61cc-4b1d-bc27-df48d1158acf | checkpoint | Pvc installed To Correct Gradient
45f9d1dc-f66f-440b-b394-234d0f6f9516 | checkpoint | Flood Tested (Add Photos Of Test)
c09c0e5a-f207-4506-9316-fc4053d3763d | checkpoint | Take Photos Of Testing
c04afc6d-5d1f-4b61-9473-b9b2ec983237 | checklist | Underslung PVC |  | Underslung PVC
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
ad2467c2-48b5-42a2-9854-d2fd6f6eb56c | checkpoint | Pvc installed To Correct Gradient
c52784ce-c3d8-4286-863c-6146e11dbb29 | checkpoint | Flood Tested (Add Photos Of Test)
afb09c7b-6036-477c-9022-abb45856330a | checkpoint | Take Photos Of Testing
35ef3a50-db2f-4d97-9fd4-66f649917156 | checklist | Washing Machine - 2nd Fix Checklist |  | Washing Machine
5cadfe3f-3f55-4275-935f-417add5428cf | section | Details
c782eace-bdc6-4c0a-86e0-97d3b5c65ffd | checkpoint | Washing machine taps installed
148b9cd6-155a-417e-a6c4-8a2ce50c8dac | checklist | Washing Machine - Commissioning Checklist |  | Washing Machine
d440af5c-e1f4-47e2-a755-6f91033f6f2e | section | Wash Machine - Commissioning
7d675775-fe07-45b0-81be-0111703774ac | checkpoint | Washing machine taps have been operated to ensure supply has bee nflushed through to clear any debris
36c6ac24-209c-485e-ac6a-ef5877c21e41 | checklist | Water Meter & Limiting Valve - 2nd Fix Checklist |  | Water Meter & Limiting Valve
8fc71833-0135-4f6c-a2b0-b024771df281 | section | Details
afb9a492-6996-4762-926d-c071f042afac | checkpoint | Water meter installed correctly
9838f20b-cffd-423c-b3bb-f7742a5319fe | checkpoint | Limiting valve installed correctly and set to the correct pressure
4075c5a5-c13c-4e69-9e85-42b30b28bf9c | checklist | Water Meter & Limiting Valve - Commissioning Checklist |  | Water Meter & Limiting Valve
758bcec6-6413-435e-a470-c3e226922cb6 | section | Details
f3314e18-806d-42b5-856e-fa205d95ff31 | checkpoint | Meter is oberved to be working correctly ( take video of the meter spinning )
54c162c1-e510-402b-9a67-5bb8ada1b1f4 | checkpoint | Water meter reading after apartment commissioning is completed
d9aae3bd-f7ca-4bf8-baa8-54745b2b3e95 | checkpoint | Limiting valve filter clear of debris
8fbed1a2-ad75-4376-b468-4f181e3a8d64 | checkpoint | Limiting valve pressure set as per design requirements ( record apartment supply pressure with a photo of a pressure guage )
359cf176-ee9c-468f-bb63-0296edcdccc4 | checklist | Water Meter Checklist |  | Water Meter Checklist
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
790c781a-90f2-47c1-9e83-9ec92be0327c | checkpoint | Meter Location
b1c7a73b-7661-4c93-b26c-bcd49e6e5355 | checkpoint | Meter Size
8d7dd646-8d3c-4290-bdf2-41df4a955b97 | checkpoint | Meter Serial Number
2958a7b0-7fc7-4d9f-a3e3-23fa53f1070e | checkpoint | BMS Module installed labelled from suppliers as per the Apartment numbering schedule
0c787af6-f706-4854-9f9d-f96b7bde6c2c | checkpoint | BMS Module Serial Number
089b2cfb-b771-49d2-b05c-7e1587f34569 | checklist | Water Stacks Checklist |  | Water Stacks Checklist
2f3b3f97-d2d0-4aee-a888-80ec2da733b3 | section | Details
093397c6-d272-444b-b0f3-43dfda80c0df | checkpoint | Tested To 1500Kpa
26b52b5a-eb20-4d89-a783-101860d279c2 | checkpoint | Pipe Labels Attached
42d9923f-f24f-438a-ab46-956c13e0bb0b | checkpoint | Lagging Of Hot Pipes
f5aa7307-f60d-414d-80e9-c18b63b60f38 | checkpoint | Water To Be Kept In Pipes To Avoid Corrosion
2f8b0c8a-39e4-41fe-b31c-fcb1d838b73c | checklist | Watermain Pipework |  | Watermain Pipework
a67d9aac-564a-43c8-a1e1-08d1891909be | section | Details
887f7798-efa4-4a2f-b05e-62c25a8301ee | checkpoint | Bedding Put In At Correct Height
80ba8dd6-ddce-482f-9a05-d585bf3cac68 | checkpoint | Grade Right
600f1191-af82-4c21-8f7a-7e3a1cd10923 | checkpoint | Check Pipes Is All The Way In
33ad627a-a16e-474a-8c01-9e121417d3b6 | checkpoint | Check Pipe Connections (No Gaps)
ae88958b-6db2-4df5-ae43-2e78213c13a1 | checkpoint | Compact Around Pipe