## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Streetlighting - Rev C | itp |  |  |  |  | ITP - Streetlighting - Rev C
section | 1.1 - General
checkpoint | 1.1.1 - Drawings
label | Acceptance / Conformance Criteria - Prior to starting works, ensure that the construction drawings are both IFC and the Current Version.
label | Standard / Specification - Downer
label | Verifying Document - IFC Drawings
label | Frequency - Prior to work planning and start
label | Activity - M
label | By - PE
checkpoint | 1.1.2 - Power Connection Application
label | Acceptance / Conformance Criteria - Submit new streetlighting connection request via WEL Connect portal.
label | Standard / Specification - WEL Requirements
label | Verifying Document - Application Form
label | Frequency - Once
label | Activity - H
label | By - PE
checkpoint | 1.1.3 - Construction Pack (1)
label | Acceptance / Conformance Criteria - ITP to be submitted to the Engineer and approved prior to works beginning
label | Standard / Specification - Downer
label | Verifying Document - In-Eight Document Approval/Acknowledgement
label | Frequency - Submit 10 days prior to commencement of works
label | Activity - H
label | By - PE
checkpoint | 1.1.3 - Construction Pack (2)
label | Acceptance / Conformance Criteria - Methodology and associated documents to be prepared, reviewed and approved internally prior to work commencement.
label | Standard / Specification - Downer
label | Verifying Document - Construction Pack Sign Off
label | Frequency - Prior to Construction & after any major incident
label | Activity - M
label | By - PE
checkpoint | 1.1.4 - Survey Set-out
label | Acceptance / Conformance Criteria - Ensure streetlight locations are set out per IFC drawings/data.
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off
label | Frequency - Prior to Construction & Every Revision of IFC Drgs / Data
label | Activity - M
label | By - PE
checkpoint | 1.1.5 - Environmental Protection
label | Acceptance / Conformance Criteria - Install Erosion Sediment Control measures in line with PWRBSS ESCP plans Inspect, monitor, and maintain ESCP measures weekly and immediately before & after significant weather events
label | Standard / Specification - Project ESCP Plans
label | Verifying Document - ITP Sign Off
label | Frequency - Prior to Construction Inspect, Monitor, and Maintain Weekly and immediately before and after significant weather events
label | Activity - M
label | By - PE
checkpoint | 1.1.6 - Stakeholder
label | Acceptance / Conformance Criteria - Inform stakeholders of upcoming works. Agree plans for maintaining access to properties during construction with landowners.
label | Standard / Specification - Project Stakeholder Management Plan
label | Verifying Document - ITP Sign Off
label | Frequency - Prior to Construction with continue updates throughout the works
label | Activity - M
label | By - PE
checkpoint | 1.1.6 - Permits
label | Acceptance / Conformance Criteria - Ground Disturbance Permit must be in place before any ground breaking activity commences, incl. trenching, driving waratahs or survey pegs, and topsoil strip.
label | ○ Permit to Dig will be based on BBO existing Services Drawings, Before U Dig Plans , potholing by the project, CAT & Genny survey, and visual inspections. Doner Permit encompasses external provider permit requirements.
label | ○ All known services must be clearly marked on site and briefed to the workforce .
label | Standard / Specification - Section 2.2.10 Project Specification
label | Verifying Document - Ground Disturbance Permit DN-ZH-FM043.1
label | Frequency - Prior to Construction Reviewed and Reissued weekly or when site conditions change
label | Activity - H
label | By - PE
section | 2.1 - General
checkpoint | 2.1.1 - Walk-over
label | Acceptance / Conformance Criteria - BBO representative to walk over and confirm/approve locations for install. Including reviewing accessibility of doors.
label | Standard / Specification - Design Drawings / RITS 3.6.3
label | Verifying Document - Written correspondence
label | Frequency - Prior to construction
label | Activity - HP
label | By - PE / BBO
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.1.2 - Light Poles Materials/Delivery
label | Acceptance / Conformance Criteria - Evidence of manufacturer and product name.
label | Standard / Specification - BBO Request
label | Verifying Document - Delivery Dockets
label | Frequency - Once per pole group installation
label | Activity - M
label | By - IBEX
section | 3.1 - Civil (Pole) Installations
checkpoint | 3.1.1 - Ducting Backfill Material
label | Acceptance / Conformance Criteria - COVERED UNDER UTILITY TRENCH ITP.
label | ○ Where there is any exposed part of the cable (i.e. between termination of the duct and entry into streetlight pole underground hatch), surround with min. 100mm thickness sand material.
label | Standard / Specification - WEL Requirement
label | Verifying Document - Photographs
label | Frequency - Verification on random selection of poles
label | Activity - M
label | By - IBEX / PE
checkpoint | 3.1.2 - Access Hatch/Door Accessibility
label | Acceptance / Conformance Criteria - Visual check to ensure accessibility of doors.
label | Standard / Specification - RITS 3.6.3
label | Verifying Document - Nil - Visual Check
label | Frequency - Each pole
label | Activity - M
label | By - IBEX / PE
checkpoint | 3.1.3 - Pole Installation Positions
label | Acceptance / Conformance Criteria - Poles within following tolerances:
label | ○ +/- 0.5m parallel to the carriageway
label | ○ +/- 0.2m perpendicular to the carriageway
label | ○ +/- 0.2m vertically
label | Standard / Specification - Design Drawings
label | Verifying Document - As-builts
label | Frequency - Each pole
label | Activity - H
label | By - PE
section | 3.2 - Cabling, Electrical Testing and Commissioning
checkpoint | 3.2.1 - Earth Wiring
label | Acceptance / Conformance Criteria - Photos of streetlight earth once completed.
label | Standard / Specification - BBO Request
label | Verifying Document - Photograph
label | Frequency - Each earth
label | Activity - M
label | By - IBEX / PE
checkpoint | 3.2.2 - Electrical Certification
label | Acceptance / Conformance Criteria - Completed and signed certificate of electrical compliance (COC) and record of inspection (ROI).
label | Confirm that poles are:
label | ○ Earthed to AS/NZS 3000:2018
label | ○ Wired to AS/NZS 3000 and AS/NZS 3008:1.2
label | ○ Conforming to the NZ Electrical (Safety) Regulations
label | Standard / Specification - Design Drawings
label | Verifying Document - Certificate
label | Frequency - Each pole
label | Activity - H
label | By - IBEX
checkpoint | 3.2.3 - Network Company Acceptance
label | Acceptance / Conformance Criteria - Written acceptance of all underground cabling and circuitry, including acceptance of assumed responsibility for future maintenance and renewal.
label | Standard / Specification - RITS 3.6.8
label | Verifying Document - Written Correspondance/Acceptance
label | Frequency - Once prior to comissioning
label | Activity - H
label | By - WEL
section | 4.1 - General
checkpoint | 4.1.1 - Survey As-Builts
label | Acceptance / Conformance Criteria - Asbuilts reviewed and submitted showing final location of all poles
label | Standard / Specification - Project Specification
label | Verifying Document - Survey Data As Built Drawings, Photographs, Red Pen As- Builts including Undercuts
label | Frequency - Post Works Completion
label | Activity - H
label | By - PE