## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | ITP 010 - O&M Manuals | itp |  |  |  | Yes | ITP 010 - O&M Manuals | 24060272-c948-4316-ba88-9cda93456ebc
checkpoint-group |  |  | section | 1.0 Asset Lists
checkpoint-status |  |  | checkpoint | 1.1 Equipment List
label | 4e0b2ca6-fbb7-5801-88d8-478b679aad58 |  | note | Acceptance Criteria - List with equipment no., make & model
label | b98f4e29-a95c-5b42-a9e7-d3b56a3c91e5 |  | note | Inspection Responsibility: BCL - D
label | 034e2cf2-ed11-5e9e-92d3-4cc8996bb7de |  | note | Verification Records of Inspection(s) / Test(s) - n/a
checkpoint-status |  |  | checkpoint | 1.2 Instrument List
label | f2bae882-7863-5fe2-ab40-c268372b8e69 |  | note | Acceptance Criteria - List with equipment no., make & model
label | 6b81eb17-f4f2-5546-8486-bdad4f6fe4d9 |  | note | Inspection Responsibility: BCL - D
label | 2ab412e1-6657-50fe-8e43-aeffba6f6634 |  | note | Verification Records of Inspection(s) / Test(s) - n/a
checkpoint-status |  |  | checkpoint | 1.3 Valve List
label | 2fd80f22-fb88-5138-8cdd-1577b0a3d759 |  | note | Acceptance Criteria - List with equipment no., make & model
label | 70269d9b-48aa-5d7e-82f3-b4ce9c4ef84f |  | note | Inspection Responsibility: BCL - D
label | 1f3c15d2-be0b-54e6-9403-ed5489db6f2f |  | note | Verification Records of Inspection(s) / Test(s) -
checkpoint-group |  |  | section | 2.0 Equipment O&M Manuals
checkpoint-status |  |  | checkpoint | 2.1 Grundfos Pumps
label | 517a0112-86eb-511c-905e-f9d4cd6f11fd |  | note | Acceptance Criteria - Vendor O&M Manual
label | 8f42df51-97c0-580d-83e7-77575558480c |  | note | Inspection Responsibility: BCL - D
label | 79c31471-fab6-5bec-801a-42ed95ea4380 |  | note | Verification Records of Inspection(s) / Test(s) - n/a
checkpoint-status |  |  | checkpoint | 2.2 GF Water Jet Suction Pump
label | c5538733-475f-544f-b9c6-eeb2f3843430 |  | note | Acceptance Criteria - Vendor O&M Manual
checkpoint-status |  |  | checkpoint | 2.3 Seat 15 Fan
label | 04a6c37a-b3c7-51d7-9d88-baecd098feef |  | note | Acceptance Criteria - Vendor O&M Manual
checkpoint-status |  |  | checkpoint | 2.4 GF Strainers
checkpoint-group |  |  | section | 3.0 Instrument O&M Manuals
checkpoint-status |  |  | checkpoint | 3.1 Endress & Hauser Flow Transmitters
checkpoint-status |  |  | checkpoint | 3.2 Endress & Hauser Level Transmitters
checkpoint-status |  |  | checkpoint | 3.3 Endress & Hauser Level Switches
checkpoint-status |  |  | checkpoint | 3.4 Prominent Fluoride Analysers
checkpoint-status |  |  | checkpoint | 3.5 Vega Level Transmitters
checkpoint-status |  |  | checkpoint | 3.6 Weber Flow Switches
checkpoint-status |  |  | checkpoint | 3.7 Wika Pressure Gauges
checkpoint-group |  |  | section | 4.0 Valve O&M Manuals
checkpoint-status |  |  | checkpoint | 4.1 Emerson Backflow Preventors
checkpoint-status |  |  | checkpoint | 4.2 GF Actuators
checkpoint-status |  |  | checkpoint | 4.3 GF Valves
checkpoint-status |  |  | checkpoint | 4.4 K-Ball Valves
checklist-sectioned |  |  | checklist | ITP 002 - Ruddells Mechanical Installation | itp |  |  |  | Yes | ITP 002 - Ruddells Mechanical Installation | 35a97bc0-4b19-410e-a75d-d3c76bd00737
checkpoint-group |  |  | section | 2.0 Documentation
checkpoint-status |  |  | checkpoint | 2.1 Construction Drawings
label | bf87d416-a32b-57f0-b164-36f7d19bc1e6 |  | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
label | f0e2cb44-c617-5022-ae84-369dbeae036b |  | note | Acceptance Criteria - IFC drawings
label | b9398855-b269-5c56-800b-e1df119ac15c |  | note | Inspection Responsibility: BCL - I
label | fe5d0e20-e01d-5bc4-a18d-f09d0ff33216 |  | note | Inspection Responsibility: Client - S
label | 8d52a008-eb4e-5583-81c8-112a641ac52b |  | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
checkpoint-status |  |  | checkpoint | 2.2 Methodology
label | 07628b18-a639-5e55-9b45-4c48e24e53e4 |  | note | Type of inspect / Test and Frequency - Approved construction plan & sequence drafted and briefed to all involved with activity prior to construction. Includes any isolation permits for tie ins.
label | 6c71a079-0a2a-5ab0-81f4-4627b3725dd1 |  | note | Acceptance Criteria - Workpack Approved
label | 8403241d-b4ab-500a-9a7e-1a2e274679e0 |  | note | Inspection Responsibility: BCL - S
label | 0d84196b-5ebc-552c-a7ad-e7fc9c0d8b1b |  | note | Inspection Responsibility: Client - A
label | 2641e880-460d-5422-9607-071f44f022b3 |  | note | Verification Records of Inspection(s) / Test(s) - Approved Workpack Isolation Permit
checkpoint-group |  |  | section | 3.0 Manufacturing
checkpoint-status |  |  | checkpoint | 3.1 Pipe & Pipe Fitting (Flanges, Elbows, Tees etc.)
label | b2283156-7ccc-5290-a65d-33a21752aca0 |  | note | Type of inspect / Test and Frequency - Confirm pipe and pipe fitting materials are correct; material grade, size, rating etc. on delivery
label | c59e04c4-71a4-56fe-828b-cd68b1137037 |  | note | Acceptance Criteria - Pipe Data Sheet, Supplier Packing Slips
label | a76573c4-656c-57d7-bea4-446c8080e78e |  | note | Inspection Responsibility: BCL - S
label | 2ce9902f-256c-52c4-bac1-2a5118794525 |  | note | Inspection Responsibility: Client - I
label | 4aeb5492-7286-5d59-bf01-273d416f560a |  | note | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
checkpoint-status |  |  | checkpoint | 3.2 Nuts & Bolts
label | c9d6f6f0-475f-5a43-bd2b-15782f329292 |  | note | Type of inspect / Test and Frequency - Confirm nuts and bolt materials are stainless steel grade 316
label | b27d2471-ddbe-54ff-b36d-4c7dcdc13122 |  | note | Acceptance Criteria - Supplier Packing Slips
label | dafd6cb0-6765-56ba-adc4-e92133cb72b3 |  | note | Inspection Responsibility: BCL - S
label | 5f5d7dce-a85a-5fad-b8c0-a6ea08cf50f6 |  | note | Inspection Responsibility: Client - I
label | 663f59ff-fc66-5f81-aa78-d44f99ae8d38 |  | note | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
checkpoint-status |  |  | checkpoint | 3.3 Consumables
label | f98a9d46-c035-5f8c-9bc9-45da40a2386b |  | note | Type of inspect / Test and Frequency - Confirm consumable materials are correct on delivery
label | 17d39c12-da50-5f13-9711-5c992d434cea |  | note | Acceptance Criteria - Supplier Packing Slips
label | d419322b-02db-5fce-9611-53e843c8bac8 |  | note | Inspection Responsibility: BCL - S
label | 1667f7d0-b3d0-5e6e-b781-015387391cdd |  | note | Inspection Responsibility: Client - A
label | 85f37f86-4545-5485-b3d1-d5e7e0ace37f |  | note | Verification Records of Inspection(s) / Test(s) - Supplier Packing Slips
checkpoint-group |  |  | section | 4.0 Delivery, Storage & Handling
checkpoint-status |  |  | checkpoint | 4.1 Delivery
label | 94c6e187-2d30-5e24-9cdd-aeb8bde77f2f |  | note | Type of inspect / Test and Frequency - Check pipe materials, tanks, structural steel and dosing cabinets are undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery
label | 62fd25cf-8972-510e-8759-b8e41393ee74 |  | note | Acceptance Criteria - N/A
label | 0bb3027b-2202-528a-977d-565dd45ab292 |  | note | Inspection Responsibility: BCL - I
label | f81c7cca-d052-5fb5-8534-9db92b30290a |  | note | Inspection Responsibility: Client - I
label | eeb277a6-55b0-5829-a100-0b493fd375de |  | note | Verification Records of Inspection(s) / Test(s) - ITC-002
checkpoint-status |  |  | checkpoint | 4.2 Storage
label | f935473c-3aca-5802-99be-26df9430f629 |  | note | Type of inspect / Test and Frequency - For project entirety store materials in clean environment, protected from external damage; cover flange faces, store off ground using pallets. Ensure materials are free from contaminants and foreign debris.
label | a187794c-9662-576b-bdd9-6e600ea6a36f |  | note | Acceptance Criteria - N/A
label | c4e7ffe0-2f86-5efd-8d11-84968dac69a8 |  | note | Inspection Responsibility: BCL - W
label | 82cc053d-d586-5cdc-ac40-d84522b15705 |  | note | Inspection Responsibility: Client - I
label | ef882d23-dcdd-5d5b-b99b-5be896c53d55 |  | note | Verification Records of Inspection(s) / Test(s) - N/A
checkpoint-status |  |  | checkpoint | 4.3 Handling
label | 247330f0-de1d-572c-8277-3b2ebb3a30a6 |  | note | Type of inspect / Test and Frequency - Handle materials with care and with the correct equipment (gloves, slings etc.)
label | 125ea9db-154d-5a94-8724-31e27cccd13b |  | note | Acceptance Criteria - N/A
label | dd79f3a3-f517-5896-9eee-07cd5345c03a |  | note | Inspection Responsibility: BCL - I
label | 01544cde-ba70-5dbf-a4cb-bafb8cf08ed3 |  | note | Inspection Responsibility: Client - I
label | 1f9041fa-602f-5c93-8c27-c93d76ee8f75 |  | note | Verification Records of Inspection(s) / Test(s) - N/A
checkpoint-group |  |  | section | 5.0 Site Installation
checkpoint-status |  |  | checkpoint | 5.1 Install Pipe Supports
label | 0334d2ba-34fa-566a-b4c4-9fef66e833e5 |  | note | Type of inspect / Test and Frequency - Install pipe supports in the correct locations before pipe installation
label | c57459da-73d0-5b34-b193-28d017f729df |  | note | Acceptance Criteria - As per pipe manufacturer specifications
label | 863e4e64-09fc-5376-89c9-97837ee992c4 |  | note | Inspection Responsibility: BCL - I
label | c0f63876-b23a-5ec2-a39a-34b7b831d571 |  | note | Inspection Responsibility: Client - I
label | 8aed560c-e0d0-5aec-aac3-94923e5f13dc |  | note | Verification Records of Inspection(s) / Test(s) - Redline Drawings, ITC-02
checkpoint-status |  |  | checkpoint | 5.2 Equipment Set-Out
label | 09448f7c-6b2f-599d-8bab-26a2e1803715 |  | note | Type of inspect / Test and Frequency - Survey and mark the correct locations of all pipes, tanks, structures and equipment before installation
label | 5b248e47-33f2-55c8-8824-aea3b41d746c |  | note | Acceptance Criteria - IFC Drawings
label | a7efdcda-7d2b-5ace-a7cc-25499303717e |  | note | Inspection Responsibility: BCL - I
label | a69ad78d-8a6c-5730-be9e-e948f4451fd6 |  | note | Inspection Responsibility: Client - I
label | 3ede0344-110e-511c-b125-2641d0295405 |  | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings, ITC-02
checkpoint-status |  |  | checkpoint | 5.3 Install Pipework
label | e58ed528-a7a2-51fd-bc73-7a1afc8d6d28 |  | note | Type of inspect / Test and Frequency - Install piping on the pipe supports during construction
label | 84a54507-c196-5005-893e-826fedc3853e |  | note | Acceptance Criteria - IFC Drawings
label | 98c7a1e9-dc4b-5fb9-ae87-f5be1bf339b2 |  | note | Inspection Responsibility: BCL - I
label | d6a1ec06-499a-5052-995a-1fa41f9c8acc |  | note | Inspection Responsibility: Client - I
label | 703a90d7-beab-5526-83dc-cae58522d5a3 |  | note | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint-status |  |  | checkpoint | 5.4 Install Dose Tank
label | 81ec58c2-3dce-5bc6-8e76-ec16b2a930d4 |  | note | Type of inspect / Test and Frequency - Install tank in correct location and orientation as specified in IFC mechanical layout drawings and tank manufacturers drawings
label | fd6a7e3c-7897-582e-ac29-f0d2a2ecda3d |  | note | Acceptance Criteria - IFC Drawings
label | 23a8e8e2-136f-5492-b0ca-d3bb5bd6e2ef |  | note | Inspection Responsibility: BCL - I
label | 4b174ce0-c5b6-51e8-ae10-11c11891f513 |  | note | Inspection Responsibility: Client - I
label | 51e652ae-6d2b-5cdb-b5ee-72cf3e550d96 |  | note | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint-status |  |  | checkpoint | 5.5 Install Access Platform
label | 8b9b90d8-cfe9-53f9-bc47-45f2b337f198 |  | note | Type of inspect / Test and Frequency - Install access platforms in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings
label | eeada1d3-80bb-5f5b-b9e4-fa7e00cff5fa |  | note | Acceptance Criteria - IFC Drawings
label | b0d809de-2d4d-59a9-96a2-d17277497e15 |  | note | Inspection Responsibility: BCL - I
label | 6b2725b4-18ba-5c6e-807e-d54c75792507 |  | note | Inspection Responsibility: Client - I
label | 20245821-a991-541e-88df-7d42dfe77f0a |  | note | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint-status |  |  | checkpoint | 5.6 Install Dosing Cabinet
label | d54d2cd3-4c7d-5309-a832-9a261725a1e1 |  | note | Type of inspect / Test and Frequency - Install cabinet in correct location and orientation as specified in IFC mechanical layout drawings and manufacturers drawings
label | 782590be-1faf-5260-8f47-e911038ebe5c |  | note | Acceptance Criteria - IFC Drawings
label | 8042530c-8b5a-527b-b0a9-c8af916f6a45 |  | note | Inspection Responsibility: BCL - I
label | 371a37b6-9f44-54ea-a734-d82328cbbf3a |  | note | Inspection Responsibility: Client - I
label | 363c6d6a-9f21-5b96-9ffd-6b1f73f733fe |  | note | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint-status |  |  | checkpoint | 5.7 Install Safety Shower
label | 4de71a0c-d651-50fe-8ff6-ba972be6d02f |  | note | Type of inspect / Test and Frequency - Install safety shower in correct location as specified in IFC mechanical layout drawings
label | c8a6c1ae-2b6e-5c3a-98e5-adb4970969ae |  | note | Acceptance Criteria - IFC Drawings
label | 9d5ba74a-a71e-534a-8487-a5352748862f |  | note | Inspection Responsibility: BCL - I
label | b433d8ce-4504-56de-9209-03d3f14215d7 |  | note | Inspection Responsibility: Client - I
label | 69b6e230-d635-5ffe-aacf-af3949b6233f |  | note | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint-status |  |  | checkpoint | 5.8 Install new nozzles into Existing Raw Water Pipework
label | 1de08fcb-faef-5a1e-af03-b29a389adce1 |  | note | Type of inspect / Test and Frequency - Hot tap into Raw water pipework for new Flow Switch and Fluoride Dose point at correct locations
label | 7aef93f9-4fa8-510a-9c33-c3581e89d4e4 |  | note | Acceptance Criteria - IFC Drawings, Flow Switch O&M manual
label | 11ca332d-9a3f-5a18-aabf-d8ba82435edd |  | note | Verification Records of Inspection(s) / Test(s) - ITC-02
checkpoint-status |  |  | checkpoint | 5.9 Pressure Testing
label | bfc4d6a3-b4fd-5287-a396-49ef980666e8 |  | note | Type of inspect / Test and Frequency - All Fluoride dosing pipelines to be hydrotested 1.5 times the maximum working pressure for 15 minutes and inspected for leaks
label | 73915b04-fa20-5979-9a44-f49daa827d7f |  | note | Acceptance Criteria - NZS 7643
label | 4400f4ec-a2d2-5f9c-ad30-68e003cccc88 |  | note | Inspection Responsibility: BCL - W
label | ab5c71f3-866a-5d1f-ab43-ec278d950550 |  | note | Inspection Responsibility: Client - A
label | f4996c9d-c5bb-5869-9775-9c68b6ebd146 |  | note | Verification Records of Inspection(s) / Test(s) - Pressure Test Records
checkpoint-group |  |  | section | 6.0 As-builts
checkpoint-status |  |  | checkpoint | 6.1 Redline Drawings
label | a72a1876-3308-53f5-9233-efa425c8b8ce |  | note | Type of inspect / Test and Frequency - Redline P&ID Drawings and Mechanical Drawings Sets post construction
label | 112e3db4-4b82-5394-b94b-7601bc271194 |  | note | Acceptance Criteria - N/A
label | 4a7e964a-37ab-5a83-86bc-a63b9d7e24da |  | note | Inspection Responsibility: BCL - S
label | d503f6c0-7e9e-5743-945d-3b8429e0e77e |  | note | Inspection Responsibility: Client - A
label | 9688de39-272b-59ad-9da1-4da787bb2bd0 |  | note | Verification Records of Inspection(s) / Test(s) - Redline Drawings Issued
checklist-sectioned |  |  | checklist | ITP 001 - Ruddells Bund Construction | itp |  |  |  | Yes | ITP 001 - Ruddells Bund Construction | 4bbda6c4-3f6c-4d98-a089-3230a4ebc41b
checkpoint-group |  |  | section | 1.0 Documentation
checkpoint-status |  |  | checkpoint | 1.1 Construction Drawings
label | 49338b9b-603f-5750-8da7-d900a897afd4 |  | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
label | 0f33c498-eeac-59bf-bb60-2dd8ee13c5ef |  | note | Acceptance Criteria - Latest IFC Drawings
label | 2eeb3371-de70-5e9c-b553-a7c9d9a2e53f |  | note | Inspection Responsibility: BCL - I
label | 489979f0-79a4-5c1d-b725-aecb0211f879 |  | note | Inspection Responsibility: Client - S
label | adc4f627-3c27-5127-9995-6d047a001e7d |  | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
checkpoint-status |  |  | checkpoint | 1.2 Concrete mix design
label | 8fda91e0-3343-539c-953b-9c960211ba13 |  | note | Type of inspect / Test and Frequency - Submitted to Beca for approval
label | 3280cab0-08cf-5a17-b880-3e0485bd97bf |  | note | Acceptance Criteria - Approved RFI
label | 6e0c78c8-25b2-5c12-ac94-c1c1ee92f4fa |  | note | Inspection Responsibility: BCL - H
label | fe009713-17a7-5f00-8a02-346b9dc2ee32 |  | note | Inspection Responsibility: Client - A
label | e93b73b7-f8d8-5c7d-ab5d-473403e7e31b |  | note | Verification Records of Inspection(s) / Test(s) - RFI
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | 2.0 Fence Relocation/Swale works
checkpoint-status |  |  | checkpoint | 2.1 Set Out, as per latest “For Construction” revision
label | 8d216d12-ebf2-52db-9941-e4dd0084d64a |  | note | Type of inspect / Test and Frequency - Survey and mark the correct location, Check Boundary location
label | ae72fbd1-4995-5384-9389-0db4bac5d3c3 |  | note | Acceptance Criteria - IFC Drawings, Survey data check by PM and Beca Engineer
label | ec92cdf7-a8ce-5cd9-91f5-af4c9d9c7466 |  | note | Inspection Responsibility: BCL - D
label | 0d7a548d-c7de-58d4-9d99-b2f3b6d3a508 |  | note | Inspection Responsibility: Client - A
label | 480d629a-1b91-5602-861a-8ce4d409353d |  | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings, Approved RFI
checkpoint-status |  |  | checkpoint | 2.2 Install new relocated fence to match existing
label | f2ab6be0-2eb4-5017-8417-440e99b7f032 |  | note | Type of inspect / Test and Frequency - New fence matches existing
label | b2364f1d-9e48-55a9-8bbe-d2351077f445 |  | note | Acceptance Criteria - Witness by engineer
label | b5a8574e-ea10-5a0d-ae72-a2384c50f23f |  | note | Inspection Responsibility: BCL - I
label | 470ee3a1-3668-56b0-aab7-e13dcf80a755 |  | note | Inspection Responsibility: Client - R
label | 20fd9f06-50d0-522c-95df-7b97254cd74d |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-status |  |  | checkpoint | 2.3 Place rock riprap
label | 28a42495-5711-5ab2-8ca9-ba311c8e00de |  | note | Type of inspect / Test and Frequency - 75-200mm size rock, 1m wide at top side to 1.5m wide at bottom end (inspected once at end of works)
label | 8f3a4b0a-8630-5ba5-92ab-6c9c02bbd751 |  | note | Acceptance Criteria - Witness by Engineer
label | 10a3749a-6ce7-5980-a8f4-19352196b59e |  | note | Inspection Responsibility: BCL - I
label | 0a0f8211-bcea-59b8-ad2b-4b443b9d0c3e |  | note | Inspection Responsibility: Client - R
label | c0d3767c-640d-548a-9081-af5d8c147298 |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-group |  |  | section | 3.0 Excavation
checkpoint-status |  |  | checkpoint | 3.1 Set Out, as per latest “For Construction” revision
label | 30c24d19-1bb6-50e9-9ffa-aa6554a99606 |  | note | Type of inspect / Test and Frequency - Survey and mark the bund location
label | 6d655fd9-9cfd-500d-9c41-3c4f11160ce1 |  | note | Acceptance Criteria - IFC Drawings, Survey data check by PM
label | 27ff986f-7541-5ac0-b6ca-3a6d20cc4ee8 |  | note | Inspection Responsibility: BCL - T
label | c21f1959-c822-5d7f-93c3-10e7df7a02e7 |  | note | Inspection Responsibility: Client - I
label | 0ae3d889-1cff-5e5a-8a36-69604a739ba3 |  | note | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings
checkpoint-status |  |  | checkpoint | 3.2 Subgrade inspection
label | e03cb1a4-dd6a-56a9-b367-2bfc56e5b2cb |  | note | Type of inspect / Test and Frequency - Scala testing to confirm subgrade is of sufficient strength
label | edb809a7-d20b-5dd7-8fea-5466e64e4646 |  | note | ○ Witness by engineer
label | af0d2e77-5277-5ee2-bd5a-db06489379c8 |  | note | ○ Minimum of 2 tests per bund pour
label | 19f2513e-a220-5dd0-a1e8-7bf47bd17b0a |  | note | Acceptance Criteria - Minimum of 5 blows per 150mm
label | b75cd556-d1a3-5469-be43-309fa5a83691 |  | note | Inspection Responsibility: BCL - H
label | f7c64104-52a9-55ba-b4bb-d99c79275657 |  | note | Inspection Responsibility: Client - A
label | b47e83aa-99c1-52d0-98c3-76ade8ba1290 |  | note | Verification Records of Inspection(s) / Test(s) - Scala Test Results
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 3.3 Ground Contaminants
label | aa240e7d-9037-5a1c-bacc-1b9a52276ba5 |  | note | Type of inspect / Test and Frequency - Soil testing to confirm no contaminants
label | a6233f80-d4fb-583a-8e29-ba45d5fac6cc |  | note | Acceptance Criteria - Test results clear for clean fill
label | 7262bd7d-96ed-5532-85de-50f202d3e412 |  | note | Inspection Responsibility: BCL - T
label | ba0a2d74-dc4b-5392-9dbe-bde1eee38d03 |  | note | Inspection Responsibility: Client - R
label | c1bcf360-16ef-51ab-9f4c-d3cee6434194 |  | note | Verification Records of Inspection(s) / Test(s) - Lab test report
checkpoint-group |  |  | section | 5.0 Post Excavation
checkpoint-status |  |  | checkpoint | 5.1 >150mm compacted hard fill under bund (GAP20)
label | 275c45a7-11de-5c63-aa68-f87b6f554837 |  | note | Type of inspect / Test and Frequency - Clegg hammer testing, 5x5 grid, minimum of 4no per bund pour
label | 64aced04-f4dc-546e-a694-1a1004b7891d |  | note | Acceptance Criteria - Clegg CIV>10
label | 488cb705-d559-5381-8909-de966841c8dd |  | note | Inspection Responsibility: BCL - T
label | c442dcf8-a65b-5d8e-a761-ce56aed97b13 |  | note | Inspection Responsibility: Client - R
label | caae07e0-8774-504b-ab85-2a715227b604 |  | note | Verification Records of Inspection(s) / Test(s) - Clegg results
checkpoint-group |  |  | section | 6.0 Concrete works
checkpoint-status |  |  | checkpoint | 6.1 Site concrete
label | 9a8e3d85-22bd-5890-bd33-7ab7c343a4d4 |  | note | Type of inspect / Test and Frequency - Visual inspection and record of site concrete install, completed for each slab pour
label | a14c2e6f-ac68-5271-9508-554f0f153799 |  | note | Acceptance Criteria - 50mm site concrete poured to base level of foundation +0mm -10mm tolerance
label | ce97db2c-aded-520e-b2d0-d707846214cf |  | note | Inspection Responsibility: BCL - D
label | 9df0e031-3f22-506a-a8b7-78123a107211 |  | note | Inspection Responsibility: Client - W
label | afb34cf2-1b5d-520e-ae8a-23f25131d92d |  | note | Verification Records of Inspection(s) / Test(s) - Photos Concrete pour record
checkpoint-status |  |  | checkpoint | 6.2 DPM
label | cea33de3-cf67-5be3-a1c5-ba64822ad76b |  | note | Type of inspect / Test and Frequency - Visual inspection and record of DPM installed, completed prior to each pour
label | 40c57e0e-b697-5e2f-b780-7ddc729b9165 |  | note | Acceptance Criteria - Polythene laid on site concrete prior to reinforcing
label | f978abde-61b8-5a35-aa12-69efd8010b87 |  | note | Inspection Responsibility: BCL - D
label | 807c6134-35a2-59ac-a67e-af565c3af7ae |  | note | Inspection Responsibility: Client - W
label | 4ae33cfc-7b90-56eb-9edf-4bfe701002f4 |  | note | Verification Records of Inspection(s) / Test(s) - Photos, Concrete pour record
checkpoint-status |  |  | checkpoint | 6.3 Reinforcing (material)
label | 0bfd40f2-e40c-57d9-9886-287b1590fa9f |  | note | Type of inspect / Test and Frequency - Review documentation for each pour
label | de3bfba9-3782-5bdb-a28d-ee0c6918365b |  | note | Acceptance Criteria - Reinforcing to be Grade 500E to ASS/NZS4671
label | 3ad4b1d6-60f3-5dff-b80a-75b42f7d377a |  | note | Inspection Responsibility: BCL - D
label | b78dd33b-16d0-5403-9d8a-2cf97d5cf64d |  | note | Inspection Responsibility: Client - W
label | 6fd56464-0240-51fc-8f75-f6b329142c0e |  | note | Verification Records of Inspection(s) / Test(s) - Mill certificates, Detail sheet
checkpoint-status |  |  | checkpoint | 6.4 Sump Construction
label | f8c0184a-657e-5a09-8e9f-ad036e6982e6 |  | note | Type of inspect / Test and Frequency - Reinforcing check, dimension check, Formwork check
label | 839cfe41-e569-5f23-8d73-15555db076e4 |  | note | Acceptance Criteria - As per IFC drawings
label | 8f6be7f0-544d-50a8-8aab-347b61875f63 |  | note | Inspection Responsibility: BCL - D
label | 7d0da8ef-0d9d-54e1-8abc-86db208e5938 |  | note | Inspection Responsibility: Client - W
label | 7774fe3b-4be1-55ff-8525-7d4dadf38795 |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint-status |  |  | checkpoint | 6.5 Reinforcing install
label | d64c2b18-0bd6-5e75-8bf4-9cf30ead9de7 |  | note | Type of inspect / Test and Frequency - Measure to check cover, bar size and arrangement, lap length and type.
label | 5fba8004-0193-54c0-835c-6ebc2472b917 |  | note | ○ Complete prior to pouring concrete
label | 8a743d71-fbd5-5a6c-a7b5-9cf6825dce5c |  | note | Acceptance Criteria - Reinforcing matches IFC drawings, any deviations recorded and acceptance agreed with engineer prior to pour
label | 4c61fa24-b741-5834-a7d9-72d313bd55fd |  | note | Inspection Responsibility: BCL - D
label | 4f63b391-ef01-54b3-b58c-684b77c604c4 |  | note | Inspection Responsibility: Client - W
label | 3b40333e-9c01-5b82-a61f-a11d5223a71e |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
checkpoint-status |  |  | checkpoint | 6.6 Reinforcing install
label | 2b4e62c1-0d21-5ed0-83e2-e282f4a5a59b |  | note | Type of inspect / Test and Frequency - Starter bars for tank plinth Starter bars for blockwork
label | a24ade89-35b6-50ea-8e3a-7b7e67661204 |  | note | Acceptance Criteria - Matches IFC drawing
label | 3c0cee4e-bffa-52bf-b59f-885684b19309 |  | note | Inspection Responsibility: BCL - D
label | df0a68b6-d756-5943-a5ba-4f56a38dbfca |  | note | Inspection Responsibility: Client - W
label | 5e9fbfd2-6577-5bd1-9ade-aed636d72f19 |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
checkpoint-status |  |  | checkpoint | 6.7 Tank plinth
label | 0f8d2fc1-9e32-50b9-bab8-93a3a281e240 |  | note | Type of inspect / Test and Frequency - Size of plinth, height of plinth, Reinforcing checked, Formwork checked
label | 0ebdd446-e345-55ae-b1cf-db7810ee61e6 |  | note | Acceptance Criteria - Matches IFC drawing and response of RFI017
label | 32d34ce1-9df0-50f4-9e51-fb16432440e9 |  | note | Inspection Responsibility: BCL - D
label | 8df737e7-ca8b-52bc-bc99-de634d8ea6b6 |  | note | Inspection Responsibility: Client - W
label | 0eb043d2-5465-529f-9959-03d8de51961b |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
checkpoint-status |  |  | checkpoint | 6.8 Concrete pour
label | 17ab1816-9142-5374-8cdf-dd74d6903dc6 |  | note | Type of inspect / Test and Frequency - Embedded items located in slab
label | 51e5f633-5a00-5d31-bf32-451dbae32bc2 |  | note | – Ducting
label | 1621cf9b-f86c-51eb-96e8-fdf1a546c483 |  | note | – Pits
label | 52f3ca44-5394-52ec-abcb-21dd290de162 |  | note | Acceptance Criteria - Matches IFC drawings
label | c4cfccc1-e3f6-5d16-be7e-1f1034d962f7 |  | note | Inspection Responsibility: BCL - D
label | 508ad425-2f8a-5b51-aaf3-1d93573daa26 |  | note | Inspection Responsibility: Client - W
label | ac4d2687-71ba-549e-a78b-fc4b3f70d4e2 |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record, photos
checkpoint-status |  |  | checkpoint | 6.9 Concrete pour
label | 7adc86b4-ad37-54cc-8f36-ebbfe7635072 |  | note | Type of inspect / Test and Frequency - Level check, formwork check, cover check.
label | 66c84803-b3f9-5793-b38b-678d1cd05215 |  | note | ○ Inspections prior to every pour.
label | c360e48c-a12d-509a-b0f1-c18233064311 |  | note | Acceptance Criteria - Matches IFC drawing dimensions and notes
label | ead9f000-4b1f-5914-93e4-9183fbf0ba64 |  | note | Inspection Responsibility: BCL - D
label | d347c640-0cd4-5d83-bfa2-47ef44180d13 |  | note | Inspection Responsibility: Client - W
label | 2ccb3a0b-cc5b-5175-904d-778d1b36dc4b |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint-status |  |  | checkpoint | 6.10 Pour inspection/Approval to pour
label | e63ea974-d541-588b-8a9f-13b4ec36180b |  | note | Type of inspect / Test and Frequency - Pre pour inspection by Beca Engineer (hold Point)
label | 2bedb25b-77e9-55b0-8aae-159d7b9e0845 |  | note | Acceptance Criteria - Approval from Engineer to pour
label | faf8497c-65f7-55d7-b639-4fe6ce38220c |  | note | Inspection Responsibility: BCL - H
label | 21639487-327d-5247-ac05-241decd0391d |  | note | Inspection Responsibility: Client - A
holdpoint |  |  | signoff | HOLD POINT
checkpoint-status |  |  | checkpoint | 6.10 Concrete strength
label | 96cb4f5c-6f81-55ec-b1a0-28ed8846c80f |  | note | Type of inspect / Test and Frequency - Test certificate
label | 797d4c78-d83f-569d-be9e-6133e208388f |  | note | ○ 7 and 2no 28day tests required for each pour day or per 70m3
label | 64a33ba4-6b36-5ffe-9ac8-8a328459128d |  | note | Acceptance Criteria - 28 day compressive strength >40mPa
label | c5279139-23d3-5848-80e5-e640c860f20e |  | note | Inspection Responsibility: BCL - D
label | 801fe12e-f41b-51a2-b458-4c76f1485708 |  | note | Inspection Responsibility: Client - R
label | 4e84c90c-9c5e-5bf8-8c03-30721aa559a9 |  | note | Verification Records of Inspection(s) / Test(s) - Test certificate
checkpoint-group |  |  | section | 7.0 Blockwork
checkpoint-status |  |  | checkpoint | 7.1 Blockwork (material)
label | d46f18fe-3350-5d1f-ad51-64f2f37e728c |  | note | Type of inspect / Test and Frequency - Manufacturer documentation.
label | 0d6ac1d4-a83c-5269-b3ea-e6206f9b8533 |  | note | ○ Required once prior to commencement of works
label | 22d51f11-3df8-52bb-ad15-dc49ff5b055d |  | note | Acceptance Criteria - Masonry units meet AS/NZS4455
label | 3cbaee21-13f7-501d-be88-f0d5b342e84e |  | note | Inspection Responsibility: BCL - D
label | 9b81cf54-836a-52af-928c-3dbf0ed03497 |  | note | Inspection Responsibility: Client - R
label | 973dcefb-021b-57dd-bacc-f454af942dda |  | note | Verification Records of Inspection(s) / Test(s) - Supplier documentation
checkpoint-status |  |  | checkpoint | 7.2 Blockwork (reinforcing)
label | dbd706a3-aeef-520f-9b3a-9ab2a65a0541 |  | note | Type of inspect / Test and Frequency - Inspect bar size, placement, lap length and number (once per pour)
label | 8b4939f7-3d59-55e1-a2ae-8d901507cd75 |  | note | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
label | b511e624-126c-56e1-8ac8-515478ae6cc2 |  | note | Inspection Responsibility: BCL - D
label | 8d3b9575-c605-58bb-9542-6adef6cff52f |  | note | Inspection Responsibility: Client - R
label | 4c0e65cf-5d9e-5dca-8d4d-d847383fb13e |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint-status |  |  | checkpoint | 7.3 Blockwork (pour)
label | e7d863f5-001b-5982-9011-3dc65e5c9ace |  | note | Type of inspect / Test and Frequency - Inspection prior to pour, check washout location, dimensions, line and level (once per pour)
label | b998acce-45d7-5a11-81c8-30c5ade26902 |  | note | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
label | 3c81e1a4-09e4-57f3-bd5a-3d6c02e31638 |  | note | Inspection Responsibility: BCL - W
label | 3d7e70c5-a58d-5884-ac92-e64d100b6532 |  | note | Inspection Responsibility: Client - A
label | c7a3f06b-8b47-5d15-a005-f9d62dfd369b |  | note | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint-status |  |  | checkpoint | 7.4 Concrete strength
label | 4ef32a55-0e97-563e-a8e9-6ab1aa24de19 |  | note | Type of inspect / Test and Frequency - Test certificate
label | 021bdbd8-23a3-5c08-80c7-b782c9dd0b1b |  | note | ○ 7 and 2no 28day tests required for each pour day
label | 11b65fc1-3614-587b-a10d-aef380aaee59 |  | note | Acceptance Criteria - 28 day compressive strength >17.5mPa
label | 8b0fd62e-b676-50fd-a874-82423d8f7555 |  | note | Inspection Responsibility: BCL - R
label | 542d2bd6-58fb-50e3-9ec3-0f19708869d4 |  | note | Inspection Responsibility: Client - R
label | 66756447-16ac-5536-bb14-2f429816de02 |  | note | Verification Records of Inspection(s) / Test(s) - Test certificate
checkpoint-group |  |  | section | 8.0 Bund Liner
checkpoint-status |  |  | checkpoint | 8.1 Pre lining check (post pour)
label | aaaf4652-fcc3-5648-8879-00a99f127aa9 |  | note | Type of inspect / Test and Frequency - Square edges on all corners
label | f6ed2896-9940-530b-9858-d70f5473cc2a |  | note | ○ Concrete surface cleaned – all excess grout/splatters removed
label | 16e93868-a00b-5857-bf0e-591ac2f14c6d |  | note | Acceptance Criteria - Placon check
label | f7c5ee13-9026-5d03-95b8-2c4ea85db7fc |  | note | Inspection Responsibility: BCL - W
label | a30e8544-6341-5804-be24-f1d08d1183cf |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-status |  |  | checkpoint | 8.2 Watertightness of bund
label | abff2b41-8915-587e-97ba-facd4712cfbe |  | note | Type of inspect / Test and Frequency - Flood test of bund
label | 28a24bba-04ba-5873-9e15-bd5304c6e564 |  | note | Acceptance Criteria - No leak, Water stable over 3 days (taking into account for evaporation, wind)
label | bf8c3e97-6b66-5b0e-aab2-c6c763cbd55e |  | note | Inspection Responsibility: BCL - I
label | 57d2ab4a-2e05-5d4e-aa5a-79566ba0f68e |  | note | Inspection Responsibility: Client - W
label | 213f6069-5e06-522d-a7ef-1d469a8aa1e5 |  | note | Verification Records of Inspection(s) / Test(s) - Photos, drop in water height measurement
checkpoint-group |  |  | section | 9.0 As-builts
checkpoint-status |  |  | checkpoint | 9.1 Redline Drawings
label | 7a47790c-521b-530d-8bd4-333746ea5558 |  | note | Type of inspect / Test and Frequency - Redline Civil Drawings Sets post construction
label | 42f92486-1813-51f1-9ac3-3146a97e36c0 |  | note | Acceptance Criteria - N/A
label | 12eb0021-2293-5463-9734-047b3ee16503 |  | note | Inspection Responsibility: BCL - D
label | 3db41d1d-bcfc-5d8d-a5e6-e8534b4c1a73 |  | note | Inspection Responsibility: Client - R
label | f3f591e4-cf58-5b82-954f-2492e13f3dba |  | note | Verification Records of Inspection(s) / Test(s) - As built drawings
checklist-sectioned |  |  | checklist | ITP 006 - Duct Install | itp |  |  |  | Yes | ITP 006 - Duct Install | 5d8b1884-e64e-4664-915d-abccb38703b3
checkpoint-group |  |  | section | 1.0 Documentation
checkpoint-status |  |  | checkpoint | 1.1 Material approval
label | ee3ab39f-588d-5d12-b981-119acc8bd1c3 |  | note | Type of inspect / Test and Frequency - RFI cover the approval of the service ducts
label | c0cbc17e-ede4-58dc-bf35-682162931b12 |  | note | Acceptance Criteria - RFI response
label | 7ef188a8-21fe-517b-8ecf-235a69d578f8 |  | note | Inspection Responsibility: BCL - D
label | d5465aac-4861-5968-8fca-995796faab02 |  | note | Inspection Responsibility: Client - A
label | 272e031d-0090-5f8b-b104-13d620296fc3 |  | note | Verification Records of Inspection(s) / Test(s) - RFI
checkpoint-status |  |  | checkpoint | 1.2 Service duct Order
label | ebf01d38-5937-5b8c-8b8d-18d83da7c708 |  | note | Type of inspect / Test and Frequency - Humes Drawings – HN-HO-72
label | bc556fce-f9a4-5e0a-91dc-11c58d546cd2 |  | note | Acceptance Criteria - Drawings
label | b67db67a-3368-533a-a8dd-d15491fbacc0 |  | note | Inspection Responsibility: BCL - D
label | 025192ef-f24c-5c6c-a793-343b29b94f8b |  | note | Inspection Responsibility: Client - I
label | 07b607e8-d7f9-5d6b-ac4b-46b13e243fa2 |  | note | Verification Records of Inspection(s) / Test(s) - Humes Drawings
checkpoint-status |  |  | checkpoint | 1.3 Delivery docket
label | 14621f08-ac0f-521a-841c-c12296087308 |  | note | Type of inspect / Test and Frequency - Confirmation that ducts delivered match RFI016 material approval
label | aeccfb25-8a6f-5c3e-8963-249d6e4abcb2 |  | note | Acceptance Criteria - Delivery docket
label | 0baf211e-1d04-56c2-b5fe-275a514d15bf |  | note | Inspection Responsibility: BCL - D
label | 1dadae54-be75-5a6d-bfdf-90dfa1b827f7 |  | note | Inspection Responsibility: Client - I
label | e284fdf8-3561-5152-a0f0-e72eb1a96479 |  | note | Verification Records of Inspection(s) / Test(s) - Delivery Docket
checkpoint-group |  |  | section | 2.0 Install
checkpoint-status |  |  | checkpoint | 2.1 Subgrade
label | a4de0ad5-af4a-5725-8e8f-f89e4fdc4acd |  | note | Type of inspect / Test and Frequency - Confirm uniform subgrade under the duct
label | 1d74aba0-74ff-5dab-80ee-d0e67e0ff682 |  | note | Acceptance Criteria - Subgrade uniform, soft spots removed
label | 1b57cb57-e8b9-5f30-8aef-78e656613426 |  | note | Inspection Responsibility: BCL - V
label | 0d47a4db-4daf-542d-b42f-19892eb12ba4 |  | note | Inspection Responsibility: Client - I
label | b963132f-0f56-5ddc-8812-f190f5dcb16c |  | note | Verification Records of Inspection(s) / Test(s) - Photo of works
checkpoint-status |  |  | checkpoint | 2.2 Bedding
label | 5ee691b5-5c65-58f6-a2c4-53d268e0a2fb |  | note | Type of inspect / Test and Frequency - Prep and bedding, installed, levelled,
label | f4cf58b2-eee5-58e4-a151-cd15c1024d5b |  | note | Acceptance Criteria - Bedding levelled to avoid uneven loading on the ducts
label | a357e57b-415d-5bcc-a742-d40b73d21383 |  | note | Inspection Responsibility: BCL - V
label | 600396aa-dd31-5625-8d3a-f424cde6e7a6 |  | note | Inspection Responsibility: Client - I
label | ef5336ae-809c-5426-8dad-c63b3961d614 |  | note | Verification Records of Inspection(s) / Test(s) - Photo of works
checkpoint-status |  |  | checkpoint | 2.3 Duct Install
label | e3d63912-7e62-5ab7-9530-8a102db3cf16 |  | note | Type of inspect / Test and Frequency - Ducts installed and locked together, top level installed to string line to avoid any steps in top of channel
label | bbe4e5d4-581e-52b6-8ba0-5799eec21810 |  | note | Acceptance Criteria - No steps in top of channel
label | edec60de-f068-5e73-a764-c675fb011144 |  | note | Inspection Responsibility: BCL - V
label | 6603963e-5e5c-560f-a371-bc516b5e3ad6 |  | note | Inspection Responsibility: Client - I
label | e5a0f863-cf9f-5350-be45-af3b6569e90f |  | note | Verification Records of Inspection(s) / Test(s) - Photo of works
checkpoint-group |  |  | section | 3.0 As-builts
checkpoint-status |  |  | checkpoint | 3.1 Redline Drawings
label | 292b85fd-c003-5877-868a-fae388680632 |  | note | Type of inspect / Test and Frequency - Redline drawings of install
label | 4154a47e-0118-5e72-84e9-3302b287f8aa |  | note | Acceptance Criteria - N/A
label | 830966bf-1f79-596e-a375-4da2c10d332b |  | note | Inspection Responsibility: BCL - S
label | e56b8b52-3441-5445-a973-e66cffed3586 |  | note | Inspection Responsibility: Client - A
label | f144d053-2257-5ca3-9dc6-36fa866a122c |  | note | Verification Records of Inspection(s) / Test(s) - Redline Drawings Issued
checkpoint-status |  |  | checkpoint | 3.2 Survey
label | da604390-1211-5971-bd05-fbe3f390fc7d |  | note | Type of inspect / Test and Frequency - GPS coordinates of duct install
label | f90e9f29-e79c-52a2-96d0-f07dc1aac3f1 |  | note | Acceptance Criteria - N/A
label | f6feab7f-c142-5388-bd4f-7cc39e5e55c4 |  | note | Inspection Responsibility: BCL - S
label | 5dec842d-02a6-5123-b02b-cfa2c7307de0 |  | note | Inspection Responsibility: Client - A
label | 099fdb21-3cc1-5159-9888-28119d00a04e |  | note | Verification Records of Inspection(s) / Test(s) - GPS coordinates marked up on drawing
checklist-sectioned |  |  | checklist | ITP 007 - Kerb and Bund Works | itp |  |  |  | Yes | ITP 007 - Kerb and Bund Works | 7bc2f48b-be5f-4479-8d72-c98016c5828e
checkpoint-group |  |  | section | 1.0 Documentation
checkpoint-status |  |  | checkpoint | 1.1 IFC drawings
label | dc767edf-0b29-5f9c-8051-5272965c84ca |  | note | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
label | cc1681a0-a8ea-5dfe-995d-8292a712a9dd |  | note | Acceptance Criteria - Approved IFC/RFI responses
label | 7c54ec8d-76b2-5cdc-92e9-c736526aa1e7 |  | note | Inspection Responsibility: BCL - D
label | d161aef2-361b-54e4-b1ee-eef0d9184403 |  | note | Inspection Responsibility: Client - A
label | ea0f1cc0-cbe4-5366-8180-020a33cd0ebd |  | note | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
checkpoint-status |  |  | checkpoint | 1.2 Material compliance
label | c3864a5b-1449-5523-8349-57281ad812e7 |  | note | Type of inspect / Test and Frequency - Material compliance prior to works – GAP40, GAP20
label | 7f8db901-1f7c-55de-83cb-2476faacdc0b |  | note | Acceptance Criteria - Quary test certificates
label | c7816fb6-0028-57f2-b948-a7afa5c91919 |  | note | Inspection Responsibility: BCL - D
label | 6baa541e-bd0e-535c-9c9f-e60ce003d7d2 |  | note | Inspection Responsibility: Client - A
label | e238dede-61c3-5c3e-9d0c-8005521da9b3 |  | note | Verification Records of Inspection(s) / Test(s) - Quary test certificates
checkpoint-status |  |  | checkpoint | 1.3 Reinforcing
label | 38ec6aee-cc45-5bae-bc19-de3befa0edf5 |  | note | Type of inspect / Test and Frequency - Documentation review
label | 53d39489-efa8-5250-8109-7728b614f8e4 |  | note | Acceptance Criteria - Mill Certs
label | a9809306-8638-56fb-9894-99f7f1c71c3e |  | note | Inspection Responsibility: BCL - D
label | 1abcd14c-b39f-5bdd-b8e0-740bc9525c67 |  | note | Inspection Responsibility: Client - A
label | c51b5aca-546d-53b0-923e-38b7a1b516fa |  | note | Verification Records of Inspection(s) / Test(s) - Mill certs
checkpoint-group |  |  | section | 2.0 Construction - Kerb
checkpoint-status |  |  | checkpoint | 2.1 Excavation
label | c1caf4bc-9301-5dec-ac9a-6aa46cca9b51 |  | note | Type of inspect / Test and Frequency - Subgrade checked and uniform
label | 3e6abb60-ee1f-55e4-a57f-091b855c9dc2 |  | note | Acceptance Criteria - Subgrade uniform
label | dc50862d-df82-54b3-b40d-e7573ebd4a23 |  | note | Inspection Responsibility: BCL - V
label | 1f0bc053-d97a-54a0-a4ba-11bcbcd43f08 |  | note | Inspection Responsibility: Client - I
label | a1f53241-50e0-5b29-aad2-de6b747d462f |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-status |  |  | checkpoint | 2.2 Bedding
label | 3d571bcf-c042-5b66-9632-6a63e13ad8b5 |  | note | Type of inspect / Test and Frequency - Prep and bedding, installed, levelled,
label | a8e989ba-55c2-5290-9210-3522e51c1ec1 |  | note | Acceptance Criteria - Level 100mm of bedding under kerb
label | 915a715b-faba-528b-b1cd-255c5ecafa98 |  | note | Inspection Responsibility: BCL - V
label | 8014e555-e93a-58ab-a4f7-64b03de89a3e |  | note | Inspection Responsibility: Client - I
label | ed825f88-fad6-5130-bd18-961e7d44aa12 |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-status |  |  | checkpoint | 2.3 Reinforcing
label | 2956f5b2-f36b-52bc-8ed2-e6221b8ea612 |  | note | Type of inspect / Test and Frequency - Bars installed at 400mm centres, top of hook checked for cover to top of concrete
label | 92e769ec-7401-5eb6-a0c5-adbc2dcdae86 |  | note | Acceptance Criteria - Visual inspection, String out the TOC
label | 1f5e9db5-215f-5a0a-81a2-9c027391748b |  | note | Inspection Responsibility: BCL - V
label | 438fef78-2e36-5826-8062-8d18c12ce2dc |  | note | Inspection Responsibility: Client - I
label | d8f83b56-1537-51dc-9cfb-1ac42ed6a130 |  | note | Verification Records of Inspection(s) / Test(s) - Photo
checkpoint-status |  |  | checkpoint | 2.4 Concrete
label | 7357f322-9869-5c1f-928a-6a53447fb98a |  | note | Type of inspect / Test and Frequency - Delivery docket checked, once per pour. Concrete strength verified.
label | 5bbc344b-84e1-551d-b1a3-f2ac893b8b1c |  | note | Acceptance Criteria - 20MPA concrete installed, level checked
label | 261cb615-ff25-5c34-846e-0567afd6d779 |  | note | Inspection Responsibility: BCL - D
label | 875228cd-ed42-5394-a160-5e76d116cc99 |  | note | Inspection Responsibility: Client - I
label | 31a26a7c-b8df-58e2-9e77-61aba32c102c |  | note | Verification Records of Inspection(s) / Test(s) - Delivery docket, Concrete crushing strength verified
checkpoint-group |  |  | section | 3.0 As-builts
checkpoint-status |  |  | checkpoint | 3.1 Excavation
label | 96bf89a7-619b-5387-868c-829ea6694689 |  | note | Type of inspect / Test and Frequency - Subgrade checked and uniform
label | 6ad59e59-b5be-5cad-b363-23425344e224 |  | note | Acceptance Criteria - Subgrade uniform
label | 682e3c3d-db24-5ddf-b5d6-b7513b9cd414 |  | note | Inspection Responsibility: BCL - V
label | 9530dac3-e5b1-581a-b6fb-9d9081628785 |  | note | Inspection Responsibility: Client - I
label | 46a2f89f-94a3-5552-ba9b-69dae4718ff7 |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-status |  |  | checkpoint | 3.2 Bedding
label | 619b6d42-851f-52be-9094-7463c0d0adb4 |  | note | Type of inspect / Test and Frequency - Prep and bedding, installed, levelled,
label | 947e8329-0708-5315-8c0b-983023fef3d5 |  | note | Acceptance Criteria - Level 100mm of bedding under kerb
label | 888cf871-9f44-5a3c-bb14-c89259e4152b |  | note | Inspection Responsibility: BCL - V
label | 5b22b2af-18d4-541c-a063-de57afcb6542 |  | note | Inspection Responsibility: Client - I
label | b9dd8e41-2aad-5656-b2ce-8f5de19d92ec |  | note | Verification Records of Inspection(s) / Test(s) - Photos
checkpoint-status |  |  | checkpoint | 3.3 Reinforcing
label | cdab7cd3-1544-5445-a574-5e586b3ad65b |  | note | Type of inspect / Test and Frequency - Bars installed at 400mm centres, top of hook checked for cover to top of concrete
label | 2a6f2f9e-9767-511a-97f6-98d0621f944e |  | note | Acceptance Criteria - Visual inspection, String out the TOC
label | cd2a51a3-f6ae-5efc-96c0-eaa7702b1322 |  | note | Inspection Responsibility: BCL - V
label | 2d4e13cc-ed7f-5392-bcf6-2bc10941ecc8 |  | note | Inspection Responsibility: Client - I
label | 90474fb7-83de-5e1b-b8ab-8922080a5bfb |  | note | Verification Records of Inspection(s) / Test(s) - Photo
checkpoint-status |  |  | checkpoint | 3.4 Concrete
label | e0f7cb3c-83ad-5b3f-9057-16e810caad24 |  | note | Type of inspect / Test and Frequency - Delivery docket checked, once per pour. Concrete strength verified.
label | 38b2ed43-66a9-5fd8-9e34-607dd1dacc24 |  | note | Acceptance Criteria - 20MPA concrete installed, level checked
label | 14f550ff-05f6-5cc6-aad4-59a30d33eb03 |  | note | Inspection Responsibility: BCL - D
label | f19fbc5c-7bd2-55dd-be1f-3bd315b549bc |  | note | Inspection Responsibility: Client - I
label | 06dc565f-3ca6-57f0-a036-c96843dbffe9 |  | note | Verification Records of Inspection(s) / Test(s) - Delivery docket, Concrete crushing strength verified
checkpoint-group |  |  | section | 4.0 Asbuilt
checkpoint-status |  |  | checkpoint | 4.1 Redline drawings
label | 008980a4-db0e-59eb-a707-1c47d4c54c0d |  | note | Type of inspect / Test and Frequency - Complete as built redline drawings of works once complete
label | cc6ed880-0706-5b9d-ab25-293206960b82 |  | note | Acceptance Criteria - Redline drawings capturing changes
label | a450b0be-1804-590b-a0d9-f155977f29f6 |  | note | Inspection Responsibility: BCL - D
label | c558546a-bf1b-58ac-9b41-b48c515461db |  | note | Inspection Responsibility: Client - A
label | 20206f0e-08c7-50f7-be78-e7d0d2c36181 |  | note | Verification Records of Inspection(s) / Test(s) - Redline drawings
checklist-sectioned |  |  | checklist | ITP 009 - PE Tank Fabrication | itp |  |  |  | Yes | ITP 009 - PE Tank Fabrication | 87f8aac4-81a5-463f-bd10-ecc2ad035cd3
checkpoint-group |  |  | section | 1.0 Documentation
checkpoint-status |  |  | checkpoint | 1.1 IFC drawings
label | 8fe94dec-60b8-533d-a7e9-de23524e8c4f |  | note | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
label | 984a34d7-8a17-546c-aeba-8124718012b3 |  | note | Acceptance Criteria - Approved IFC/RFI responses
label | 7006edd7-a6ff-5cab-9629-a566914c5f49 |  | note | Inspection Responsibility: BCL - D
label | 3cf41d9c-e36e-5471-b44a-1771582ea35d |  | note | Inspection Responsibility: Client - A
label | 4d82abf5-b91b-5b73-9fb2-49b92ecb26b8 |  | note | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
checkpoint-status |  |  | checkpoint | 1.2 Design Report complete
label | 35fbd46f-2967-5a31-bcdf-4fefe471e828 |  | note | Type of inspect / Test and Frequency - Design report from fabricator
label | 2eebf8ec-a9a8-5d85-94bc-f4020b07c051 |  | note | Acceptance Criteria - Design report from fabricator
label | 0fd266ea-0fd5-52d8-b345-b298cef44dd0 |  | note | Inspection Responsibility: BCL - D
label | 87961a81-4520-539c-ba6b-1b9e3d27cb14 |  | note | Verification Records of Inspection(s) / Test(s) - Upload design report
checkpoint-group |  |  | section | 2.0 Construction
checkpoint-status |  |  | checkpoint | 2.1 Tank Construction
label | 7f89eb46-487f-5765-986b-faf04a52ab00 |  | note | Type of inspect / Test and Frequency - PE Tank fabricated by approved/competent fabricator
label | 6c772e7c-a2a1-5327-a5b9-4e0898e4b0ff |  | note | Acceptance Criteria - Visual inspection
label | 645e6cd9-0e2a-5b48-bcca-e3dcfa85aab3 |  | note | Inspection Responsibility: BCL - D
label | 17be818c-4d05-5721-9044-9f656b4a83b7 |  | note | Verification Records of Inspection(s) / Test(s) - Upload tank construction documentation from Placon. Photos.
checkpoint-group |  |  | section | 3.0 Testing
checkpoint-status |  |  | checkpoint | 3.1 Leak test tank
label | 1a1264bb-d23a-560e-ac2b-5a5a41339fb9 |  | note | Type of inspect / Test and Frequency - Fill to overflow level, hold for 24 hours. No level change, no visual leaks
label | d28869f8-31b5-5111-bacf-3ec3cacd7dca |  | note | Acceptance Criteria - Leak Test passed
label | f0cb5fe2-42c0-5ec2-9f65-368676d77c42 |  | note | Inspection Responsibility: BCL - T
label | 6341f43c-e5ea-5e97-9083-cde478958f07 |  | note | Verification Records of Inspection(s) / Test(s) - Upload Leak Test report
checkpoint-status |  |  | checkpoint | 3.2 Spark test tank
label | 11abdca4-f04f-5205-9eee-e679da022506 |  | note | Type of inspect / Test and Frequency - Spark test all welds
label | 28d702cd-a276-5580-8af0-c85ef6bc2eb0 |  | note | Acceptance Criteria - Spark Test passed
label | 15d00d9a-ba6e-5323-9bae-a03749639255 |  | note | Inspection Responsibility: BCL - T
label | 1386baf2-ec67-5527-ab25-1597b83c2fce |  | note | Verification Records of Inspection(s) / Test(s) - Upload Spark test report
checkpoint-group |  |  | section | 4.0 Certification
checkpoint-status |  |  | checkpoint | 4.1 Stationary Container Tank Compliance Certificate
label | d94cc94f-93ed-5ef8-a7a9-2d13e5126b28 |  | note | Type of inspect / Test and Frequency - Worksafe authorised certifier to provide compliance certificate
label | 3f3b8525-611e-59a8-888b-60156683c67b |  | note | Acceptance Criteria - Compliance certificate
label | b08c3399-2d8c-5629-a77c-29ba16d926e9 |  | note | Inspection Responsibility: BCL - D
label | dc1f53fc-96c3-5de4-83e7-5fc14ee6987e |  | note | Verification Records of Inspection(s) / Test(s) - Upload certificate
checklist-sectioned |  |  | checklist | ITP 003 - Structural Steel | itp |  |  |  | Yes | ITP 003 - Structural Steel | 9a817ee9-29bb-4a36-9cfe-dd520b69e221
checkpoint-group |  |  | section | 1.0 Documentation
checkpoint-status |  |  | checkpoint | 1a Construction Drawings
label | b67b579b-08e9-5b01-b091-71dda0157ef9 |  | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
label | 7a3841dd-3e01-5a8c-ac1c-f3b5e2a38275 |  | note | Acceptance Criteria - IFC Drawings
label | 97f7f8ff-36a9-58ce-b465-4a74d1a04831 |  | note | Inspection Responsibility: BCL - I
label | 2534d32d-f5d8-56d6-bbbf-53025882df23 |  | note | Inspection Responsibility: Client - S
label | adce0c16-53ec-5595-bbb3-c72e0ca61cc4 |  | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
checkpoint-status |  |  | checkpoint | 1b Shop Drawings
label | 74781f40-91e4-58ec-ba72-c2ee72ffad36 |  | note | Type of inspect / Test and Frequency - All drawings are for construction and latest revision. (hold Point)
label | 10d95601-aa1d-5fbd-9b83-2790b8d61f05 |  | note | Acceptance Criteria - AISC Detailing for Steel Construction
label | d5ee86c9-b755-5ef7-8936-f684a85ebfe1 |  | note | Inspection Responsibility: BCL - H
label | 9a09be82-fc5f-5714-b3fb-acdd55cfe886 |  | note | Inspection Responsibility: Client - A
label | 56923599-2018-5349-9092-647a9eaa2bfc |  | note | Verification Records of Inspection(s) / Test(s) - Drawing Register
holdpoint |  |  | signoff | HOLD POINT
checkpoint-group |  |  | section | 2.0 Manufacturing
checkpoint-status |  |  | checkpoint | 2a Structural Steel
label | c9beee47-f1f5-5dda-aae4-0d435a2ca571 |  | note | Type of inspect / Test and Frequency - Confirm structural steel grade is correct
label | a693c76a-f3e1-5bf2-ada7-2793a482a797 |  | note | Acceptance Criteria - Sec. 19 4.15.1.1 Table 1. Materials
label | 39a480b8-80e6-57b3-b054-628cd07aa043 |  | note | Inspection Responsibility: BCL - D
label | b1dc7899-a7fc-5caa-83cb-3c594de4df6e |  | note | Inspection Responsibility: Client - R
label | 643195b7-f673-526b-808d-a8ef3d65a202 |  | note | Verification Records of Inspection(s) / Test(s) - Manufacturers Mill Certificates
checkpoint-status |  |  | checkpoint | 2b Nuts, Bolts, & Washers
label | e3b7a973-d4ff-570c-b276-767d7021ef48 |  | note | Type of inspect / Test and Frequency - Confirm nuts, bolt and washer materials are hot dip galvanised
label | cf197d17-6c6c-50a9-9ee7-618d09ce29eb |  | note | ○ Approved stainless steel components must be Grade A4 (Austenitic 316) strength 70
label | a79ff392-89df-502e-890c-49ba3b5984e4 |  | note | Acceptance Criteria - AS 1214 IFC Shop Drawings Bill of Materials
label | b044cf10-e725-54b4-a7d4-95d44165d563 |  | note | Inspection Responsibility: BCL - D
label | 4b9aa9ce-7416-55fc-934d-b71852ff6b74 |  | note | Inspection Responsibility: Client - R
label | 79465dbf-5685-5c18-8abd-c6817f167d9f |  | note | Verification Records of Inspection(s) / Test(s) - Manufacturers Mill Certificates
checkpoint-group |  |  | section | 3.0 Delivery, Storage & Handling
checkpoint-status |  |  | checkpoint | 3a Delivery
label | 0663b731-202b-59df-aca7-154388851055 |  | note | Type of inspect / Test and Frequency - Check structural steel is undamaged; not misshapen, no surface damage, free from contaminants etc. on delivery
label | 9b62d5ee-0412-52f7-9bf5-fa21e091cb41 |  | note | Acceptance Criteria - NZS 3404
label | 381084f8-34b3-5a5b-a731-0d4daa170986 |  | note | Inspection Responsibility: BCL - D
label | 89c596ca-44bd-5f78-83da-6c38e33b8cb3 |  | note | Inspection Responsibility: Client - R
label | 509445d1-0365-5bbe-91c2-2514723ffb5b |  | note | Verification Records of Inspection(s) / Test(s) - Delivery Dockets Photos
checkpoint-group |  |  | section | 4.0 Welding
checkpoint-status |  |  | checkpoint | 4a Nominate Inspector
label | f224957e-c6d2-5cfd-8fc2-12c2fea5462f |  | note | Type of inspect / Test and Frequency - Employ approved independent Welding Inspector.
label | 8063a093-a130-5dec-b60d-afcf81b88ad3 |  | note | ○ Submit two weeks before fabrication
label | 7677c2e2-4ddc-5eed-a7e1-5951aa8875a9 |  | note | Acceptance Criteria - CBIP
label | cef84662-b28f-521e-8c30-c0ab0db0fb08 |  | note | Inspection Responsibility: BCL - S
label | 627c6de6-6325-5ff8-8d1e-a68618d482b9 |  | note | Inspection Responsibility: Client - A
label | 458ecbc8-5af1-5b2b-a112-490cbbb61fcf |  | note | Verification Records of Inspection(s) / Test(s) - N/A
checkpoint-status |  |  | checkpoint | 4b Welder Qualifications
label | 6dbe7b3e-6d73-5e8b-9b00-2df7549d9ac0 |  | note | Type of inspect / Test and Frequency - Ensure welders are competent and accredited to carry out welding activity prior to construction.
label | ab06b41e-a1fd-5c61-aa75-acfaf4868294 |  | note | Acceptance Criteria - ASME IX
label | 5f28dd2b-774d-55d2-b4cc-1430540d3274 |  | note | Inspection Responsibility: BCL - I
label | 3f82328a-a77b-5fd4-8bdc-2949ffe1545f |  | note | Inspection Responsibility: Client - I
label | 56698b2b-31b7-5eb1-9a5f-f39d2e1618b6 |  | note | Verification Records of Inspection(s) / Test(s) - Welder Qualification Records
checkpoint-status |  |  | checkpoint | 4c Weld Procedure
label | d095b31a-6383-5ff9-851a-ca1ed5ff4dc3 |  | note | Type of inspect / Test and Frequency - Ensure procedure is Code compliant to weld specification of applicable work being done
label | 7616bd75-e438-54a6-82a9-e948df58734d |  | note | ○ All welds to be category GP unless category SP nominated
label | d8ab1382-c663-5175-bd95-d5c5ef2c5d38 |  | note | Acceptance Criteria - ASME IX
label | fcbe2135-1a83-5954-96d3-6993aeb70a48 |  | note | Inspection Responsibility: BCL - A
label | 2bb3344e-d541-512a-8280-7d44d761756a |  | note | Inspection Responsibility: Client - I
label | ac7896b1-69d8-5412-9023-3911f26bd895 |  | note | Verification Records of Inspection(s) / Test(s) - Welding Procedure
checkpoint-status |  |  | checkpoint | 4d Weld Inspection (Visual)
label | b3abc3f8-8175-51aa-959b-45ebc31693b3 |  | note | Type of inspect / Test and Frequency - The extent of Non-Destructive examination listed in Sec. 19 4.15.2.4
label | cd79b3ab-8c07-5eab-9ad5-95144065acc2 |  | note | Acceptance Criteria - ASME IX
label | bb32da98-6123-5e1b-8f44-bf2f1f6f7312 |  | note | Inspection Responsibility: BCL - I
label | 63f09455-4517-58ac-8960-07e94debaae1 |  | note | Inspection Responsibility: Client - I
label | 4084571a-3203-5116-9651-677c45e5c60a |  | note | Verification Records of Inspection(s) / Test(s) - Inspector report
checkpoint-group |  |  | section | 5.0 Corrosion Protection
checkpoint-status |  |  | checkpoint | 5a Nominate Inspector
label | 183a1b3b-ee15-5104-b980-91e0917b933f |  | note | Type of inspect / Test and Frequency - Employ approved independent Painting Inspector
label | 83f413b9-de15-5163-9936-1499ad8e3517 |  | note | Acceptance Criteria - CBIP
label | 6bce3563-7fff-5509-afa4-ad162852e35b |  | note | Inspection Responsibility: BCL - D
label | 224f1c2e-e785-577e-9d43-2d7695067634 |  | note | Inspection Responsibility: Client - R
label | c905b015-0ee5-5a18-9ea1-1fbd4108c254 |  | note | Verification Records of Inspection(s) / Test(s) - N/A
checkpoint-status |  |  | checkpoint | 5b Preparation
label | a57fc077-8d3e-50fd-bc38-2f0da950f21f |  | note | Type of inspect / Test and Frequency - Thoroughly clean all surfaces of oil and grease with turpentine, not kerosene.
label | 20ab367c-86b8-58f3-aa50-ace164909890 |  | note | ○ Visual Inspection
label | 0e77d813-45ea-5851-8395-e97265c5ab7a |  | note | Acceptance Criteria - Sa 21/2 in S1S 055900
label | 34596ca7-9d19-577c-bd19-e2a887756504 |  | note | Inspection Responsibility: BCL - D
label | 9fafb592-c43c-58ab-a367-0e86e0b15428 |  | note | Inspection Responsibility: Client - R
label | b08962e9-8ee3-5d14-99b1-78c0f0255870 |  | note | Verification Records of Inspection(s) / Test(s) - Galvanising QA Package
checkpoint-status |  |  | checkpoint | 5c Galvanising
label | 854b0811-b3eb-53f7-b63c-7bc2f99c804c |  | note | Type of inspect / Test and Frequency - Apply Zinc coating by hot dip process to give coating weight of not less than 600g/m2
label | 9e7110c4-8c64-562c-a301-82625af4091b |  | note | Acceptance Criteria - AS/NZS 4680
label | b4e754d2-5055-5c24-b189-827f689c941d |  | note | Inspection Responsibility: BCL - D
label | 5cc6c635-932c-5591-a7bd-36436ac5e0a0 |  | note | Inspection Responsibility: Client - R
label | ea118955-6380-5020-87fc-6c4bfa338c90 |  | note | Verification Records of Inspection(s) / Test(s) - Galvanising QA Package
checkpoint-status |  |  | checkpoint | 5d Galvanising Inspection
label | 86d80fa6-05cb-5b9c-ad7a-13705977c65c |  | note | Type of inspect / Test and Frequency - Inspect for defects, misses, etc.
label | beb1174a-29d7-54d9-8162-67a06e05b6a8 |  | note | ○ Dry film thickness measurements and demonstration that film build up has been achieved
label | e760dfe8-21bb-5e62-a429-edcb17600f6b |  | note | Acceptance Criteria - AS3894
label | 910e8523-de60-5988-8f05-44ebc8e716d4 |  | note | Inspection Responsibility: BCL - D
label | 0b30708e-c459-5f82-92fb-77f352afb802 |  | note | Inspection Responsibility: Client - R
label | 76fc4f10-5e45-5a3f-b911-e64a53f67cf8 |  | note | Verification Records of Inspection(s) / Test(s) - Galvanising QA Package Painting Inspector Report
checkpoint-group |  |  | section | 6.0 Grouting
checkpoint-status |  |  | checkpoint | 6a Grouting Mix
label | 9546eca1-5676-5009-8935-a90b8596d959 |  | note | Type of inspect / Test and Frequency - 50MPa grout to be used, mixing as per the manufacturer spec
label | 5325a99b-acac-5541-a06a-ea64b0a22def |  | note | Acceptance Criteria - NZS 3404
label | 5c73ffc0-3f53-59e9-9050-3b5e430d928d |  | note | Inspection Responsibility: BCL - D
label | d51b3727-07ae-5e82-b525-37aef27be580 |  | note | Inspection Responsibility: Client - R
label | 61c3b1b1-ea07-58b0-9249-ceb47e34ebac |  | note | Verification Records of Inspection(s) / Test(s) - Delivery docket
checkpoint-group |  |  | section | 7.0 As-builts
checkpoint-status |  |  | checkpoint | 7a Redline Drawings
label | 770e2c1f-e92b-57af-a5e8-d00220bfc7ee |  | note | Type of inspect / Test and Frequency - Redline Structural Drawings Sets post construction
label | 17b82f5e-3bca-5d03-bd49-16732d486620 |  | note | Acceptance Criteria - N/A
label | b9481f30-23bf-5c96-b818-71285b3cf585 |  | note | Inspection Responsibility: BCL - D
label | f013e141-cf3e-5de9-9bda-aab6a00e6259 |  | note | Inspection Responsibility: Client - R
label | 45fabb00-6ddc-5602-a2fd-16e339ecfbcf |  | note | Verification Records of Inspection(s) / Test(s) - As-Builts
checklist-sectioned |  |  | checklist | ITP 008 - Bund Liner Fabrication & Installation | itp |  |  |  | Yes | ITP 008 - Bund Liner Fabrication & Installation | b212975b-c921-4db8-8f14-ac5c58e331d4
checkpoint-group |  |  | section | 1.0 Documentation
checkpoint-status |  |  | checkpoint | 1.1 IFC drawings
label | fe759bbd-07cb-5d6d-aecc-0d5268004f8e |  | note | Type of inspect / Test and Frequency - IFC drawings and RFIs for any changes
label | 48771e88-e838-5eea-b7ae-6d14de56ad5f |  | note | Acceptance Criteria - Approved IFC/RFI responses
label | a3442b8c-52fa-594e-b8ad-f5bbeb58fb81 |  | note | Inspection Responsibility: BCL - D
label | 5572a5c4-47c3-57ef-abcc-68f295f8b18e |  | note | Inspection Responsibility: Client - A
label | a07d4424-c280-5d7d-acfc-9ca794f92fc6 |  | note | Verification Records of Inspection(s) / Test(s) - IFC Drawings and RFIs uploaded
checkpoint-status |  |  | checkpoint | 1.2 Design Report complete
label | c4a0be49-c326-5608-bf08-ca8547888f9f |  | note | Type of inspect / Test and Frequency - Design report from fabricator
label | 9d89aa88-148c-50d3-bfd3-7c2995991cf4 |  | note | Acceptance Criteria - Design report from fabricator
label | b5a23116-2480-5d40-ba88-45289fcdef69 |  | note | Inspection Responsibility: BCL - D
label | e52e93c2-a16b-53e9-ae40-e3b091fd3e72 |  | note | Verification Records of Inspection(s) / Test(s) - Upload design report
checkpoint-group |  |  | section | 2.0 Construction
checkpoint-status |  |  | checkpoint | 2.1 Tank Construction
label | 14ce1e9d-881e-5784-9e14-89f389f952c0 |  | note | Type of inspect / Test and Frequency - PE Tank fabricated by approved/competent fabricator
label | 1b581d6b-1f03-5120-9861-82f8bee386d4 |  | note | Acceptance Criteria - Visual inspection
label | de3994c8-ee3c-5a16-a41a-3a37f641fefd |  | note | Inspection Responsibility: BCL - D
label | 9defb522-a70b-5786-90f4-7944e2cb5359 |  | note | Verification Records of Inspection(s) / Test(s) - Upload tank construction documentation from Placon. Photos.
checkpoint-group |  |  | section | 3.0 Testing
checkpoint-status |  |  | checkpoint | 3.1 Leak test tank
label | 502cc4cc-e42c-5680-9da7-0be25ecb8317 |  | note | Type of inspect / Test and Frequency - Fill to overflow level, hold for 24 hours. No level change, no visual leaks
label | 4c5f78cb-2545-5b25-b37f-0c9fa980ca3a |  | note | Acceptance Criteria - Leak Test passed
label | 45e6bd43-46b4-5098-9bea-2e09a8b623ad |  | note | Inspection Responsibility: BCL - T
label | 4a11fb9a-10ee-5713-afd0-131f1a9daa4a |  | note | Verification Records of Inspection(s) / Test(s) - Upload Leak Test report
checkpoint-status |  |  | checkpoint | 3.2 Spark test tank
label | b09c4916-0eeb-5e53-91a0-72cba9e6d6c1 |  | note | Type of inspect / Test and Frequency - Spark test all welds
label | 5b1e7e74-c98d-5661-9d6f-c3c94f08abae |  | note | Acceptance Criteria - Spark Test passed
label | 60a1c245-fcb4-5c88-953a-e0beb7b7b42e |  | note | Inspection Responsibility: BCL - T
label | 2cb775fa-dded-5058-841e-7663eeebca47 |  | note | Verification Records of Inspection(s) / Test(s) - Upload Spark test report
checkpoint-group |  |  | section | 4.0 Certification
checkpoint-status |  |  | checkpoint | 4.1 Stationary Container Tank Compliance Certificate
label | bc858bef-701a-56b3-9736-fffdb6d6f1c8 |  | note | Type of inspect / Test and Frequency - Worksafe authorised certifier to provide compliance certificate
label | a29913dc-b606-536d-875e-70120a78c5d8 |  | note | Acceptance Criteria - Compliance certificate
label | 46ac0504-df0f-55fe-ab82-037f5a1ce473 |  | note | Inspection Responsibility: BCL - D
label | cdc163ce-f8c4-5b30-a936-53ca1cd235bd |  | note | Verification Records of Inspection(s) / Test(s) - Upload certificate