## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP 011 - Bund Construction - Concrete Works | itp |  |  |  |  | ITP 011 - Bund Construction - Concrete Works
section | 1.0 Documentation
checkpoint | 1.1 Construction Drawings
label | Type of inspect / Test and Frequency - All drawings are for construction and latest revision.
label | Acceptance Criteria - Latest IFC Drawings
label | Inspection Responsibility: BCL - I
label | Inspection Responsibility: Client - S
label | Verification Records of Inspection(s) / Test(s) - Drawing Register
checkpoint | 1.2 Concrete mix design
label | Type of inspect / Test and Frequency - Submitted to Beca for approval
label | Acceptance Criteria - Approved RFI
label | Inspection Responsibility: BCL - H
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - RFI
holdpoint | HOLD POINT
section | 2.0 Excavation
checkpoint | 2.1 Set Out, as per latest “For Construction” revision
label | Type of inspect / Test and Frequency - Survey and mark the bund location
label | Acceptance Criteria - IFC Drawings, Survey data check by PM
label | Inspection Responsibility: BCL - T
label | Inspection Responsibility: Client - I
label | Verification Records of Inspection(s) / Test(s) - Survey Record, Redline Drawings
checkpoint | 2.2 Subgrade inspection
label | Type of inspect / Test and Frequency - Scala testing to confirm subgrade is of sufficient strength
label | ○ Witness by engineer
label | ○ Minimum of 2 tests per bund pour
label | Acceptance Criteria - Minimum of 5 blows per 150mm
label | Inspection Responsibility: BCL - H
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - Scala Test Results
holdpoint | HOLD POINT
section | 3.0 Post Excavation
checkpoint | 3.1 >150mm compacted hard fill under bund (GAP20)
label | Type of inspect / Test and Frequency - Clegg hammer testing, 5x5 grid, minimum of 4no per bund pour
label | Acceptance Criteria - Clegg CIV>10
label | Inspection Responsibility: BCL - T
label | Inspection Responsibility: Client - R
label | Verification Records of Inspection(s) / Test(s) - Clegg results
section | 4.0 Concrete works
checkpoint | 4.1 Site concrete
label | Type of inspect / Test and Frequency - Visual inspection and record of site concrete install, completed for each slab pour
label | Acceptance Criteria - 50mm site concrete poured to base level of foundation +0mm -10mm tolerance
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Photos, Concrete pour record
checkpoint | 4.2 DPM
label | Type of inspect / Test and Frequency - Visual inspection and record of DPM installed, completed prior to each pour
label | Acceptance Criteria - Polythene laid on site concrete prior to reinforcing
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Photos, Concrete pour record
checkpoint | 4.3 Reinforcing (material)
label | Type of inspect / Test and Frequency - Review documentation for each pour
label | Acceptance Criteria - Reinforcing to be Grade 500E to ASS/NZS4671
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Mill certificates, Detail sheet
checkpoint | 4.4 Sump Construction
label | Type of inspect / Test and Frequency - Reinforcing check, dimension check, Formwork check
label | Acceptance Criteria - As per IFC drawings
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint | 4.5 Reinforcing install
label | Type of inspect / Test and Frequency - Measure to check cover, bar size and arrangement, lap length and type. Complete prior to pouring concrete.
label | Acceptance Criteria - Reinforcing matches IFC drawings, any deviations recorded and acceptance agreed with engineer prior to pour
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
checkpoint | 4.6 Reinforcing install
label | Type of inspect / Test and Frequency - Starter bars for tank plinth, Starter bars for blockwork
label | Acceptance Criteria - Matches IFC drawing
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
checkpoint | 4.7 Tank plinth
label | Type of inspect / Test and Frequency - Size of plinth, height of plinth, Reinforcing checked, Formwork checked
label | Acceptance Criteria - Matches IFC drawing and response of RFI017
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record, Photos
checkpoint | 4.8 Concrete pour
label | Type of inspect / Test and Frequency - Embedded items located in slab
label | ○ Ducting
label | ○ Pits
label | Acceptance Criteria - Matches IFC drawings
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record, photos
checkpoint | 4.9 Concrete pour
label | Type of inspect / Test and Frequency - Level check, formwork check, cover check. Inspections prior to every pour.
label | Acceptance Criteria - Matches IFC drawing dimensions and notes
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - W
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint | 4.10 Pour inspection/Approval to pour
label | Type of inspect / Test and Frequency - Pre pour inspection by Beca Engineer (hold Point)
label | Acceptance Criteria - Approval from Engineer to pour
label | Inspection Responsibility: BCL - H
label | Inspection Responsibility: Client - A
holdpoint | HOLD POINT
checkpoint | 4.11 Concrete strength
label | Type of inspect / Test and Frequency - Test certificate 7 and 2no 28day tests required for each pour day or per 70m3
label | Acceptance Criteria - 28 day compressive strength >40mPa
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - R
label | Verification Records of Inspection(s) / Test(s) - Test certificate
section | 5.0 Blockwork
checkpoint | 5.1 Blockwork (material)
label | Type of inspect / Test and Frequency - Manufacturer documentation. Required once prior to commencement of works.
label | Acceptance Criteria - Masonry units meet AS/NZS4455
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - R
label | Verification Records of Inspection(s) / Test(s) - Supplier documentation
checkpoint | 5.2 Blockwork (reinforcing)
label | Type of inspect / Test and Frequency - Inspect bar size, placement, lap length and number (once per pour)
label | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - R
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint | 5.3 Blockwork (pour)
label | Type of inspect / Test and Frequency - Inspection prior to pour, check washout location, dimensions, line and level (once per pour)
label | Acceptance Criteria - Install matches IFC drawings and notes. Deviations agreed with engineer via approved RFI
label | Inspection Responsibility: BCL - W
label | Inspection Responsibility: Client - A
label | Verification Records of Inspection(s) / Test(s) - Concrete pour record
checkpoint | 5.4 Concrete strength
label | Type of inspect / Test and Frequency - Test certificate 7 and 2no 28day tests required for each pour day
label | Acceptance Criteria - 28 day compressive strength >17.5mPa
label | Inspection Responsibility: BCL - R
label | Inspection Responsibility: Client - R
label | Verification Records of Inspection(s) / Test(s) - Test certificate
section | 6.0 As-builts
checkpoint | 6.1 Redline Drawings
label | Type of inspect / Test and Frequency - Redline Civil Drawings Sets post construction
label | Acceptance Criteria - N/A
label | Inspection Responsibility: BCL - D
label | Inspection Responsibility: Client - R
label | Verification Records of Inspection(s) / Test(s) - As built drawings