## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | Master 11kV Bus Testing |  | Master 11kV Bus Testing | 91b63bb5-a899-49bb-b5fc-3018319ceceb
| checkpoint | Test Report for Circuit Breaker
| checkpoint | Bus Work Resistance Test
| checkpoint | Earthing Resistance Test
| checkpoint | All poles in same position before first operation
| checkpoint | Resistance of main circuit
| checkpoint | Timing
| checkpoint | Insulation Resistance
| checkpoint | Control Equipment Insulation Resistance
| checkpoint | Interlock functioning
| checkpoint | Alarms and Indications correct
| checkpoint | Functional operation checks
| checkpoint | HV Pressure Test
| checklist | Master 11kV Circuit Breaker Testing |  | Master 11kV Circuit Breaker Testing | 32b00acb-01ce-424f-86c6-8ad4c80f67c7
| checkpoint | Test Report for CBs
| checkpoint | Insulation Resistance
| checkpoint | Main Contact Resistance
| checkpoint | Minimum Operation
| checkpoint | CB Timing
| checkpoint | Control and Alarm Pressure Switch Test
| checkpoint | Function Checks
| checkpoint | HV Pressure Test
| checklist | Master 11kV Current Transformer Testing |  | Master 11kV Current Transformer Testing | 029619ff-a78f-4706-b6b5-a2d40e536956
| checkpoint | Confirm system Numbering "AS BUILD" SLD as required
| checkpoint | Test Report for CT
| checkpoint | Insulation Resistance
| checkpoint | Ratio Error Tests
| checkpoint | Excitation Characteristics
| checkpoint | CT Burden Tests
| checkpoint | Polarity & Primary Injection to Device
| checklist | Master 11kV Indoor Switchgear Installation |  | Master 11kV Indoor Switchgear Installation | c1c67120-10bf-4947-a02e-54774b8f56e8
| checkpoint | Check items complete and for transit damage
| checkpoint | Assemble equipment to manufacturers drawings and instructions
| checkpoint | Equipment installed on hold down bolts and bolts torqued
| checkpoint | All bolts tightened as specified
| checkpoint | Connected to Earth Grid as per drawings
| checkpoint | Connect equipment ancillaries
| checkpoint | Busbar DC Resistance checked (Ductor)
| checkpoint | Cable installation and termination completed
| checkpoint | Correct terminal crimp lugs used
| checkpoint | Cabling Terminated to Circuit Breaker Junction Boxes and JB's cleaned
| checkpoint | Trunking and termination covers in place
| checkpoint | Nameplate data recorded
| checkpoint | Phase colours and equipment numbers installed
| checkpoint | Mark up "As built" drawings.
| checklist | Master 11kV Voltage Transformer Testing |  | Master 11kV Voltage Transformer Testing | 0fb7eb84-e4f3-4f4b-8969-6b8dcaa46fd3
| checkpoint | Confirm system Numbering "AS BUILD" SLD as required
| checkpoint | Test Report for Voltage Transformers
| checkpoint | Polarity Test
| checkpoint | Insulation Resistance
| checkpoint | VT Ratio & Phasing Check
| checkpoint | Low Voltage Terminal earthed
| checkpoint | Terminals d1/d2 shorted
| checkpoint | Tightness of all connections checked
| checkpoint | Frame & control cabinets checked as earthed
| checkpoint | Burden and Loading Resistor Checks
| checklist | Master Bus Duct Installation 1 |  | Master Bus Duct Installation 1 | 16bdbd0d-418c-48ef-aab8-9b7f4299fb9d
| checkpoint | Setting Out: Floor Box slab penetration have been coordinated and accurately marked out.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master Cable Ladder/Tray Installation |  | Master Cable Ladder/Tray Installation | c6c6160f-2c1b-4904-b157-d18f6003745f
| checkpoint | Ladder rack approved for use in relay or control room
| checkpoint | Cable ladder supported by fixing to structural members of building
| checkpoint | No cable ladder supported by relay or control panels
| checkpoint | Cable ladder earthed directly to the main station earth grid at an interval of not more than 5m
| checkpoint | No cable ladder earthed via panel earthing
| checkpoint | Joints bonded to earthed
| checkpoint | Cut ends of ladder and tray correctly treated
| checkpoint | Fit labels on ladder/tray if required by Specification
| checkpoint | Fit ladder covers if required by specification
| checkpoint | Rodent proofing - All entry Points to raceway rodent/fire proof
| checkpoint | Mark up "As built" drawings.
| checklist | Master Cable Tray, Ladder & Basket Installation |  | Master Cable Tray, Ladder & Basket Installation | 19b72231-9055-4fc7-a8a5-3958597d2a94
| checkpoint | Setting Out: Tray, Ladder and Basket has been run level, straight and parallel with the building lines as per C2112.3.
| checkpoint | Installation: Tray, Ladder and Basket has been installed per agreed technical submission requirements and as per C2112.10, 11 & 13.
| checkpoint | Installation: Fixings and fastenings are of material appropriate to the parts being fixed and the loads imposed as per C2112.3 and approved Gravity Support methods.
| checkpoint | Installation: Fixings and fastenings are of material appropriate to the parts being fixed and the loads imposed as per C2112.3 and approved Seismic Support methods.
| checkpoint | Installation: HST3 M12 x 145 seismic anchors are used/installed as per the WSP seismic design
| checkpoint | Installation: Correct embedment (145mm) of HST3 seismic anchors has been achieved in accordance with Hilti installation instructions.
| checkpoint | Installation: Correct torque setting (60nM) of HST3 seismic anchors has been achieved in accordance with Hilti installation instructions.
| checkpoint | Installation: Joints and accessories fit closely and are correctly matched as per C2112.3.
| checkpoint | Installation: All sharp edges have been removed, cut ends/cut-outs are neat and square and protected against corrosion as per C2112.3.
| checkpoint | Installation: Cable support systems have been assembled so that sharp edges, screws or other fixing materials do not penetrate the cable corridor as per C2112.3.
| checkpoint | Installation: Colour coding of Tray, Ladder and Basket has been installed as per C2112.9.
| checkpoint | Installation: Solar shields, covers and guards have been installed as per C2112.12.
| checkpoint | Installation: Non-continuous runs of Tray, Ladder and Basket have been provided with additional earth continuity straps bolted between sections as per C2112.8.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master DC Installation |  | Master DC Installation | b24f95c6-7f0d-40e5-9615-82e4b9e1a9e5
| checkpoint | Verify that drawings are latest revision and manufacturer's manuals
| checkpoint | Use rubber gloves and eye protection when handling batteries. Install bank.
| checkpoint | Look for corrosion, heat, sturdiness/tightness of links, straps - terminals. Petroleum jelly on terminals should be clean, if necessary add. Clean top of batteries where necessary.
| checkpoint | Modern batteries are a `sealed unit' type. Do not open vent plugs nor take specific gravity test, nor fluid top up.
| checkpoint | When battery bank is connected to the load, check and record `load volts' reading is taken under normal in service conditions with all fuses in and charger on.
| checkpoint | Read and record ambient air temperature.
| checkpoint | Install clip on ammeter on any suitable flexible battery link.
| checkpoint | Read and record ripple current.
| checkpoint | Using the Bite Battery Impedance Tester. Carry out Battery Impedance Tests.
| checkpoint | Note and record total AC current on clip on ammeter which must be more than 5 amp. If less than 5 amp receiver will read Lo=(A).
| checkpoint | If receiver reading is suitable i.e. approx 1.635 AC m/ohms is encountered, note and record this result. Check manufacturers spec. Record results on battery impedance sheet.
| checkpoint | Note and record total current. Read from clip on ammeter.
| checkpoint | Note and record source current. Read from `bite' meter. Repeat for all Battery Units
| checkpoint | Analyse results according to "Biddle" instruction manual. Any individual battery with an AC OHM reading outside the tolerance requires particular notification and further investigation. +/- 20% Tolerance allowed.
| checkpoint | Battery impedance test is to determine the gradual deterioration of batteries by comparing one to others in the bank. Note new battery profile is required on acceptance of bank.
| checkpoint | Ensure all tests completed and result sheets filled out.
| checkpoint | Battery stand equipment located in correct position. All parts for assembly complete.
| checkpoint | Assembly of stand carried out to manufacturer specifications.
| checkpoint | Battery stand bolted to the floor and earthed correctly.
| checkpoint | Batteries mounted in stand with orientation and polarity markings correct.
| checkpoint | Correct links used to connect up batteries used.
| checkpoint | Links bolted up to the correct manufacturers tension.
| checkpoint | Labels fixed in position and are correct.
| checkpoint | Inspection of stand completed.
| checkpoint | Drawings are 'as built'
| checklist | Master DC Testing |  | Master DC Testing | df245365-7bef-44bf-b1d4-7747f93aaeb9
| checkpoint | Battery Charger Acceptance Tested
| checkpoint | Battery Impedance/ Discharge Tests completed
| checklist | Master Ducting Installation |  | Master Ducting Installation | 40300ae6-6b19-49b8-a735-9f4d28885ff7
| checkpoint | Hold Point: Trenching completed by others, requirements listed under C2115.2.
| checkpoint | Setting Out: Bedding material selected and installed as per AS/NZS 3000:2007 3.11.4.2.
| checkpoint | Setting Out: Clearance from other services maintained as per AS/NZS 3000:2007 3.9.8.4.
| checkpoint | Installation: Category of installation selected per specification and installed as per AS/NZS 3000:2007 3.11.3.
| checkpoint | Installation: Long radius sweeps or bends used for all changes in direction (elbows not acceptable) as per C2115.3.3.
| checkpoint | Installation: Mechanical protection selected and installed in accordance with category of underground wiring system.
| checkpoint | Installation: Duct joints glued to prevent water ingress as per C2115.3.3.
| checkpoint | Installation: Ducts cleaned of rocks/debris as per C2115.3.3.
| checkpoint | Installation: Duct proved and draw wire installed as per C2115.3.3.
| checkpoint | Installation: Ducts provided with suitable sized end caps to prevent the ingress of soil as per C2115.3.3.
| checkpoint | Hold Point: Notice has been issued to BECA for inspection prior to backfilling as per C2115.1.
| checkpoint | Hold Point: Backfilling completed by others, requirements listed under C2115.4.
| checkpoint | Installation: Identification of underground wiring provided as per AS/NZ 3000:2007 3.11.4.5.
| checkpoint | Installation: Duct penetrations to subfloor maintained as continuous as per C2100.2.3.
| checkpoint | Ducts cut flush with level 0 slab for passive fire treatment as per C2100.2.3.
| checkpoint | Sign-Off: Underground wiring system minimum depth of cover achieved as per AS/NZS 3000:2007 table 3.6.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master Earthing |  | Master Earthing | f2b696df-a5a8-4284-9fd4-285528756c8e
| checkpoint | All staff briefed on safety requirements and installation procedure
| checkpoint | Verify that drawings are latest revision and manufacturer's manuals available on site.
| checkpoint | Correct type and rating of Earthing Conductor
| checkpoint | Earth bus bars installed standoffs correct size
| checkpoint | Mark out Earthing layout per drawing
| checkpoint | Tray etc installed and bonded
| checkpoint | Install earthing conductor attached to tray as applicable
| checkpoint | All equipment connected to earth grid/bus bar
| checkpoint | Check each piece of equipment is earthed by connection to the nearest earth bar
| checkpoint | Check continuity of all earthing cables.
| checkpoint | Resistivity of earth (using fall of potential)
| checkpoint | Continuity of new earths
| checkpoint | Resistance to Earth grid ( point to point tests )
| checkpoint | Drawings are 'as built'
| checklist | Master First Fix Installation |  | Master First Fix Installation | d36fcdc1-2476-495a-a3da-1b8c81276c44
| checkpoint | Cable Supports: Catenary Wires are galvanised steel type with a maximum of 5 cables as per C2102.6 and appropriately sized and secured as per C2112.19.
| checkpoint | Cable Supports: Cables are adequately supported at all points (max 500mm intervals) and are neatly fixed with clips, saddles or ties as per C2111.5.
| checkpoint | Cable Supports: Cable ties are appropriated selected and sized e.g. black cable = black tie, white cable = white tie, fire resistant cable = stainless steel tie.
| checkpoint | Cable Supports: Single core cables forming part of a 3-phase system are rigidly held in trefoil formation by approved clamps as per C2111.5.
| checkpoint | Cable Supports: Cables passing through large draw pits have been supported on pit walls or with central supports to prevent sag as per C2115.3.
| checkpoint | Setting Out: All flush boxes are of the required type and rating for the partition/wall type and are secured with a minimum of 2 screws as per C2141.3.
| checkpoint | Setting Out: All flush boxes, electrical termination points and lighting points have been marked out as per the current Architectural drawings and sufficient blockings/dwangs have been provided by the Building Trade.
| checkpoint | First Fix: All subcircuit cabling is concealed within walls, ceilings or floor spaces as per C2102.6. Alternatively, cables are laid within continuous ducts as per C2115.3.
| checkpoint | First Fix: No subcircuit cable bunches exist and overheating has been considered as per C2102.6.
| checkpoint | First Fix: All bends and cables under tension have been reviewed and are within manufacturer's recommendations as per C2102.6 and C2115.3.
| checkpoint | First Fix: Cables are neatly arranged on trays or in trunking and no twists or crossovers exist. Cables are stacked no more than 6 high with 1 cable width spacing to the next bunch as per C2111.5.
| checkpoint | First Fix: All cables are protected where they pass through any openings, gaps, holes by ensuring the surrounding surfaces are smooth as per C2111.5.
| checkpoint | First Fix: ELV, LV and HV circuits are appropriately segregated as per C2111.5.
| checkpoint | First Fix: Any cable joints have been documented (as-built) and approved in writing by the Engineer as per C2111.5.
| checkpoint | First Fix: All cables where changing direction or containment method e.g. duct to draw pit or cable tray to catenary wire, or passing through a penetration have been installed with sufficient seismic slack and no sharp changes in direction exist.
| checkpoint | First Fix: All installed cables have been labelled with permanent marker multiple times at each end with neat handwriting as per Aotea agreed sequence of works.
| checkpoint | First Fix (Ducting): Cable lubricant used during cable installation as per C2115.3.3.
| checkpoint | First Fix (Ducting): Conduits/ducts passing through sub-floor void are limited to a maximum of one power cable or two lighting cables as per C2100.2.3
| checkpoint | First Fix (Ducting): Combined cabling installed via ducting system does not exceed 750mm² as per C2100.2.3.
| checkpoint | Sign-Off: All cables have been installed and inspected as per the project DB schedules and current construction drawings and pre-line inspections can proceed.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master Floor Box Installation 1 |  | Master Floor Box Installation 1 | dbf71589-681e-4f37-b0cc-ef6e92345ece
| checkpoint | Setting Out: Floor Box slab penetration have been coordinated and accurately marked out.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master Floor Penetrations Installation |  | Master Floor Penetrations Installation | 73e6657d-b153-4fb5-9f31-5705a1dcd677
| checkpoint | Setting Out: Floor penetrations have been coordinated and accurately marked out.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master HV Cable Inspection and Testing |  | Master HV Cable Inspection and Testing | c0390fc2-e154-442b-808d-c3e86e114c90
| checkpoint | Confirm all terminations are complete, including sheath earthing
| checkpoint | Confirm all cable supports are complete
| checkpoint | Ensure all cleating is complete
| checkpoint | Confirm all cables are numbered at transformer end
| checkpoint | Confirm all cables are numbered at circuit breaker end
| checkpoint | Resistance tests Y
| checkpoint | Resistance tests Y
| checkpoint | Resistance tests B
| checkpoint | Sheath IR test R
| checkpoint | Sheath IR test Y
| checkpoint | Sheath IR test B
| checkpoint | VLF Test R
| checkpoint | VLF Test Y
| checkpoint | VLF Test B
| checkpoint | Power factor test R
| checkpoint | Power factor test Y
| checkpoint | Power factor test B
| checkpoint | PI and IR tests R
| checkpoint | PI and IR tests Y
| checkpoint | PI and IR tests B
| checklist | Master HV Cable Installation |  | Master HV Cable Installation | ebc59a39-c79c-4c85-ada7-9a239c072b78
| checkpoint | Verify correct drawings and latest revision
| checkpoint | Check for any transit damage, no damage to cable prior to laying
| checkpoint | Correct size, type as shown on cable schedule
| checkpoint | Protect existing and new cables from physical damage during laying
| checkpoint | Segregation of cables as specified, neat & tidy installation, bending radius adhered to.
| checkpoint | Direct buried Cables: cable bedded on specified crusher dust
| checkpoint | Cables in Ducts: All debris removed from ducts prior to installation, neat & tidy installation.
| checkpoint | Test HV cable prior to terminating as per specification
| checkpoint | Cables correctly glanded, screens earthed.
| checkpoint | Cables numbered / identified correctly, tail lengths sufficient,
| checkpoint | Cable terminated per manufacturer specification, results input to test report
| checkpoint | Backfill as per spec
| checkpoint | Mark up "As built" drawings.
| checklist | Master HV Ducting Installation |  | Master HV Ducting Installation | 81bb83df-3ed3-403a-b5ab-0c73e05f2c84
| section | Details
| checkpoint | Preinstallation: All staff briefed on safety requirements and installation procedure
| checkpoint | Ducts: Verify that drawings are latest revision
| checkpoint | Ducts: Excavations complete
| checkpoint | Ducts: Inspect trench correct depth/profile clear of sharp obstructions etc
| checkpoint | Ducts: All ducts of the correct rating
| checkpoint | Ducts: All ducts laid flat or as required
| checkpoint | Ducts: All Duct joints face the same direction
| checkpoint | Ducts: All ducts bends are >/= minimum radius
| checkpoint | Ducts: All ducts >/= minimum required depth
| checkpoint | Ducts: All ducts sitting naturally IE, no strained joints
| checkpoint | Ducts: All ducts are sitting on a 50mm bed of crusher dust.
| checkpoint | Ducts: All installed ducts have end caps fitted
| checkpoint | Ducts: Back filled to correct depth for Mag Slab installation Compacted
| checkpoint | Ducts: Maglab installed covering entire duct route
| checkpoint | Ducts: Back filled to correct depth for Danger Tape installation Compacted
| checkpoint | Ducts: Dangertape installed covering entire duct route
| checkpoint | Ducts: Complete backfill and compact with appropriate material.
| checkpoint | Finalisation: Mark up "As built" drawings
| checklist | Master LV Cable Installation |  | Master LV Cable Installation | 1085c466-0c69-4f86-9b24-b04029745292
| checkpoint | Verify that drawings are latest revision and manufacturer's manuals
| checkpoint | Correct cable space (cores /pairs, csa, element or overall screen)
| checkpoint | Inspect cable routing, segregation & fixing details
| checkpoint | Inspect cable protective measures adequate (eg kick guards, protection from sharp edges)
| checkpoint | Inspect cable identification fixed at both ends is correct
| checkpoint | Remove JB/control box cover. Inspect gland assembly inner/outer seals
| checkpoint | Check cores tidy in termination chamber
| checkpoint | Inspect cable earth bonding, SWA clamping
| checkpoint | Insulation resistance check: Record on cable card
| checkpoint | Treatment of screens correct (NB: screens insulated from earth and electrically continuous throughout loop, except at Marshalling Cabinet where connected to instrument earth)
| checkpoint | Check core secure in terminal & pin crimp secure on core.
| checkpoint | Yellow line check continuity of each core against interconnect diagram point to point
| checkpoint | Fit JB/control box cover (including correct grease for Ex’d’ box)
| checkpoint | Install cable gland tape protection system as appropriate
| checklist | Master LV Ducting Installation |  | Master LV Ducting Installation | 8db2a3cb-9274-45e1-b4db-120e27809f98
| section | Details
| checkpoint | Hold Point: Trenching completed by others, requirements listed under C2115.2.
| checkpoint | Setting Out: Bedding material selected and installed as per AS/NZS 3000:2007 3.11.4.2.
| checkpoint | Setting Out: Clearance from other services maintained as per AS/NZS 3000:2007 3.9.8.4.
| checkpoint | Installation: Category of installation selected per specification and installed as per AS/NZS 3000:2007 3.11.3.
| checkpoint | Installation: Long radius sweeps or bends used for all chnages in direction (elbows not acceptable) as per C2115.3.3.
| checkpoint | Installation: Mechanical protection selected and installed in accordance with category of underground wiring system.
| checkpoint | Installation: Duct joints glued to prevent water ingress as per C2115.3.3.
| checkpoint | Installation: Ducts cleaned of rocks/debris as per C2115.3.3.
| checkpoint | Installation: Duct proved and draw wire installed as per C2115.3.3.
| checkpoint | Installation: Ducts provided with suitable sized end caps to prevent the ingress of soil as per C2115.3.3.
| checkpoint | Hold Point: Notice has been issued to BECA for inspection prior to back filling as per C2115.1.
| checkpoint | Hold Point: Backfilling completed by others, requirements listed under C2115.4.
| checkpoint | Installation: Identifcation of underground wiring provided as per AS/NZ 3000:2007 3.11.4.5.
| checkpoint | Installation: Duct penetrations to subfloor maintained as continuous as per C2100.2.3.
| checkpoint | Ducts cut flush with level 0 slab for passive fire treatment as per C2100.2.3.
| checkpoint | Sign-Off: Underground wiring system minimum depth of cover achieved as per AS/NZS 3000:2007 table 3.6.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master Panel/Junction Box Installation |  | Master Panel/Junction Box Installation | a2943548-657d-4a22-b69e-71a746ec8d57
| checkpoint | Check Panel location, obstructions and dimensions
| checkpoint | Door and cover are correctly fitted and open and close easily
| checkpoint | Install and secure Panel / JB
| checkpoint | Heater installed and functions correctly
| checkpoint | Door and other equipment is adequately earthed
| checkpoint | All equipment is clearly labelled and in accordance with drawings
| checkpoint | The installation and wiring in accordance with drawings
| checkpoint | Conductors are correctly clamped and identified with correct markers
| checkpoint | Cable does not impose strain on the terminals
| checkpoint | Cable terminated per manufacturer specification
| checkpoint | Complete COC as Required
| checkpoint | Mark up "As built" drawings.
| checklist | Master Power Transformer Commissioning Tests |  | Master Power Transformer Commissioning Tests | af351fa0-251d-410c-bb58-825a78a31bf0
| checkpoint | Livening and Soak checks off load
| checkpoint | Phasing checks
| checkpoint | Onload Temperature checks
| checkpoint | Onload Stability checks
| checklist | Master SCADA & Communications Testing |  | Master SCADA & Communications Testing | 5abda26f-2537-42f6-9f68-aee7351a545b
| checkpoint | Acceptance testing of RTAC RTU Relay completed
| checkpoint | Acceptance testing of HMI & Keyboard completed
| checkpoint | Spreadsheet prepared for RTAC config
| checkpoint | RTAC config developed from Spreadsheet
| checkpoint | RTAC config download and checked
| checkpoint | Network Switches installed, configured & operational
| checkpoint | Communication fibres & connections correct as per drawings
| checkpoint | All devices online with RTAC with acceptable error rate
| checkpoint | RTAC connection to BMS established
| checkpoint | All relay DNP points tested to RTAC
| checkpoint | Field inputs operated from devices correctly as per drawings
| checkpoint | Controls confirmed operational from RTAC
| checkpoint | All points checked from RTAC to HMI
| checkpoint | All controls checked, HMI to device
| checkpoint | All points checked from RTAC to BMS
| checkpoint | All controls checked, BMS to device
| checklist | Master Second Fix Installation |  | Master Second Fix Installation | 7e16fa37-0b9b-4cb7-bcee-1de9c2c89a1c
| checkpoint | General Lighting: All luminaires have been installed with required brackets and fixings as per C2100.2, or suspended as per C2102.7 and C2130.4.
| checkpoint | General Lighting: All luminaires have been installed with all necessary componants, control devices and accessories as per C2100.2.
| checkpoint | General Lighting: When installed within suspended ceilings, all luminaires have been installed with installation couplers as per C2100.2.
| checkpoint | General Lighting: When installed within Isolation Spaces, all luminaires have been sealed to prevent air leaks as per C2100.2.
| checkpoint | General Lighting: When installed within MRI rooms, all luminaire drivers have been located externally to the room as per C2100.2.
| checkpoint | General Lighting: No manufacturer's name or trade mark is visible on an installed internal luminaire as per C2130.2.
| checkpoint | General Lighting: When luminaires are recessed they are installed with appropriate hold down fixings that facilitate easy removal as per C2130.2.
| checkpoint | General Lighting: All luminaires are installed to manufacturer's specifications as per C2130.4.
| checkpoint | General Lighting: Terminations are suitably supported and are not carrying the weight of the cable as per C2111.5.
| checkpoint | General Lighting: Following final installation and practical completion, all luminaires have been cleaned as per C2130.4.
| checkpoint | Sign-Off: All luminaires been installed as per the current construction drawings and commissioning can proceed.
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checkpoint | Emergency Lighting: All emergency luminaires have been provided with a contrasting colour unique ID label as per AS/NZS 2293 2.5
| checkpoint | Emergency Lighting: All emergency luminaires have been installed in the correct orientation and the LED light is directed at the required area e.g. egress pathways, change in level
| checkpoint | Sign-Off: All emergency luminaires been installed as per the current construction drawings and commissioning can proceed.
| checkpoint | Sign-Off: Lighting: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checkpoint | LV Power: Socket outlets in patient areas are red coloured, or beige for cleaners or blue for UPS as per C2100.2.
| checkpoint | LV Power: Socket outlets in non-patient areas are white coloured as per subcontractor quote clarifications item 3.08, except 13 outlets in the Main Entrance.
| checkpoint | LV Power: Cabling to motors or mechanical plant has been terminated with slack/loops to allow for vibration and movement as per C2111.5.
| checkpoint | LV Power: Where wall voids are not present outlets have been installed on mounting blocks as per C2141.2.
| checkpoint | LV Power: Outlets are labelled as per AS/NZS 3003, to identify the RCD and with power available indication.
| checkpoint | LV Power: All cable terminations have been made using correctly sized crimp or compression lugs as per C2111.5. Alternatively, cable terminations have
| checkpoint | LV Power: Outlets have been installed clean and level.
| checkpoint | LV Power: Outlets have been provided with suitable labelling.
| checkpoint | Sign-Off: All outlets have been installed as per the current construction drawings and commissioning can proceed.
| checkpoint | Sign-Off: Lighting: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checkpoint | Earthing: Main equipotential earth bars have been installed 500mm AFFL with a 120mm² 1C connection and 20% spare space as per C2160.1
| checkpoint | Earthing: Earth bars have been installed in the MDF room and Aurora substation with a 70mm² connection as per C2160.1
| checkpoint | Earthing: Earthing connections have been installed to all communication racks and frames as per C2160.1
| checkpoint | Earthing: Earthing connections (EPJ) have been installed as per AS/NZS 3003 for both Body and Cardiac Protected Areas as per C2160.1
| checkpoint | Earthing: Supplementary earthing connections have been installed as per AS/NZS 3003 for all metallic equipment within both Body and Cardiac Protected Areas as per C2160.1
| checkpoint | Sign-Off: Lighting: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Master SEL387L Protection Relay Testing |  | Master SEL387L Protection Relay Testing | bc7e7d37-92e6-49c5-8695-bee2d3b44205
| checkpoint | Acceptance testing of SEL387L Relay completed
| checkpoint | SEL387L Relay settings applied
| checkpoint | Relay settings download and checked
| checkpoint | Secondary relay injection completed to confirm settings
| checkpoint | Confirmation Relay setting sheet faxed to AOTEA
| checkpoint | Field inputs operated from devices correctly as per drawings
| checkpoint | Output operate correct devices as per drawings
| checkpoint | DC Circuits Insulation Resistance
| checkpoint | CT insulation resistance
| checkpoint | CT Polarity checked correct
| checkpoint | CT primary injections completed
| checkpoint | CB Functional tests completed
| checkpoint | SCADA tests to SCH completed and checksheet filled in
| checkpoint | Local Alarms checked
| checklist | Master SEL735 Protection Relay Testing |  | Master SEL735 Protection Relay Testing | fd0ebe35-6257-483f-b089-1bf8edbc8d7a
| checkpoint | Acceptance testing of SEL735 Relay completed
| checkpoint | SEL735 Relay settings applied
| checkpoint | Relay settings download and checked
| checkpoint | Secondary relay injection completed to confirm settings
| checkpoint | Confirmation Relay setting sheet faxed to AOTEA
| checkpoint | Field inputs operated from devices correctly as per drawings
| checkpoint | Output operate correct devices as per drawings
| checkpoint | DC Circuits Insulation Resistance
| checkpoint | CT insulation resistance
| checkpoint | CT Polarity checked correct
| checkpoint | CT primary injections completed
| checkpoint | CB Functional tests completed
| checkpoint | SCADA tests to SCH completed and checksheet filled in
| checkpoint | Local Alarms checked
| checklist | Master SEL751 Protection Relay Testing |  | Master SEL751 Protection Relay Testing | 26a54601-ea52-466c-a3a5-db3266f945ce
| checkpoint | Acceptance testing of SEL751 Relay completed
| checkpoint | SEL751 Relay settings applied
| checkpoint | Relay settings download and checked
| checkpoint | Secondary relay injection completed to confirm settings
| checkpoint | Confirmation Relay setting sheet faxed to AOTEA
| checkpoint | Field inputs operated from devices correctly as per drawings
| checkpoint | Output operate correct devices as per drawings
| checkpoint | DC Circuits Insulation Resistance
| checkpoint | CT insulation resistance
| checkpoint | CT Polarity checked correct
| checkpoint | CT primary injections completed
| checkpoint | CB Functional tests completed
| checkpoint | BZ/CBF & ARC flash tests complete
| checkpoint | SCADA tests to SCH completed and checksheet filled in
| checkpoint | Local Alarms checked
| checklist | Master SEL2600 Protection Relay Testing |  | Master SEL2600 Protection Relay Testing | bb445514-bb1d-4fce-a490-2810250c45e5
| checkpoint | Acceptance testing of SEL2600 Relay completed
| checkpoint | Field inputs operated from devices correctly as per drawings
| checklist | Master Test Report |  | Master Test Report | b21c06b4-ce21-4fd0-9721-f7f7df9bf6b2
| checkpoint | Test Reort Completed
| checkpoint | CHECKED
| checkpoint | APPROVED
| checkpoint | Uploaded to CONQA
| checklist | Master Transformer Installation |  | Master Transformer Installation | 3d4902b6-dc94-465d-964c-865a89a52b07
| checkpoint | All staff briefed on safety requirements and installation procedure
| checkpoint | Confirm floor loading specifications satisfactory for installation
| checkpoint | Verify that drawings are latest revision and manufacturer's manuals available on site
| checkpoint | No damage to Transformer, foundation matches transformer fixing arrangements, no damage to bushings, and paint work to specification.
| checkpoint | Impact recorder removed and returned.
| checkpoint | Check location, orientation, level and alignment and vibration pads installed.
| checkpoint | Record stud embedment depth
| checkpoint | Transformer Hold Down completed as per: CAL002Transformer Hold Down Design V1.mcdx
| checkpoint | Connection to earth grid complete. Two separate paths to earth.
| checkpoint | Installation of HV & LV bushings as per manufacturer's specification.
| checkpoint | Primary connections made as per manufacturer's specification, correct grease used, secondary connection made correctly, tight and protected.
| checkpoint | Bus flexibles have specified phase-phase and phase-earth clearances, temporary earth points installed.
| checkpoint | Clean insulator surface, no porcelain damage
| checkpoint | Clean the transformer windings from inside and outside, by air blower
| checkpoint | Serial numbers are in correct order and recorded, system numbers and phases correctly identified
| checkpoint | All bolts tightened as specified check transformer manufacturer's checklist.
| checkpoint | Cable installation and termination checklist completed,
| checkpoint | All auxiliary wiring tight in terminals and in accordance with drawings. Terminal crimp lugs and bootlace ferrules used. Trunking and termination covers in place.
| checkpoint | Calibrate temperature sensors. Test alarm, fan start (where applicable) and trip temperature operation.
| checkpoint | Drawings are 'as built'
| checklist | Master Transformer Testing |  | Master Transformer Testing | 06cb8f66-48ab-4ee0-84d5-bb68d9a8c4fe
| checkpoint | Test Report for Power Transformers
| checkpoint | Bushing Data
| checkpoint | Winding DC Resistance
| checkpoint | Ratio / Polarity
| checkpoint | Impedance
| checkpoint | Transport Test ( Excitation )
| checkpoint | Phasing / Vector checks
| checkpoint | Insulation Resistance/Polarisation Tests
| checkpoint | Core and end frame Insulation Resistance
| checkpoint | Winding Power Factor Tests
| checkpoint | Bushing Power Factor Tests
| checkpoint | AVR Acceptance Tests
| checkpoint | Ancillary Equipment Functionally checked
| checkpoint | Ancillary Equipment Insulation Resistance
| checkpoint | Cooling fan control and alarm checked
| checkpoint | Differential Stability tests completed
| checkpoint | REF Stability tests completed
| checkpoint | NER Resistance Tests
| checkpoint | Test results compare favourably with manufacturer's results and pre-installation acceptance tests
| checklist | Master Wricon Installation |  | Master Wricon Installation | 40e7557a-9152-4548-a009-10c3e61af020
| checkpoint | Setting Out: Wricon slab penetrations have been coordinated and accurately marked out.
| checkpoint | Installation: Wricon has been welded securely to reo by a third party qualified Welder
| checkpoint | Sign-Off: All changes to the current construction drawings have been documented and issued to James Eymael for action.
| checkpoint | Sign-Off: Any comments below.
| checklist | Seismic Bracketing |  | Seismic Bracketing | 4393888f-8710-4f2e-9f12-c28f76b6d24d
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
| checkpoint | Location of Bracket checked on shop drawings
| checkpoint | Correct bracket type selected
| checkpoint | Correct Anchor selected and checked
| checkpoint | Anchor Hole Size and Depth checked
| checkpoint | Correct torque set for anchor
| checkpoint | Final Photo of bracket