## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
High Voltage (Transformers)
| Scope |  |  | High Voltage | Transformers
Rows
|  | Transformers | dynamic | High Voltage | Transformers
Columns
|  | All staff briefed on safety requirements & installation procedure |  | All staff briefed on safety requirements and installation procedure
|  | Confirm floor loading specs. satisfactory for installation |  | Confirm floor loading specifications satisfactory for installation
|  | Verify that drawings are latest revision & manufacturer's manuals available on site |  | Verify that drawings are latest revision and manufacturer's manuals available on site
|  | No damage to Transformer, foundation matches transformer fixing arrangements, no damage to bushings, & paint work to spec. |  | No damage to Transformer, foundation matches transformer fixing arrangements, no damage to bushings, and paint work to specification.
|  | Impact recorder removed & returned |  | Impact recorder removed and returned.
|  | Check location, orientation, level & alignment & vibration pads installed |  | Check location, orientation, level and alignment and vibration pads installed.
|  | Record stud embedment depth |  | Record stud embedment depth
|  | Transformer Hold Down completed as per: CAL002Transformer Hold Down Design V1.mcdx |  | Transformer Hold Down completed as per: CAL002Transformer Hold Down Design V1.mcdx
|  | Connection to earth grid complete/Two separate paths to earth |  | Connection to earth grid complete. Two separate paths to earth.
|  | Installation of HV & LV bushings as per manufacturer's spec. |  | Installation of HV & LV bushings as per manufacturer's specification.
|  | Primary connections made as per manufacturer's spec. |  | Primary connections made as per manufacturer's specification, correct grease used, secondary connection made correctly, tight and protected.
|  | Bus flexibles have specified phase-phase & phase-earth clearances, temporary earth points installed |  | Bus flexibles have specified phase-phase and phase-earth clearances, temporary earth points installed.
|  | Clean insulator surface, no porcelain damage |  | Clean insulator surface, no porcelain damage
|  | Clean the transformer windings from inside & outside, by air blower |  | Clean the transformer windings from inside and outside, by air blower
|  | Serial numbers are in correct order & recorded, system numbers & phases correctly identified |  | Serial numbers are in correct order and recorded, system numbers and phases correctly identified
|  | All bolts tightened as specified check transformer manufacturer's checklist |  | All bolts tightened as specified check transformer manufacturer's checklist.
|  | Cable installation & termination checklist completed |  | Cable installation and termination checklist completed,
|  | All auxiliary wiring tight in terminals & in accordance with drawings |  | All auxiliary wiring tight in terminals and in accordance with drawings. Terminal crimp lugs and bootlace ferrules used. Trunking and termination covers in place.
|  | Calibrate temperature sensors |  | Calibrate temperature sensors. Test alarm, fan start (where applicable) and trip temperature operation.
|  | Drawings are 'as built' |  | Drawings are 'as built'
|  | Ladder rack approved for use in relay/control room |  | Ladder rack approved for use in relay or control room
|  | Cable ladder supported by fixing to structural members of building |  | Cable ladder supported by fixing to structural members of building
|  | No cable ladder supported by relay or control panels |  | No cable ladder supported by relay or control panels
|  | Cable ladder earthed directly to main station earth grid at an interval of not more than 5m |  | Cable ladder earthed directly to the main station earth grid at an interval of not more than 5m
|  | No cable ladder earthed via panel earthing |  | No cable ladder earthed via panel earthing
|  | Joints bonded to earthed |  | Joints bonded to earthed
|  | Cut ends of ladder & tray correctly treated |  | Cut ends of ladder and tray correctly treated
|  | Fit labels on ladder/tray if required by spec. |  | Fit labels on ladder/tray if required by Specification
|  | Fit ladder covers if required by spec. |  | Fit ladder covers if required by specification
|  | Rodent proofing - All entry Points to raceway rodent/fire proof |  | Rodent proofing - All entry Points to raceway rodent/fire proof
|  | Mark up "As built" drawings |  | Mark up "As built" drawings.
|  | Verify that drawings are latest revision & manufacturer's manuals |  | Verify that drawings are latest revision and manufacturer's manuals
|  | Correct cable space |  | Correct cable space (cores /pairs, csa, element or overall screen)
|  | Inspect cable routing, segregation & fixing details |  | Inspect cable routing, segregation & fixing details
|  | Inspect cable protective measures adequate |  | Inspect cable protective measures adequate (eg kick guards, protection from sharp edges)
|  | Inspect cable identification fixed at both ends is correct |  | Inspect cable identification fixed at both ends is correct
|  | Remove JB/control box cover. Inspect gland assembly inner/outer seals |  | Remove JB/control box cover. Inspect gland assembly inner/outer seals
|  | Check cores tidy in termination chamber |  | Check cores tidy in termination chamber
|  | Inspect cable earth bonding, SWA clamping |  | Inspect cable earth bonding, SWA clamping
|  | Insulation resistance check: Record on cable card |  | Insulation resistance check: Record on cable card
|  | Treatment of screens correct |  | Treatment of screens correct (NB: screens insulated from earth and electrically continuous throughout loop, except at Marshalling Cabinet where connected to instrument earth)
|  | Check core secure in terminal & pin crimp secure on core. |  | Check core secure in terminal & pin crimp secure on core.
|  | Yellow line check continuity of each core against interconnect diagram point to point |  | Yellow line check continuity of each core against interconnect diagram point to point
|  | Fit JB/control box cover |  | Fit JB/control box cover (including correct grease for Ex’d’ box)
|  | Install cable gland tape protection system as appropriate |  | Install cable gland tape protection system as appropriate
|  | Verify that drawings are latest revision & manufacturer's manuals available on site |  | Verify that drawings are latest revision and manufacturer's manuals available on site.
|  | Correct type & rating of Earthing Conductor |  | Correct type and rating of Earthing Conductor
|  | Earth bus bars installed standoffs correct size |  | Earth bus bars installed standoffs correct size
|  | Mark out Earthing layout per drawing |  | Mark out Earthing layout per drawing
|  | Tray etc installed & bonded |  | Tray etc installed and bonded
|  | Install earthing conductor attached to tray as applicable |  | Install earthing conductor attached to tray as applicable
|  | All equipment connected to earth grid/bus bar |  | All equipment connected to earth grid/bus bar
|  | Check each piece of equipment is earthed by connection to the nearest earth bar |  | Check each piece of equipment is earthed by connection to the nearest earth bar
|  | Check continuity of all earthing cables. |  | Check continuity of all earthing cables.
|  | Resistivity of earth |  | Resistivity of earth (using fall of potential)
|  | Continuity of new earths |  | Continuity of new earths
|  | Resistance to Earth grid |  | Resistance to Earth grid ( point to point tests )
|  | Test Report for Power Transformers |  | Test Report for Power Transformers
|  | Bushing Data |  | Bushing Data
|  | Winding DC Resistance |  | Winding DC Resistance
|  | Ratio/Polarity |  | Ratio / Polarity
|  | Impedance |  | Impedance
|  | Transport Test (Excitation) |  | Transport Test ( Excitation )
|  | Phasing/Vector checks |  | Phasing / Vector checks
|  | Insulation Resistance/Polarisation Tests |  | Insulation Resistance/Polarisation Tests
|  | Core & end frame Insulation Resistance |  | Core and end frame Insulation Resistance
|  | Winding Power Factor Tests |  | Winding Power Factor Tests
|  | Bushing Power Factor Tests |  | Bushing Power Factor Tests
|  | AVR Acceptance Tests |  | AVR Acceptance Tests
|  | Ancillary Equipment Functionally checked |  | Ancillary Equipment Functionally checked
|  | Ancillary Equipment Insulation Resistance |  | Ancillary Equipment Insulation Resistance
|  | Cooling fan control & alarm checked |  | Cooling fan control and alarm checked
|  | Differential Stability tests completed |  | Differential Stability tests completed
|  | REF Stability tests completed |  | REF Stability tests completed
|  | NER Resistance Tests |  | NER Resistance Tests
|  | Test results compare favourably with manufacturer's results & pre-installation acceptance tests |  | Test results compare favourably with manufacturer's results and pre-installation acceptance tests
|  | Livening & Soak checks off load |  | Livening and Soak checks off load
|  | Phasing checks |  | Phasing checks
|  | Onload Temperature checks |  | Onload Temperature checks
|  | Onload Stability checks |  | Onload Stability checks
High Voltage (HV Cables)
| Scope |  |  | High Voltage | HV Cables
Rows
|  | HV Cables | dynamic | High Voltage | HV Cables
Columns
|  | Verify correct drawings & latest revision |  | Verify correct drawings and latest revision
|  | Check for any transit damage, no damage to cable prior to laying |  | Check for any transit damage, no damage to cable prior to laying
|  | Correct size, type as shown on cable schedule |  | Correct size, type as shown on cable schedule
|  | Protect existing & new cables from physical damage during laying |  | Protect existing and new cables from physical damage during laying
|  | Segregation of cables as specified, neat & tidy installation, bending radius adhered to |  | Segregation of cables as specified, neat & tidy installation, bending radius adhered to.
|  | Direct buried Cables: cable bedded on specified crusher dust |  | Direct buried Cables: cable bedded on specified crusher dust
|  | Cables in Ducts: All debris removed from ducts prior to installation, neat & tidy installation |  | Cables in Ducts: All debris removed from ducts prior to installation, neat & tidy installation.
|  | Test HV cable prior to terminating as per spec |  | Test HV cable prior to terminating as per specification
|  | Cables correctly glanded, screens earthed. |  | Cables correctly glanded, screens earthed.
|  | Cables numbered/identified correctly, tail lengths sufficient, |  | Cables numbered / identified correctly, tail lengths sufficient,
|  | Cable terminated per manufacturer spec, results input to test report |  | Cable terminated per manufacturer specification, results input to test report
|  | Backfill as per spec |  | Backfill as per spec
|  | Mark up "As built" drawings. |  | Mark up "As built" drawings.
|  | Confirm all terminations are complete, including sheath earthing |  | Confirm all terminations are complete, including sheath earthing
|  | Confirm all cable supports are complete |  | Confirm all cable supports are complete
|  | Ensure all cleating is complete |  | Ensure all cleating is complete
|  | Confirm all cables are numbered at transformer end |  | Confirm all cables are numbered at transformer end
|  | Confirm all cables are numbered at circuit breaker end |  | Confirm all cables are numbered at circuit breaker end
|  | Resistance tests Y |  | Resistance tests Y
|  | Resistance tests Y |  | Resistance tests Y
|  | Resistance tests B |  | Resistance tests B
|  | Sheath IR test R |  | Sheath IR test R
|  | Sheath IR test Y |  | Sheath IR test Y
|  | Sheath IR test B |  | Sheath IR test B
|  | VLF Test R |  | VLF Test R
|  | VLF Test Y |  | VLF Test Y
|  | VLF Test B |  | VLF Test B
|  | Power factor test R |  | Power factor test R
|  | Power factor test Y |  | Power factor test Y
|  | Power factor test B |  | Power factor test B
|  | PI & IR tests R |  | PI and IR tests R
|  | PI & IR tests Y |  | PI and IR tests Y
|  | PI & IR tests B |  | PI and IR tests B