## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
High Voltage (Transformers)
| Scope |  |  | High Voltage | Transformers
Rows
|  | Transformers - Transformer: TX-112-4-1A | dynamic | High Voltage | Transformers | Transformer: TX-112-4-1A
|  | Transformers - Transformer: TX-112-4-1B | dynamic | High Voltage | Transformers | Transformer: TX-112-4-1B
Columns
|  | All staff briefed on safety requirements & installation procedure |  | All staff briefed on safety requirements and installation procedure
|  | Confirm floor loading specs. satisfactory for installation |  | Confirm floor loading specifications satisfactory for installation
|  | Verify that drawings are latest revision & manufacturer's manuals available on site |  | Verify that drawings are latest revision and manufacturer's manuals available on site
|  | No damage to Transformer, foundation matches transformer fixing arrangements, no damage to bushings, & paint work to specification. |  | No damage to Transformer, foundation matches transformer fixing arrangements, no damage to bushings, and paint work to specification.
|  | Impact recorder removed & returned. |  | Impact recorder removed and returned.
|  | Check location, orientation, level & alignment & vibration pads installed. |  | Check location, orientation, level and alignment and vibration pads installed.
|  | Record stud embedment depth |  | Record stud embedment depth
|  | Transformer Hold Down completed as per: CAL002Transformer Hold Down Design V1.mcdx |  | Transformer Hold Down completed as per: CAL002Transformer Hold Down Design V1.mcdx
|  | Connection to earth grid complete. Two separate paths to earth. |  | Connection to earth grid complete. Two separate paths to earth.
|  | Installation of HV & LV bushings as per manufacturer's specification. |  | Installation of HV & LV bushings as per manufacturer's specification.
|  | Primary connections made as per manufacturer's specification, correct grease used, secondary connection made correctly, tight & protected. |  | Primary connections made as per manufacturer's specification, correct grease used, secondary connection made correctly, tight and protected.
|  | Bus flexibles have specified phase-phase & phase-earth clearances, temporary earth points installed. |  | Bus flexibles have specified phase-phase and phase-earth clearances, temporary earth points installed.
|  | Clean insulator surface, no porcelain damage |  | Clean insulator surface, no porcelain damage
|  | Clean the transformer windings from inside & outside, by air blower |  | Clean the transformer windings from inside and outside, by air blower
|  | Serial numbers are in correct order & recorded, system numbers & phases correctly identified |  | Serial numbers are in correct order and recorded, system numbers and phases correctly identified
|  | All bolts tightened as specified check transformer manufacturer's checklist. |  | All bolts tightened as specified check transformer manufacturer's checklist.
|  | Cable installation & termination checklist completed, |  | Cable installation and termination checklist completed,
|  | All auxiliary wiring tight in terminals & in accordance with drawings. Terminal crimp lugs & bootlace ferrules used. Trunking & termination covers in place. |  | All auxiliary wiring tight in terminals and in accordance with drawings. Terminal crimp lugs and bootlace ferrules used. Trunking and termination covers in place.
|  | Calibrate temperature sensors. Test alarm, fan start (where applicable) & trip temperature operation. |  | Calibrate temperature sensors. Test alarm, fan start (where applicable) and trip temperature operation.
|  | Drawings are 'as built' |  | Drawings are 'as built'
|  | Ladder rack approved for use in relay or control room |  | Ladder rack approved for use in relay or control room
|  | Cable ladder supported by fixing to structural members of building |  | Cable ladder supported by fixing to structural members of building
|  | No cable ladder supported by relay or control panels |  | No cable ladder supported by relay or control panels
|  | Cable ladder earthed directly to the main station earth grid at an interval of not more than 5m |  | Cable ladder earthed directly to the main station earth grid at an interval of not more than 5m
|  | No cable ladder earthed via panel earthing |  | No cable ladder earthed via panel earthing
|  | Joints bonded to earthed |  | Joints bonded to earthed
|  | Cut ends of ladder & tray correctly treated |  | Cut ends of ladder and tray correctly treated
|  | Fit labels on ladder/tray if required by Specification |  | Fit labels on ladder/tray if required by Specification
|  | Fit ladder covers if required by specification |  | Fit ladder covers if required by specification
|  | Rodent proofing - All entry Points to raceway rodent/fire proof |  | Rodent proofing - All entry Points to raceway rodent/fire proof
|  | Mark up "As built" drawings. |  | Mark up "As built" drawings.
|  | Verify that drawings are latest revision & manufacturer's manuals |  | Verify that drawings are latest revision and manufacturer's manuals
|  | Correct cable space (cores /pairs, csa, element or overall screen) |  | Correct cable space (cores /pairs, csa, element or overall screen)
|  | Inspect cable routing, segregation & fixing details |  | Inspect cable routing, segregation & fixing details
|  | Inspect cable protective measures adequate (eg kick guards, protection from sharp edges) |  | Inspect cable protective measures adequate (eg kick guards, protection from sharp edges)
|  | Inspect cable identification fixed at both ends is correct |  | Inspect cable identification fixed at both ends is correct
|  | Remove JB/control box cover. Inspect gland assembly inner/outer seals |  | Remove JB/control box cover. Inspect gland assembly inner/outer seals
|  | Check cores tidy in termination chamber |  | Check cores tidy in termination chamber
|  | Inspect cable earth bonding, SWA clamping |  | Inspect cable earth bonding, SWA clamping
|  | Insulation resistance check: Record on cable card |  | Insulation resistance check: Record on cable card
|  | Treatment of screens correct (NB: screens insulated from earth & electrically continuous throughout loop, except at Marshalling Cabinet where connected to instrument earth) |  | Treatment of screens correct (NB: screens insulated from earth and electrically continuous throughout loop, except at Marshalling Cabinet where connected to instrument earth)
|  | Check core secure in terminal & pin crimp secure on core. |  | Check core secure in terminal & pin crimp secure on core.
|  | Yellow line check continuity of each core against interconnect diagram point to point |  | Yellow line check continuity of each core against interconnect diagram point to point
|  | Fit JB/control box cover (including correct grease for Ex’d’ box) |  | Fit JB/control box cover (including correct grease for Ex’d’ box)
|  | Install cable gland tape protection system as appropriate |  | Install cable gland tape protection system as appropriate
|  | Verify that drawings are latest revision & manufacturer's manuals available on site. |  | Verify that drawings are latest revision and manufacturer's manuals available on site.
|  | Correct type & rating of Earthing Conductor |  | Correct type and rating of Earthing Conductor
|  | Earth bus bars installed standoffs correct size |  | Earth bus bars installed standoffs correct size
|  | Mark out Earthing layout per drawing |  | Mark out Earthing layout per drawing
|  | Tray etc installed & bonded |  | Tray etc installed and bonded
|  | Install earthing conductor attached to tray as applicable |  | Install earthing conductor attached to tray as applicable
|  | All equipment connected to earth grid/bus bar |  | All equipment connected to earth grid/bus bar
|  | Check each piece of equipment is earthed by connection to the nearest earth bar |  | Check each piece of equipment is earthed by connection to the nearest earth bar
|  | Check continuity of all earthing cables. |  | Check continuity of all earthing cables.
|  | Resistivity of earth (using fall of potential) |  | Resistivity of earth (using fall of potential)
|  | Continuity of new earths |  | Continuity of new earths
|  | Resistance to Earth grid (point to point tests) |  | Resistance to Earth grid ( point to point tests )
|  | Test Report for Power Transformers |  | Test Report for Power Transformers
|  | Bushing Data |  | Bushing Data
|  | Winding DC Resistance |  | Winding DC Resistance
|  | Ratio/Polarity |  | Ratio / Polarity
|  | Impedance |  | Impedance
|  | Transport Test (Excitation) |  | Transport Test ( Excitation )
|  | Phasing/Vector checks |  | Phasing / Vector checks
|  | Insulation Resistance/Polarisation Tests |  | Insulation Resistance/Polarisation Tests
|  | Core & end frame Insulation Resistance |  | Core and end frame Insulation Resistance
|  | Winding Power Factor Tests |  | Winding Power Factor Tests
|  | Bushing Power Factor Tests |  | Bushing Power Factor Tests
|  | AVR Acceptance Tests |  | AVR Acceptance Tests
|  | Ancillary Equipment Functionally checked |  | Ancillary Equipment Functionally checked
|  | Ancillary Equipment Insulation Resistance |  | Ancillary Equipment Insulation Resistance
|  | Cooling fan control & alarm checked |  | Cooling fan control and alarm checked
|  | Differential Stability tests completed |  | Differential Stability tests completed
|  | REF Stability tests completed |  | REF Stability tests completed
|  | NER Resistance Tests |  | NER Resistance Tests
|  | Test results compare favourably with manufacturer's results & pre-installation acceptance tests |  | Test results compare favourably with manufacturer's results and pre-installation acceptance tests
|  | Livening & Soak checks off load |  | Livening and Soak checks off load
|  | Phasing checks |  | Phasing checks
|  | Onload Temperature checks |  | Onload Temperature checks
|  | Onload Stability checks |  | Onload Stability checks
High Voltage (HV Cables)
| Scope |  |  | High Voltage | HV Cables
Rows
|  | HV Cables - CHV/4-MSB1/4-TX.1A | dynamic | High Voltage | HV Cables | CHV/4-MSB1/4-TX.1A
|  | HV Cables - CHV/4-MSB2/4-TX.1B | dynamic | High Voltage | HV Cables | CHV/4-MSB2/4-TX.1B
Columns
|  | Verify correct drawings & latest revision |  | Verify correct drawings and latest revision
|  | Check for any transit damage, no damage to cable prior to laying |  | Check for any transit damage, no damage to cable prior to laying
|  | Correct size, type as shown on cable schedule |  | Correct size, type as shown on cable schedule
|  | Protect existing & new cables from physical damage during laying |  | Protect existing and new cables from physical damage during laying
|  | Segregation of cables as specified, neat & tidy installation, bending radius adhered to |  | Segregation of cables as specified, neat & tidy installation, bending radius adhered to.
|  | Direct buried Cables: cable bedded on specified crusher dust |  | Direct buried Cables: cable bedded on specified crusher dust
|  | Cables in Ducts: All debris removed from ducts prior to installation, neat & tidy installation |  | Cables in Ducts: All debris removed from ducts prior to installation, neat & tidy installation.
|  | Test HV cable prior to terminating as per spec |  | Test HV cable prior to terminating as per specification
|  | Cables correctly glanded, screens earthed. |  | Cables correctly glanded, screens earthed.
|  | Cables numbered/identified correctly, tail lengths sufficient, |  | Cables numbered / identified correctly, tail lengths sufficient,
|  | Cable terminated per manufacturer spec, results input to test report |  | Cable terminated per manufacturer specification, results input to test report
|  | Backfill as per spec |  | Backfill as per spec
|  | Mark up "As built" drawings. |  | Mark up "As built" drawings.
|  | Confirm all terminations are complete, including sheath earthing |  | Confirm all terminations are complete, including sheath earthing
|  | Confirm all cable supports are complete |  | Confirm all cable supports are complete
|  | Ensure all cleating is complete |  | Ensure all cleating is complete
|  | Confirm all cables are numbered at transformer end |  | Confirm all cables are numbered at transformer end
|  | Confirm all cables are numbered at circuit breaker end |  | Confirm all cables are numbered at circuit breaker end
|  | Resistance tests Y |  | Resistance tests Y
|  | Resistance tests Y |  | Resistance tests Y
|  | Resistance tests B |  | Resistance tests B
|  | Sheath IR test R |  | Sheath IR test R
|  | Sheath IR test Y |  | Sheath IR test Y
|  | Sheath IR test B |  | Sheath IR test B
|  | VLF Test R |  | VLF Test R
|  | VLF Test Y |  | VLF Test Y
|  | VLF Test B |  | VLF Test B
|  | Power factor test R |  | Power factor test R
|  | Power factor test Y |  | Power factor test Y
|  | Power factor test B |  | Power factor test B
|  | PI & IR tests R |  | PI and IR tests R
|  | PI & IR tests Y |  | PI and IR tests Y
|  | PI & IR tests B |  | PI and IR tests B
High Voltage (11kV Switchboard / 11kV Switch Room)
| Scope |  |  | High Voltage
Rows
|  | 11kV Switchboard - MSB/HV-112-0-1/2 Installation | dynamic | High Voltage | 11kV Switchboard | MSB/HV-112-0-1/2 Installation
|  | 11kV Switchboard - CB112-1 | dynamic | High Voltage | 11kV Switchboard | CB112-1
|  | 11kV Switchboard - CB112-2 | dynamic | High Voltage | 11kV Switchboard | CB112-2
|  | 11kV Switchboard - CB112-3 | dynamic | High Voltage | 11kV Switchboard | CB112-3
|  | 11kV Switchboard - CB112-4 | dynamic | High Voltage | 11kV Switchboard | CB112-4
|  | 11kV Switchboard - CB112-5 | dynamic | High Voltage | 11kV Switchboard | CB112-5
|  | 11kV Switchboard - CB112-6 | dynamic | High Voltage | 11kV Switchboard | CB112-6
|  | 11kV Switchboard - CB112-7 | dynamic | High Voltage | 11kV Switchboard | CB112-7
|  | 11kV Switchboard - CB112-8 | dynamic | High Voltage | 11kV Switchboard | CB112-8
|  | 11kV Switchboard - CB112-9 | dynamic | High Voltage | 11kV Switchboard | CB112-9
|  | 11kV Switch Room - Room Fit Out | dynamic | High Voltage | 11kV Switch Room | Room Fit Out
|  | 11kV Switch Room - DC | dynamic | High Voltage | 11kV Switch Room | DC
|  | 11kV Switch Room - Comms/SCADA | dynamic | High Voltage | 11kV Switch Room | Comms/SCADA
Columns
|  | Acceptance testing of HMI & Keyboard completed |  | Acceptance testing of HMI & Keyboard completed
|  | Acceptance testing of RTAC RTU Relay completed |  | Acceptance testing of RTAC RTU Relay completed
|  | Acceptance testing of SEL2600 Relay completed |  | Acceptance testing of SEL2600 Relay completed
|  | Acceptance testing of SEL387L Relay completed |  | Acceptance testing of SEL387L Relay completed
|  | Acceptance testing of SEL735 Relay completed |  | Acceptance testing of SEL735 Relay completed
|  | Acceptance testing of SEL751 Relay completed |  | Acceptance testing of SEL751 Relay completed
|  | Alarms & Indications correct |  | Alarms and Indications correct
|  | All bolts tightened as specified |  | All bolts tightened as specified
|  | All controls checked, BMS to device |  | All controls checked, BMS to device
|  | All controls checked, HMI to device |  | All controls checked, HMI to device
|  | All devices online with RTAC with acceptable error rate |  | All devices online with RTAC with acceptable error rate
|  | All equipment connected to earth grid/bus bar |  | All equipment connected to earth grid/bus bar
|  | All equipment is clearly labelled & in accordance with drawings |  | All equipment is clearly labelled and in accordance with drawings
|  | All points checked from RTAC to BMS |  | All points checked from RTAC to BMS
|  | All points checked from RTAC to HMI |  | All points checked from RTAC to HMI
|  | All poles in same position before first operation |  | All poles in same position before first operation
|  | All relay DNP points tested to RTAC |  | All relay DNP points tested to RTAC
|  | All staff briefed on safety requirements & installation procedure |  | All staff briefed on safety requirements and installation procedure
|  | Analyse results according to "Biddle" instruction manual |  | Analyse results according to "Biddle" instruction manual. Any individual battery with an AC OHM reading outside the tolerance requires particular notification and further investigation. +/- 20% Tolerance allowed.
|  | Assemble equipment to manufacturers drawings & instructions |  | Assemble equipment to manufacturers drawings and instructions
|  | Assembly of stand carried out to manufacturer specs. |  | Assembly of stand carried out to manufacturer specifications.
|  | Batteries mounted in stand with orientation & polarity markings correct |  | Batteries mounted in stand with orientation and polarity markings correct.
|  | Battery Charger Acceptance Tested |  | Battery Charger Acceptance Tested
|  | Battery impedance test to determine the gradual deterioration of batteries by comparing one to others in bank |  | Battery impedance test is to determine the gradual deterioration of batteries by comparing one to others in the bank. Note new battery profile is required on acceptance of bank.
|  | Battery Impedance/ Discharge Tests completed |  | Battery Impedance/ Discharge Tests completed
|  | Battery stand bolted to the floor & earthed correctly |  | Battery stand bolted to the floor and earthed correctly.
|  | Battery stand equipment located in correct position/All parts for assembly complete. |  | Battery stand equipment located in correct position. All parts for assembly complete.
|  | Burden & Loading Resistor Checks |  | Burden and Loading Resistor Checks
|  | Bus Work Resistance Test |  | Bus Work Resistance Test
|  | Busbar DC Resistance checked (Ductor) |  | Busbar DC Resistance checked (Ductor)
|  | BZ/CBF & ARC flash tests complete |  | BZ/CBF & ARC flash tests complete
|  | Cable does not impose strain on the terminals |  | Cable does not impose strain on the terminals
|  | Cable installation & termination completed |  | Cable installation and termination completed
|  | Cable ladder earthed directly to the main station earth grid at an interval of not more than 5m |  | Cable ladder earthed directly to the main station earth grid at an interval of not more than 5m
|  | Cable ladder supported by fixing to structural members of building |  | Cable ladder supported by fixing to structural members of building
|  | Cable terminated per manufacturer specification |  | Cable terminated per manufacturer specification
|  | Cabling Terminated to Circuit Breaker Junction Boxes & JB's cleaned |  | Cabling Terminated to Circuit Breaker Junction Boxes and JB's cleaned
|  | CB Functional tests completed |  | CB Functional tests completed
|  | CB Timing |  | CB Timing
|  | Check continuity of all earthing cables |  | Check continuity of all earthing cables.
|  | Check core secure in terminal & pin crimp secure on core |  | Check core secure in terminal & pin crimp secure on core.
|  | Check cores tidy in termination chamber |  | Check cores tidy in termination chamber
|  | Check each piece of equipment is earthed by connection to the nearest earth bar |  | Check each piece of equipment is earthed by connection to the nearest earth bar
|  | Check items complete & for transit damage |  | Check items complete and for transit damage
|  | Check Panel location, obstructions & dimensions |  | Check Panel location, obstructions and dimensions
|  | Communication fibres & connections correct as per drawings |  | Communication fibres & connections correct as per drawings
|  | Complete COC as Required |  | Complete COC as Required
|  | Conductors are correctly clamped & identified with correct markers |  | Conductors are correctly clamped and identified with correct markers
|  | Confirm system Numbering "AS BUILD" SLD as required |  | Confirm system Numbering "AS BUILD" SLD as required
|  | Confirmation Relay setting sheet faxed to AOTEA |  | Confirmation Relay setting sheet faxed to AOTEA
|  | Connect equipment ancillaries |  | Connect equipment ancillaries
|  | Connected to Earth Grid as per drawings |  | Connected to Earth Grid as per drawings
|  | Continuity of new earths |  | Continuity of new earths
|  | Control & Alarm Pressure Switch Test |  | Control and Alarm Pressure Switch Test
|  | Control Equipment Insulation Resistance |  | Control Equipment Insulation Resistance
|  | Controls confirmed operational from RTAC |  | Controls confirmed operational from RTAC
|  | Correct cable space (cores/pairs, csa, element or overall screen) |  | Correct cable space (cores /pairs, csa, element or overall screen)
|  | Correct links used to connect up batteries used. |  | Correct links used to connect up batteries used.
|  | Correct terminal crimp lugs used |  | Correct terminal crimp lugs used
|  | Correct type & rating of Earthing Conductor |  | Correct type and rating of Earthing Conductor
|  | CT Burden Tests |  | CT Burden Tests
|  | CT insulation resistance |  | CT insulation resistance
|  | CT Polarity checked correct |  | CT Polarity checked correct
|  | CT primary injections completed |  | CT primary injections completed
|  | Cut ends of ladder & tray correctly treated |  | Cut ends of ladder and tray correctly treated
|  | DC Circuits Insulation Resistance |  | DC Circuits Insulation Resistance
|  | Door & cover are correctly fitted & open & close easily |  | Door and cover are correctly fitted and open and close easily
|  | Door & other equipment is adequately earthed |  | Door and other equipment is adequately earthed
|  | Drawings are 'as built' |  | Drawings are 'as built'
|  | Earth bus bars installed standoffs correct size |  | Earth bus bars installed standoffs correct size
|  | Earthing Resistance Test |  | Earthing Resistance Test
|  | Ensure all tests completed & result sheets filled out |  | Ensure all tests completed and result sheets filled out.
|  | Equipment installed on hold down bolts & bolts torqued |  | Equipment installed on hold down bolts and bolts torqued
|  | Excitation Characteristics |  | Excitation Characteristics
|  | Field inputs operated from devices correctly as per drawings |  | Field inputs operated from devices correctly as per drawings
|  | Fit JB/control box cover (incl. correct grease for Ex’d’ box) |  | Fit JB/control box cover (including correct grease for Ex’d’ box)
|  | Fit labels on ladder/tray if required by Specification |  | Fit labels on ladder/tray if required by Specification
|  | Fit ladder covers if required by specification |  | Fit ladder covers if required by specification
|  | Frame & control cabinets checked as earthed |  | Frame & control cabinets checked as earthed
|  | Function Checks |  | Function Checks
|  | Functional operation checks |  | Functional operation checks
|  | Heater installed & functions correctly |  | Heater installed and functions correctly
|  | HV Pressure Test |  | HV Pressure Test
|  | If receiver reading is suitable |  | If receiver reading is suitable i.e. approx 1.635 AC m/ohms is encountered, note and record this result. Check manufacturers spec. Record results on battery impedance sheet.
|  | Inspect cable earth bonding, SWA clamping |  | Inspect cable earth bonding, SWA clamping
|  | Inspect cable identification fixed at both ends is correct |  | Inspect cable identification fixed at both ends is correct
|  | Inspect cable protective measures adequate |  | Inspect cable protective measures adequate (eg kick guards, protection from sharp edges)
|  | Inspect cable routing, segregation & fixing details |  | Inspect cable routing, segregation & fixing details
|  | Inspection of stand completed |  | Inspection of stand completed.
|  | Install & secure Panel/JB |  | Install and secure Panel / JB
|  | Install cable gland tape protection system as appropriate |  | Install cable gland tape protection system as appropriate
|  | Install clip on ammeter on any suitable flexible battery link |  | Install clip on ammeter on any suitable flexible battery link.
|  | Install earthing conductor attached to tray as applicable |  | Install earthing conductor attached to tray as applicable
|  | Insulation Resistance |  | Insulation Resistance
|  | Insulation resistance check: Record on cable card |  | Insulation resistance check: Record on cable card
|  | Interlock functioning |  | Interlock functioning
|  | Joints bonded to earthed |  | Joints bonded to earthed
|  | Labels fixed in position & are correct. |  | Labels fixed in position and are correct.
|  | Ladder rack approved for use in relay or control room |  | Ladder rack approved for use in relay or control room
|  | Links bolted up to the correct manufacturers tension. |  | Links bolted up to the correct manufacturers tension.
|  | Local Alarms checked |  | Local Alarms checked
|  | Look for corrosion, heat, sturdiness/tightness of links, straps - terminals |  | Look for corrosion, heat, sturdiness/tightness of links, straps - terminals. Petroleum jelly on terminals should be clean, if necessary add. Clean top of batteries where necessary.
|  | Low Voltage Terminal earthed |  | Low Voltage Terminal earthed
|  | Main Contact Resistance |  | Main Contact Resistance
|  | Mark out Earthing layout per drawing |  | Mark out Earthing layout per drawing
|  | Mark up "As built" drawings |  | Mark up "As built" drawings.
|  | Minimum Operation |  | Minimum Operation
|  | Modern batteries are a `sealed unit' type |  | Modern batteries are a `sealed unit' type. Do not open vent plugs nor take specific gravity test, nor fluid top up.
|  | Nameplate data recorded |  | Nameplate data recorded
|  | Network Switches installed, configured & operational |  | Network Switches installed, configured & operational
|  | No cable ladder earthed via panel earthing |  | No cable ladder earthed via panel earthing
|  | No cable ladder supported by relay or control panels |  | No cable ladder supported by relay or control panels
|  | Note & record source current/Read from `bite' meter |  | Note and record source current. Read from `bite' meter. Repeat for all Battery Units
|  | Note & record total AC current on clip on ammeter which must be more than 5 amp |  | Note and record total AC current on clip on ammeter which must be more than 5 amp. If less than 5 amp receiver will read Lo=(A).
|  | Note & record total current/Read from clip on ammeter |  | Note and record total current. Read from clip on ammeter.
|  | Output operate correct devices as per drawings |  | Output operate correct devices as per drawings
|  | Phase colours & equipment numbers installed |  | Phase colours and equipment numbers installed
|  | Polarity & Primary Injection to Device |  | Polarity & Primary Injection to Device
|  | Polarity Test |  | Polarity Test
|  | Ratio Error Tests |  | Ratio Error Tests
|  | Read & record ambient air temperature |  | Read and record ambient air temperature.
|  | Read & record ripple current |  | Read and record ripple current.
|  | Relay settings download & checked |  | Relay settings download and checked
|  | Remove JB/control box cover |  | Remove JB/control box cover. Inspect gland assembly inner/outer seals
|  | Resistance of main circuit |  | Resistance of main circuit
|  | Resistance to Earth grid (point to point tests) |  | Resistance to Earth grid ( point to point tests )
|  | Resistivity of earth (using fall of potential) |  | Resistivity of earth (using fall of potential)
|  | Rodent proofing - All entry Points to raceway rodent/fire proof |  | Rodent proofing - All entry Points to raceway rodent/fire proof
|  | RTAC config developed from Spreadsheet |  | RTAC config developed from Spreadsheet
|  | RTAC config download & checked |  | RTAC config download and checked
|  | RTAC connection to BMS established |  | RTAC connection to BMS established
|  | SCADA tests to SCH completed & checksheet filled in |  | SCADA tests to SCH completed and checksheet filled in
|  | Secondary relay injection completed to confirm settings |  | Secondary relay injection completed to confirm settings
|  | SEL387L Relay settings applied |  | SEL387L Relay settings applied
|  | SEL735 Relay settings applied |  | SEL735 Relay settings applied
|  | SEL751 Relay settings applied |  | SEL751 Relay settings applied
|  | Spreadsheet prepared for RTAC config |  | Spreadsheet prepared for RTAC config
|  | Terminals d1/d2 shorted |  | Terminals d1/d2 shorted
|  | Test Report for CBs |  | Test Report for CBs
|  | Test Report for Circuit Breaker |  | Test Report for Circuit Breaker
|  | Test Report for CT |  | Test Report for CT
|  | Test Report for Voltage Transformers |  | Test Report for Voltage Transformers
|  | The installation & wiring in accordance with drawings |  | The installation and wiring in accordance with drawings
|  | Tightness of all connections checked |  | Tightness of all connections checked
|  | Timing |  | Timing
|  | Tray etc installed & bonded |  | Tray etc installed and bonded
|  | Treatment of screens correct |  | Treatment of screens correct (NB: screens insulated from earth and electrically continuous throughout loop, except at Marshalling Cabinet where connected to instrument earth)
|  | Trunking & termination covers in place |  | Trunking and termination covers in place
|  | Use rubber gloves & eye protection when handling batteries. Install bank |  | Use rubber gloves and eye protection when handling batteries. Install bank.
|  | Using the Bite Battery Impedance Tester |  | Using the Bite Battery Impedance Tester. Carry out Battery Impedance Tests.
|  | Verify that drawings are latest revision & manufacturer's manuals |  | Verify that drawings are latest revision and manufacturer's manuals
|  | Verify that drawings are latest revision & manufacturer's manuals available on site |  | Verify that drawings are latest revision and manufacturer's manuals available on site.
|  | VT Ratio & Phasing Check |  | VT Ratio & Phasing Check
|  | When battery bank is connected to load, check & record `load volts' reading taken under normal in service cond. |  | When battery bank is connected to the load, check and record `load volts' reading is taken under normal in service conditions with all fuses in and charger on.
|  | Yellow line check continuity of each core against interconnect diagram point to point |  | Yellow line check continuity of each core against interconnect diagram point to point
High Voltage (Test Report)
| Scope |  |  | High Voltage | Test Report
Rows
|  | Test Report | dynamic | High Voltage | Test Report
Columns
|  | Test Reort Completed |  | Test Reort Completed
|  | CHECKED |  | CHECKED
|  | APPROVED |  | APPROVED
|  | Uploaded to CONQA |  | Uploaded to CONQA