## QA Folder Structure
QA Folder Structure |  |  |  |  | Checklists
Site QA
Building A
Sprinkler Rough In
LG
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
|  |  |  | Sprinkler Rough In 2 | ITP 301 - Sprinkler Installation - Install RI, High level
LGM
GRD
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
|  |  |  | Sprinkler Rough In 2 | ITP 301 - Sprinkler Installation - Install RI, High level
|  |  |  | Sprinkler Rough In 3 | ITP 301 - Sprinkler Installation - Install RI, High level
L1
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
L2
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
L3
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
L4
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
L5
|  |  |  | Sprinkler Rough In 1 | ITP 301 - Sprinkler Installation - Install RI, High level
Drencher Rough In
LG
LGM
GRD
L1
L2
|  |  |  | Drencher 1 | ITP 301 - Sprinkler Installation - Install RI, High level
L3
L4
L5
Sprinkler Fit Off
LG
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
|  |  |  | Sprinkler 2 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
LGM
GRD
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
|  |  |  | Sprinkler 2 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
|  |  |  | Sprinkler 3 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
L1
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
L2
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
L3
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
L4
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
L5
|  |  |  | Sprinkler 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
Drencher Fit Off
LG
LGM
GRD
L1
L2
|  |  |  | Drencher 1 | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
L3
L4
L5
Hydrant Install
LG
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
LGM
GRD
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
L1
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
L2
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
L3
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
L4
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
L5
|  |  |  | Hydrant 1 | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
Sprinkler Control Valve Install & Operation
LG
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
|  |  |  | SCV 2 | ITP 304 - Sprinkler Control Valve Installation
LGM
GRD
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
|  |  |  | SCV 2 | ITP 304 - Sprinkler Control Valve Installation
|  |  |  | SCV 3 | ITP 304 - Sprinkler Control Valve Installation
L1
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
L2
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
L3
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
L4
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
L5
|  |  |  | SCV 1 | ITP 304 - Sprinkler Control Valve Installation
Drencher Control Valve Install & Operation
LG
LGM
GRD
L1
L2
|  |  |  | DCV 1 | ITP 304 - Sprinkler Control Valve Installation
L3
L4
L5
Vortex System Install & Operation
LG
LGM
GRD
L1
L2
L3
L4
L5
|  |  |  | Vortex 1 | PLACEHOLDER
Sprinkler Hydrostatic Test
LG
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
|  |  |  | Test 2 | ITP 401 - Sprinkler Hydrostatic Pressure Test
LGM
GRD
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
|  |  |  | Test 2 | ITP 401 - Sprinkler Hydrostatic Pressure Test
|  |  |  | Test 3 | ITP 401 - Sprinkler Hydrostatic Pressure Test
L1
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
L2
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
L3
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
L4
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
L5
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
Drencher Hydrostatic Test
LG
LGM
GRD
L1
L2
|  |  |  | Test 1 | ITP 401 - Sprinkler Hydrostatic Pressure Test
L3
L4
L5
Hydrant Hydrostatic Test
|  |  | Test 1 |  | ITP 402 - Hydrant Hydrostatic Pressure Test
Extinguisher Install
LG
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
LGM
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
GRD
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
L1
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
L2
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
L3
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
L4
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
L5
|  |  |  | Drawing | Drawing - Fire Extinguisher Installation
Pump Install & Operation
Booster Install
Final Documentation and Signage

## Checklists
type | name | values
checklist-flat | ITP 301 - Sprinkler Installation - Install RI, High level
checkpoint | 1. Dr’g No: / Revision Correct.
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Supports spacing & fixing as per code AS2118 Part 9.
checkpoint | 3. Pipework installed as per Dr’g.
checkpoint | 4. Concealed space sprinklers installed.
checkpoint | 6. Pipes left out as noted below.
checkpoint | 7. Flexibles installed.
checkpoint | 8. Charge hand inspection.
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 302 - Sprinkler Installation - Below Ceiling Fit-off
checkpoint | 1. Drg No / Revision
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Ceiling grid levelled
checkpoint | 3. Sprinklers installed as per drg
checkpoint | 4. All escutcheon plates installed
checkpoint | 5. Areas not fitted-off as noted below
checkpoint | 6. Pressure Tested (refer I&TR 401)
checkpoint | 7. Charge hand inspection
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
checkpoint | 1. Drg No / Revision
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Supports spacing & fixing as per code. AS:2419
checkpoint | 3. Pipework installed as per drg
checkpoint | 4. Pipes left out as notes & reason
checkpoint | 5. Hyd valve installed at correct height
checkpoint | 6. Hosereel installed at correct height
checkpoint | 7. Signage & labelling installed
checkpoint | 8. Hydrant valves locked open
checkpoint | 9. Valve Numbers and Labelling installed
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 304 - Sprinkler Control Valve Installation
checkpoint | Sprinkler Rough-In completed
checkpoint | 1. Monitored Alarm Valve Operated
checkpoint | 2. Solenoid Valve Operated
checkpoint | 3. Flow Switch Operated
checkpoint | 4. Run Remote Test Drain
checkpoint | 5. Installation Pressure Switch Operated
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 401 - Sprinkler Hydrostatic Pressure Test
checkpoint | First Sighting
label | Guidelines - “1400 kPa for 2 hours” with no pressure loss.
text | Date
text | Time
text | Pressure
text | Witness (Contractfire)
text | Witness (Multiplex)
checkpoint | Second Sighting
label | Guidelines - “1400 kPa for 2 hours” with no pressure loss.
text | Date
text | Time
text | Pressure
text | Witness (Contractfire)
text | Witness (Multiplex)
checkpoint | Subsequent Sightings, if required
text | Date
text | Time
text | Pressure
text | Witness (Contractfire)
text | Witness (Multiplex)
checklist-flat | ITP 402 - Hydrant Hydrostatic Pressure Test
checkpoint | First Sighting
label | Guidelines - “1700 kPa for 2 hours” with no pressure loss.
text | Date
text | Time
text | Pressure
text | Witness (Contractfire)
text | Witness (Multiplex)
checkpoint | Second Sighting
label | Guidelines - “1700 kPa for 2 hours” with no pressure loss.
text | Date
text | Time
text | Pressure
text | Witness (Contractfire)
text | Witness (Multiplex)
checkpoint | Subsequent Sightings, if required
text | Date
text | Time
text | Pressure
text | Witness (Contractfire)
text | Witness (Multiplex)
checklist-flat | Drawing - Fire Extinguisher Installation
checkpoint | Installation locations as per drawing
checkpoint | Drg No / Revision
text | Drawing No.
text | Revision No.
checklist-flat | ITP 501 - Fire Extinguisher Installation
checkpoint | 1. Location confirmed with MFB stamped drawing or building surveyor descriptions
checkpoint | 2. Correct unit height & clearances
checkpoint | 3. Extinguishers tagged
checkpoint | 4. Extinguishers in new condition
checkpoint | 5. Instruction signage plate installed
checkpoint | 6. Location signage installed to code
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 601 - Diesel Pump Installation / Commissioning
checkpoint | 1. Pump room drawing revision
text | Drawing No.
text | Revision No.
checkpoint | 2. Piping as per installation
checkpoint | 3. Power available from electrical contractor & approved for use
checkpoint | 6. Pump performance site test results Diesel S1
checkpoint | 7. Pump performance site test results Diesel S2
checkpoint | 8. Panel function test for Diesel Controllers
checkpoint | 9. Panel function test for Electrical Controllers
checkpoint | 10. 15 minute pump run test
checkpoint | 11. 90 Minute pump run test
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 601 - Electric Pump Installation / Commissioning
checkpoint | 1. Pump room drawing revision
text | Drawing No.
text | Revision No.
checkpoint | 2. Piping as per installation
checkpoint | 3. Power available from electrical contractor & approved for use
checkpoint | 4. Pump performance site test results Elec S1
checkpoint | 5. Pump performance site test results Elec S2
checkpoint | 8. Panel function test for Diesel Controllers
checkpoint | 9. Panel function test for Electrical Controllers
checkpoint | 10. 15 minute pump run test
checkpoint | 11. 90 Minute pump run test
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 701 - Booster Installation
checkpoint | 1. Installed as per drawing
checkpoint | 2. Drawing revision
checkpoint | 3. MFB required clearance confirmed
checkpoint | 4. Labelling per stage & level provided
checkpoint | 5. Isolations valves closed & locked
checkpoint | 6. Pressure gauges at T.M pressure
checkpoint | 7. Storz couplings installed to suction points
checkpoint | 8. Hydrostatic Test Completed (1700 kpa)
checkpoint | 9. Independent Certification
checkpoint | 10. Contractfire Completion Statement
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date:
checklist-flat | ITP 801 - Project Completion/Certification Checklist
checkpoint | 1. Hydrostatic Test Completed (ITR401)
checkpoint | 2. Independent Certification
checkpoint | 3. Contractfire Completion Statement
checkpoint | 4. Contractfire Warranty Statement
checkpoint | 5. Operation & Maintenance Manuals
checkpoint | 6. Quality Assurance Documentation
checkpoint | 7. As Installed Documentation
checkpoint | 8. Testing & Maintenance Commences
checkpoint | Contractfire Sign Off
text | Checked By:
text | Date: