## Wall And Slab Materials
Wall And Slab Materials Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S114 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL
4.08 | Concrete Materials
4.08.01 | Embankment Walls and Foundations Mix Design | The Contractor shall submit a concrete mix design certified by an independent testing laboratory no later than four weeks prior to the commencement of concrete placement to the Engineer for Approval. | RSV - CS - 1.4 / 1.6 | Approved Mix Design | Four weeks prior to the commencement of concrete | HP | ENG
4.08.02 | Spillway Mix Design | The Contractor shall submit a concrete mix design certified by an independent testing laboratory no later than four weeks prior to the commencement of concrete placement to the Engineer for Approval. | RSV - CS - 1.4 / 1.6 DWG 41-32443-05-G002 | Approved Mix Design | Four weeks prior to the commencement of concrete | HP | ENG
4.08.03 | Overlay Slab & Pile Cap Mix Design | The Contractor shall submit a concrete mix design certified by an independent testing laboratory no later than four weeks prior to the commencement of concrete placement to the Engineer for Approval. | RSV - CS - 1.4 / 1.6 DWG 41-32443-05-G002 | Approved Mix Design | Four weeks prior to the commencement of concrete | HP | ENG
4.08.04 | Stilling Basin Mix Design | The Contractor shall submit a concrete mix design certified by an independent testing laboratory no later than four weeks prior to the commencement of concrete placement to the Engineer for Approval. | RSV - CS - 1.4 / 1.6 DWG 41-32443-05-G002 | Approved Mix Design | Four weeks prior to the commencement of concrete | HP | ENG
4.08.05 | Concrete Compression Testing Laboratory | Compression testing shall be carried out at the cost of the Contractor by an independent laboratory to which the Engineer has no objection. | RSV - CS - 1.12 | Approval | Prior to Placement | HP | ENG
4.08.06 | Reinforcement | Reinforcing bars and mesh shall comply with AS/NZS4671:2001. | RSV - CS - 1.19 | Mill Certs | Each Pour | R | PE

## Wall And Slab Overarching
Wall And Slab Overarching Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S115 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
3.01 | Site Requirements
3.01.01 | Construction Pack | Submit a Construction Pack including a Methodology and JESA to the Engineer before works | Downer | Construction Pack | Submit Prior to commencement of works | H | PE
3.01.02 | Survey Setout | Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed. | Downer | Survey Records | Prior to Works | H | SV
3.01.03 | Service Location | Complete the Excavation permit process to identify, locate and protect all services. | Downer | Excavation Permit | Prior to Excavation | H | SE
3.01.04 | Internal Permits | Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc. | Downer | Internal Permits | Prior to Excavation | H | SE
3.01.05 | External Permits | Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc. | Downer | External Permits | Prior to Excavation | H | PE
3.01.06 | Approved Construction Drawings | Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version. | Downer | IFC Drawings | Prior to works start | H | PE
SECTION 10 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
10.01 | Site Post Construction Activities
10.01.01 | Construction Record Compilation | Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted. | Downer | Records | Post construction | H | SE
10.01.02 | Survey Records | Ensure all items have been surveyed and records are assembled for asbuilting | Downer P&G 20.1 | Records | Post construction | H | SV
10.01.03 | Redline Drawings | Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. Red-pen mark-up copies of the Drawings and Specifications and other design documentation showing any deviations from the specified details and requirements produced in accordance with industry good practice. | Downer P&G 20.1 | Redlines | Post construction | H | PE
10.01.04 | Defect, Snag and Punch List | Update the project Defect, Snag and Punch List Register | Downer | Register | Post construction | H | PE

## Wall And Slab Installation
Wall And Slab Installation Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S116 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 8 – CONSTRUCTION ACTIVITY – CONCRETE CONSTRUCTION (Excluding Jet-Grouting)
8.01 | Concrete Subgrade Preparation
8.01.01 | Wall Type 1 Subgrade Preparation | Concrete of the existing dam surface to be water blast cleaned and roughened to provide NZS3109 Type B Construction Joint. | RSV - GS - 1.1 | Photo | Prior to Pour | R | PE
8.01.02 | Wall Type 2 Subgrade Preparation | Existing concrete under and to the sides of the foundation to be thoroughly water blasted back to sound concrete. | RSV - GS - 1.1 | Photo | Prior to Pour | R | PE
8.01.03 | Wall Type 3 & 4 Subgrade Preparation | Any soft soil or silts to be removed from site and subgrade to be inspected. Fill to underside of foundation with AP40 or approved fill. Fill to be compacted in 200mm layers. | RSV - GS - 1.1 | Approved Subgrade | Prior to Pour | R | PE
8.01.04 | Return Wall Subgrade Preparation | Ground excavated to footing level. Backfill as required with AP40 or approved fill. Fill to be compacted in 200mm layers. | RSV - GS - 1.1 | Approved Backfill | Prior to Pour | R | PE
8.02 | Concrete Pour (Pre and Post Pour Checksheet)
| General Details |  |  | Pre-Pour Checksheet
Pre Pour Date
Concrete Strength (mPa)
Volume (m3)
Mix Design
Additives
| Reinforcing has been checked and conforms to the drawings included: |  |  | Pre-Pour Checksheet
Bar Size & Grade, Lap Lengths, Lap Locations, Bar Supports, Bar Spacing, Cover
8.02.01 | Construction Joint Locations | Proposed location of construction joints to be submitted to the engineer for review prior to concrete pour. | RSV - CS - 1.15 | Approval | Prior to Pour | HP | ENG
8.02.02 | Grouting of Bars | Reinforcement installed into existing concrete shall be epoxied into the cured concrete with Hilti HIT RE 500 V3 epoxy mortar to the depth shown on the drawings and all strictly installed to the manufacturers written instructions. | RSV - CS - 1.18 | Photos | Prior to Pour | R | SE
8.02.03 | Reinforcement Washdown | Washdown all steel reinforcement prior to pouring concrete to remove salts. | RSV - CS - 1.19 | Pre-Pour Checksheet | Prior to Pour | R | SE
8.02.04 | Pre-Pour Inspections | Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area. | P&G 14 | Signed Pre-Pour | 48 Hours Notice Prior to Each Occurrence | HP | ENG
Pour Details
Weather:
8.02.05 | Delivery Dockets | The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size. | RSV - CS - 1.9 | Dockets | Each Pour | R | PE
8.02.06 | Slump Testing | Slump tests shall be taken for each delivery of concrete and the results recorded by the Contractor. | RSV - CS - 1.12 | Pre Pour | Each Pour | R | PE
8.02.07 | Compression Testing | A set of specimens for concrete tests shall consist of four specimens from each major pour of concrete, one of which shall be tested at 7 days and the remaining three at 28 days after casting. | RSV - CS - 1.12 | Test Results | Each Pour | R | PE
Post Pour Acceptance and Survey
8.03 | Pre-Past Concrete Placement
8.03.01 | Bearing for Precast Concrete Tolerances | In addition to the requirements of NZS 3109 insitu concrete surfaces to provide a bearing for precast concrete work shall be cast with a level tolerance of +0mm and -3mm. | RSV - CS - 1.17 | Survey | Prior to Placement | D | SV