## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | DS2672-ITP-S117 - Rail and Walkway Materials - Rev 1 | itp |  |  |  |  | DS2672-ITP-S117 - Rail and Walkway Materials - Rev 1
section | 4.09 Timber Handrail Materials
checkpoint | 4.09.01 - Timber Posts
note | Acceptance / Conformance Criteria - Posts shall be a minimum SG8 grade and treated to TPA H5 requirements.
note | Standard / Specification - RSV - TS - 1.3
note | Verifying Document - Datasheet / Docket
note | Frequency - Prior to use
note | Activity - R
note | By - SE
checkpoint | 4.09.02 - Sawn timber rails
note | Acceptance / Conformance Criteria - Sawn timber rails and palings shall be a minimum SG8 grade and treated to TPA H3 requirements.
note | Standard / Specification - RSV - TS - 1.3
note | Verifying Document - Datasheet / Docket
note | Frequency - Prior to use
note | Activity - R
note | By - SE
checkpoint | 4.09.03 - Timber Fixings
note | Acceptance / Conformance Criteria - All fixings shall be stainless steel unless specifically stated.
note | Standard / Specification - RSV - TS - 1.4
note | Verifying Document - Datasheet
note | Frequency - Prior to use
note | Activity - R
note | By - SE
section | 4.10 Rail and Walkway Materials
checkpoint | 4.10.01 - Steel Conformance
note | Acceptance / Conformance Criteria - Material certificates shall be in accordance with the requirements of the relevant steel standard with testing completed by a reputable ISO/IANZ or NATA accredited laboratory.
note | Standard / Specification - ALD-0424-REP - 2.5.2.1
note | Verifying Document - Material Certificates
note | Frequency - Prior to Commissioning
note | Activity - R
note | By - SE
checkpoint | 4.10.02 - Steel Plates
note | Acceptance / Conformance Criteria - All steel plates shall be grade 300 or 350 to AS/NZs 3678 unless specified otherwise
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Mill Certs
note | Frequency - Prior to Commissioning
note | Activity - R
note | By - SE
checkpoint | 4.10.03 - Steel Sections
note | Acceptance / Conformance Criteria - All steel sections shall be grade 300 to AS/NZs 3679 unless specified otherwise
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Mill Certs
note | Frequency - Prior to Commissioning
note | Activity - R
note | By - SE
checkpoint | 4.10.04 - Fasteners
note | Acceptance / Conformance Criteria - All Fasteners To Be Grade 8.8 Galvanized Metric Threads
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Material Certificates
note | Frequency - Prior to Commissioning
note | Activity - R
note | By - SE
checkpoint | 4.10.05 - Roller Chain
note | Acceptance / Conformance Criteria - The chain shall be a 12b-1 simplex roller chain to iso 606:2015 3/4" / 19.05mm pitch approx. length - 99m
note | Standard / Specification - DWG - ALD-0323-ASY
note | Verifying Document - Material Certificates
note | Frequency - Prior to Commissioning
note | Activity - R
note | By - SE