## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | DS2672-ITP-S119 - Welding Finishing and Coating - Rev 1 | itp |  |  |  |  | DS2672-ITP-S119 - Welding Finishing and Coating - Rev 1
section | 9.01 Steel Welding
checkpoint | 9.01.01 - Welders
note | Acceptance / Conformance Criteria - Welders to be competent and hold current relevant certificates to AS/NZS 1554.1 SP for carbon steel.
note | Standard / Specification - ALD-0424-REP - 2.5.2.3
note | Verifying Document - Qualification
note | Frequency - Prior to Welding
note | Activity - R
note | By - PE
checkpoint | 9.01.02 - Welding Methodology
note | Acceptance / Conformance Criteria - Fabrication, testing and inspection of welded fabrications shall be in accordance with the welding standard specifically defined on the drawing or when no specific requirement is provided, the latest applicable version of AS/NZS 1554.1 SP for carbon steel.
note | Standard / Specification - ALD-0424-REP - 2.5.2.2
note | Verifying Document - Methodology
note | Frequency - Prior to Welding
note | Activity - R
note | By - PE
checkpoint | 9.01.03 - Welding Inspector
note | Acceptance / Conformance Criteria - Welds shall be non-destructively tested in accordance with the requirements of the welding standard utilised by a CBIP-NZ qualified inspector.
note | Standard / Specification - ALD-0424-REP - 2.5.2.4
note | Verifying Document - Qualification
note | Frequency - Prior to Welding
note | Activity - R
note | By - PE
checkpoint | 9.01.04 - Periodic Inspection of Manufacturing Process’s
note | Acceptance / Conformance Criteria - The Contractor shall provide the Principal with 2 weeks’ notice and ongoing co-ordination to allow for the Principal to witness Periodic inspection of manufacturing process’s (timing TBC).
note | Standard / Specification - ALD-0424-REP - 2.5.2.8
note | Verifying Document - Notice
note | Frequency - 2 weeks’ notice
note | Activity - W
note | By - ENG
checkpoint | 9.01.05 - Welding Records
note | Acceptance / Conformance Criteria - Welding Should Be Performed By Qualified Personnel In Accordance With AS/NZS 1554. Manufacturer’s product code & batch number of all welding consumables must be Recorded by the supplier.
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Welding Records
note | Frequency - Prior to Delivery
note | Activity - R
note | By - PE
checkpoint | 9.01.06 - General NDT Welding Inspection
note | Acceptance / Conformance Criteria - A minimum of 20% of welds in components shall be examined along their full-length using dye penetrant (PT) or magnetic particle inspection (MPI) techniques.
note | • It is important to include a variety of welds typically used on the fabrication under scrutiny to obtain a comprehensive understanding of the weld quality.
note | • NDT Acceptance levels shall be in accordance with the standard apply to the weld.
note | Standard / Specification - ALD-0424-REP - 2.5.2.4
note | Verifying Document - Inspector Report
note | Frequency - 20% of Welds in Components
note | Activity - I
note | By - PE
checkpoint | 9.01.07 - Fillet and But Welding Visual NDT
note | Acceptance / Conformance Criteria - All fillet welds and butt welds shall be subjected to 100% visual examination.
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Inspector Report
note | Frequency - 100% of Welds
note | Activity - I
note | By - PE
checkpoint | 9.01.08 - Fabrication Fillet and But Welding MPE NDT
note | Acceptance / Conformance Criteria - All fillet welds and butt welds carried out in the fabrication shall be subjected to 50% of magnetic particle examination (MPE).
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Inspector Report
note | Frequency - 50% of Welds
note | Activity - I
note | By - PE
checkpoint | 9.01.09 - Site Fillet and But Welding MPE NDT
note | Acceptance / Conformance Criteria - All fillet welds and butt welds carried out on site shall be subjected to 100% MPE.
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Inspector Report
note | Frequency - 100% of Welds
note | Activity - I
note | By - PE
checkpoint | 9.01.10 - Failed NDT
note | Acceptance / Conformance Criteria - The Contractor shall inform the Principal of the results as soon as practical, specifically where failures are noted, and shall submit a formal NDT report to the Principal within 14 calendar days of undertaking the tests.
note | • Failed Welds shall be subject to 100% re-examination by the same respective method after repair.
note | Standard / Specification - ALD-0424-REP - 2.5.2.4
note | Verifying Document - NCR and Retest Reports
note | Frequency - As Required
note | Activity - R
note | By - PE
checkpoint | 9.01.11 - Rails and Walkaway Fabrication Inspection
note | Acceptance / Conformance Criteria - A Hold point shall be adhered to during the manufacturing of the rails and walkaway assembly After fabrication and NDT prior to assembly.
note | Standard / Specification - ALD-0424-REP - 2.5.2.9
note | Verifying Document - Hold Point Release
note | Frequency - Prior to Assembly
note | Activity - HP
note | By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 9.02 Finishing / Coating
checkpoint | 9.02.01 - Painting Methodology / Procedure / Certification
note | Acceptance / Conformance Criteria - Where painting is specified, the structural weldment for each component shall be properly prepared by rounding any sharp edges and dry abrasive blasting the steel surfaces to satisfy preparation requirements specified on the manufacturing drawings.
note | Standard / Specification - ALD-0424-REP - 2.5.2.5
note | Verifying Document - Methodology / Procedure / Certification
note | Frequency - Prior to Painting
note | Activity - R
note | By - PE
checkpoint | 9.02.02 - Paint DFT
note | Acceptance / Conformance Criteria - A three-coat protective coating shall be applied in accordance with paint supplier recommendations to achieve an overall Dry Film Thickness (DFT) as specified on manufacturing drawings.
note | Standard / Specification - ALD-0424-REP - 2.5.2.5
note | Verifying Document - Test Results
note | Frequency - Random locations covering ≈10% of the painted product.
note | Activity - I
note | By - PE
checkpoint | 9.02.03 - Paint Holiday testing
note | Acceptance / Conformance Criteria - Post application holiday testing shall be completed in accordance with NACE PRO 1880 or equivalent procedure approved by the Principal.
note | Standard / Specification - ALD-0424-REP - 2.5.2.5
note | Verifying Document - Test Results
note | Frequency - Each Occurance
note | Activity - I
note | By - PE
checkpoint | 9.02.04 - Hot Dip Galvanising Methodology / Procedure / Certification
note | Acceptance / Conformance Criteria - Parts shall be thoroughly pickled before galvanising. Matter likely to resist removal by pickling such as welding slag, paint and grease shall be removed prior to pickling by blast cleaning to AS 1627 Pt 9 Grade Sa 2 ½.
note | • Coatings shall be unbroken and of a minimum thickness of 80 microns to AS 1650:1989. Galvanising shall be applied by the hot dip process in accordance with AS / NZS 4680: 2006.
note | Standard / Specification - ALD-0424-REP - 2.5.2.6
note | Verifying Document - Methodology / Procedure / Certification
note | Frequency - Prior to Galv
note | Activity - I
note | By - PE
checkpoint | 9.02.05 - Rail Straightness
note | Acceptance / Conformance Criteria - Confirm the rails straightness after galvanising.
note | Standard / Specification - ALD-0424-REP - 2.5.3
note | Verifying Document - Factory Acceptance Test Records
note | Frequency - Prior to Installation
note | Activity - I
note | By - PE
checkpoint | 9.02.06 - Hot Dip Galvanising NDT
note | Acceptance / Conformance Criteria - Evidence of coating mass and local thickness shall be provided in accordance with AS/NZS 4680:2006 as part of the Contractors Quality Management plan
note | Standard / Specification - ALD-0424-REP - 2.5.2.6
note | Verifying Document - Test Results
note | Frequency - Each Batch
note | Activity - I
note | By - PE
checkpoint | 9.02.07 - Thermal Zinc Spraying Methodology / Procedure / Certification
note | Acceptance / Conformance Criteria - Parts to be free of burrs, weld splatter and slag, and prepared in accordance with AS/NZS 4680:2006. Parts to be sand blasted to Sa 2.5 as per ISO 8501-1:2007 to achieve a minimum roughness of 50μm.
note | • All thermal zinc spraying to be done in accordance with AS/NZS 2312 and ISO 2063, with a nominal thickness of 150 μm of TSZ / zinc metal spray, with no spot less than 120μm, using Dichtol WFT 1532 penetrating sealer.
note | • The part shall then be finished with a 50μm epoxy sealer.
note | Standard / Specification - ALD-0424-REP - 2.5.2.7
note | Verifying Document - Methodology / Procedure / Certification
note | Frequency - Prior to Zinc
note | Activity - I
note | By - PE
checkpoint | 9.02.08 - Thermal Zinc Spraying NDT
note | Acceptance / Conformance Criteria - Evidence of coating mass and local thickness shall be provided in accordance with AS/NZS 4680:2006 as part of the Contractors Quality Management plan.
note | Standard / Specification - ALD-0424-REP - 2.5.2.7
note | Verifying Document - Test Results
note | Frequency - Each Batch
note | Activity - I
note | By - PE
checkpoint | 9.02.09 - Rails and Walkaway Galvanising Inspection
note | Acceptance / Conformance Criteria - A Hold point shall be adhered to during the manufacturing of the rails and walkaway assembly After galvanising.
note | Standard / Specification - ALD-0424-REP - 2.5.2.9
note | Verifying Document - Hold Point Release
note | Frequency - Prior to Installation
note | Activity - HP
note | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.02.10 - Finishing / Coating Repair Methodology
note | Acceptance / Conformance Criteria - The Contractor is responsible to make good any damage (i.e., paint abrasion etc.) arising from transportation, lifting and installation.
note | Standard / Specification - ALD-0424-REP - 2.6.3.4
note | Verifying Document - Methodology
note | Frequency - Prior to Delivery
note | Activity - R
note | By - PE
checkpoint | 9.02.11 - Final Inspection of Manufactured Goods Prior to Dispatch
note | Acceptance / Conformance Criteria - The Contractor shall provide the Principal with 2 weeks’ notice and ongoing co-ordination to allow for the Principal to witness Final inspection of manufactured goods prior to dispatch.
note | Standard / Specification - ALD-0424-REP - 2.5.2.8
note | Verifying Document - Notice
note | Frequency - 2 weeks’ notice
note | Activity - W
note | By - ENG