## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | DS2672-ITP-S120 - Rail and Walkway Installation - Rev 1 | itp |  |  |  |  | DS2672-ITP-S120 - Rail and Walkway Installation - Rev 1
section | SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT) - 3.01 Site Requirements
checkpoint | 3.01.01 - Construction Pack
note | Acceptance / Conformance Criteria - Submit a Construction Pack including a Methodology and JESA to the Engineer before works
note | Standard / Specification - Downer
note | Verifying Document - Construction Pack
note | Frequency - Submit Prior to commencement of works
note | Activity - H
note | By - PE
checkpoint | 3.01.02 - Survey Setout
note | Acceptance / Conformance Criteria - Survey Set out as per contract drawings and specification, capturing pre-construction levels where needed.
note | Standard / Specification - Downer
note | Verifying Document - Survey Records
note | Frequency - Prior to Works
note | Activity - H
note | By - SV
checkpoint | 3.01.03 - Service Location
note | Acceptance / Conformance Criteria - Complete the Excavation permit process to identify, locate and protect all services.
note | Standard / Specification - Downer
note | Verifying Document - Excavation Permit
note | Frequency - Prior to Excavation
note | Activity - H
note | By - SE
checkpoint | 3.01.04 - Internal Permits
note | Acceptance / Conformance Criteria - Complete internal Permits as required to complete works including but not limited to: Hot works, concrete saw, lift, confined space, working at height etc.
note | Standard / Specification - Downer
note | Verifying Document - Internal Permits
note | Frequency - Prior to Excavation
note | Activity - H
note | By - SE
checkpoint | 3.01.05 - External Permits
note | Acceptance / Conformance Criteria - Obtain External Permits as required to complete works including but not limited to: Close approach, Worksafe Notice etc.
note | Standard / Specification - Downer
note | Verifying Document - External Permits
note | Frequency - Prior to Excavation
note | Activity - H
note | By - PE
checkpoint | 3.01.06 - Approved Construction Drawings
note | Acceptance / Conformance Criteria - Prior to starting works, Ensure that the construction drawings are both IFC and the Current Version.
note | Standard / Specification - Downer
note | Verifying Document - IFC Drawings
note | Frequency - Prior to works start
note | Activity - H
note | By - PE
section | SECTION 9 – CONSTRUCTION ACTIVITY – RAIL AND WALKWAY - 9.03 Removal and Installation
checkpoint | 9.03.01 - Safe Work Method Statements
note | Acceptance / Conformance Criteria - The Contractor shall Provide detailed Safe Work Method Statements for review and approval by the Engineer at least 4 weeks prior to the commencement of site works.
note | Standard / Specification - ALD-0424-REP - 2.6.1
note | Verifying Document - Construction Pack
note | Frequency - 4 weeks prior to the commencement of site works
note | Activity - HP
note | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.03.02 - Existing Concrete Pier Survey
note | Acceptance / Conformance Criteria - Before any installation work commences, the contractor shall survey all 6 of the existing concrete pier structures and confirm the Horizontal alignment of the US face of the Stoplog slot and the Vertical alignment of the top face.
note | Standard / Specification - ALD-0424-REP - 2.6.3.1
note | Verifying Document - Survey Results
note | Frequency - Before any installation work commences
note | Activity - D
note | By - SV
checkpoint | 9.03.03 - Grout Pre-Pour Inspections
note | Acceptance / Conformance Criteria - Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area.
note | Standard / Specification - P&G 14
note | Verifying Document - Signed Pre-Pour
note | Frequency - 48 Hours Notice Prior to Each Occurrence
note | Activity - HP
note | By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 9 – CONSTRUCTION ACTIVITY – RAIL AND WALKWAY - 9.04 Installation and Alignment of Bottom Steel Corbels
checkpoint | 9.04.01 - Bottom steel corbels Setout
note | Acceptance / Conformance Criteria - The contractor shall install the Bottom steel corbels (ALD-0284-WLD) such that the top of all 11 steel corbels is with +/- 5mm.
note | Standard / Specification - ALD-0424-REP - 2.6.3.2
note | Verifying Document - Survey Records
note | Frequency - Each steel corbel
note | Activity - D
note | By - SV
checkpoint | 9.04.02 - Surface in contact with Grout
note | Acceptance / Conformance Criteria - Ensure the back surface that will be Exposed to grout, is coated with carboguard 636
note | Standard / Specification - DWG - ALD-0032-ASY
note | Verifying Document - Site Records
note | Frequency - Each Grout Location
note | Activity - I
note | By - SE
checkpoint | 9.04.03 - Bolt pattern
note | Acceptance / Conformance Criteria - The contractor shall mark out the bolt pattern for the bottom steel corbel drilling using their own methodology.
note | Standard / Specification - ALD-0424-REP - 2.6.3.2
note | Verifying Document - Site Records
note | Frequency - Each steel corbel
note | Activity - I
note | By - SE
checkpoint | 9.04.04 - Clean-out
note | Acceptance / Conformance Criteria - Clean out drill holes such that no dust, silt, or debris remains in the hole. If anchors are not to be installed immediately, tightly plug the holes and clean out again just prior to anchor installation.
note | Standard / Specification - ALD-0424-REP - 2.6.3.2
note | Verifying Document - Site Records
note | Frequency - Each steel corbel
note | Activity - I
note | By - SE
checkpoint | 9.04.05 - Procedure
note | Acceptance / Conformance Criteria - Install the anchors strictly as per the drawings and in accordance with the epoxy manufacturer’s instructions and in such a manner that bending of the bolt shank and/or damage to the projecting threads is avoided.
note | Standard / Specification - ALD-0424-REP - 2.6.3.2
note | Verifying Document - Site Records
note | Frequency - Each steel corbel
note | Activity - I
note | By - SE
checkpoint | 9.04.06 - Anchor Embedment Site Acceptance Tests
note | Acceptance / Conformance Criteria - The Contractor shall provide the Principal with 2 weeks’ notice and ongoing co-ordination to allow for the Principal to witness Anchor embedment Site acceptance tests
note | Standard / Specification - ALD-0424-REP - 2.5.2.8
note | Verifying Document - Notice
note | Frequency - 2 weeks’ notice
note | Activity - W
note | By - ENG
checkpoint | 9.04.07 - Bolt Torqueing
note | Acceptance / Conformance Criteria - All Bolted Connections To Be Assembled To The Correct Torque.
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Torque Checksheet
note | Frequency - Each Bolt
note | Activity - I
note | By - SE
checkpoint | 9.04.08 - Pull-Out Tests
note | Acceptance / Conformance Criteria - The Contractor shall as part of the SAT, undertake pull-out tests to be conducted on a minimum of two anchors installed per corbel (chosen at random).
note | • When tested, the anchor shall be capable of withstanding without movement a pull-out test load equal to the ultimate strength of the threaded section of the bolt shank.
note | Standard / Specification - ALD-0424-REP - 2.6.3.2
note | Verifying Document - Test Report
note | Frequency - Two anchors per corbel
note | Activity - I
note | By - SE
checkpoint | 9.04.09 - Alignment check
note | Acceptance / Conformance Criteria - The contractor shall survey the installed corbels to confirm alignment, prior to commencing further assembly.
note | Standard / Specification - ALD-0424-REP - 2.6.3.2
note | Verifying Document - Survey Results
note | Frequency - Prior to commencing further assembly
note | Activity - D
note | By - SV
checkpoint | 9.04.10 - Rails and Walkaway Bottom Steel Corbels Inspection
note | Acceptance / Conformance Criteria - A Hold point shall be adhered to during the manufacturing of the rails and walkaway assembly After surveying the installation of bottom steel corbels prior to grouting.
note | Standard / Specification - ALD-0424-REP - 2.5.2.9
note | Verifying Document - Hold Point Release
note | Frequency - Prior to Grouting
note | Activity - HP
note | By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 9 – CONSTRUCTION ACTIVITY – RAIL AND WALKWAY - 9.05 Installation and Alignment of Top Steel Corbels
checkpoint | 9.05.01 - Top steel corbels Setout
note | Acceptance / Conformance Criteria - The contractor shall install the Top steel corbels (ALD-0285-WLD) such that the top of all 11 steel corbels is with +/- 1mm.
note | Standard / Specification - ALD-0424-REP - 2.6.3.3
note | Verifying Document - Survey Records
note | Frequency - Each steel corbel
note | Activity - D
note | By - SE
checkpoint | 9.05.02 - Bolt Torqueing
note | Acceptance / Conformance Criteria - All Bolted Connections To Be Assembled To The Correct Torque.
note | Standard / Specification - DWG - ALD-0454-GAD
note | Verifying Document - Torque Checksheet
note | Frequency - Each Bolt
note | Activity - I
note | By - SE
checkpoint | 9.05.03 - Alignment check
note | Acceptance / Conformance Criteria - The contractor shall survey the installed top corbels to confirm alignment, prior to commencing further assembly.
note | Standard / Specification - ALD-0424-REP - 2.6.3.3
note | Verifying Document - Survey Results
note | Frequency - Prior to commencing further assembly
note | Activity - D
note | By - SV
checkpoint | 9.05.04 - Rails and Walkaway Top Steel Corbels Inspection
note | Acceptance / Conformance Criteria - A Hold point shall be adhered to during the manufacturing of the rails and walkaway assembly After surveying the installed top steel corbels.
note | Standard / Specification - ALD-0424-REP - 2.5.2.9
note | Verifying Document - Hold Point Release
note | Frequency - After surveying the installed top steel corbels.
note | Activity - HP
note | By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 9 – CONSTRUCTION ACTIVITY – RAIL AND WALKWAY - 9.06 Lifting and Handling
checkpoint | 9.06.01 - Lifting Plans and Certifications
note | Acceptance / Conformance Criteria - Lifting shall be conducted by certified riggers in accordance with industry best practice using rated lifting apparatus and techniques. Where lifting chains are used, as opposed to strops, care shall be taken to guard against damage to paint work.
note | Standard / Specification - ALD-0424-REP - 2.6.3.4
note | Verifying Document - Plans and Certifications
note | Frequency - Prior to Lifting
note | Activity - R
note | By - PE
checkpoint | 9.06.02 - Finishing / Coating Repairs
note | Acceptance / Conformance Criteria - The Contractor is responsible to make good any damage (i.e., paint abrasion etc.) arising from transportation, lifting and installation.
note | Standard / Specification - ALD-0424-REP - 2.6.3.4
note | Verifying Document - Photos
note | Frequency - Each Occurrence
note | Activity - I
note | By - SE
section | SECTION 9 – CONSTRUCTION ACTIVITY – RAIL AND WALKWAY - 9.07 Rail and Assembly
checkpoint | 9.07.01 - Rail Alignment
note | Acceptance / Conformance Criteria - Rail alignment (verticality, parallelism, straightness (along assembly), rotational alignment) shall be confirmed.
note | Standard / Specification - ALD-0424-REP - 2.7
note | Verifying Document - Survey Records
note | Frequency - On completion
note | Activity - D
note | By - SV
checkpoint | 9.07.02 - Chain Position
note | Acceptance / Conformance Criteria - Chain position with respect rails shall be confirmed.
note | Standard / Specification - ALD-0424-REP - 2.7
note | Verifying Document - Survey Records
note | Frequency - On completion
note | Activity - D
note | By - SV
section | SECTION 10 – POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER) - 10.01 Site Post Construction Activities
checkpoint | 10.01.01 - Construction Record Compilation
note | Acceptance / Conformance Criteria - Compile construction records for final submission ensuring defects (NCRs) / Snags / missing records are captured or closed out, all tests have been received and passed, and changes / omissions have been noted.
note | Standard / Specification - Downer
note | Verifying Document - Records
note | Frequency - Post construction
note | Activity - H
note | By - SE
checkpoint | 10.01.02 - Survey Records
note | Acceptance / Conformance Criteria - Ensure all items have been surveyed and records are assembled for asbuilting
note | Standard / Specification - Downer P&G 20.1
note | Verifying Document - Records
note | Frequency - Post construction
note | Activity - H
note | By - SV
checkpoint | 10.01.03 - Redline Drawings
note | Acceptance / Conformance Criteria - Create a set of Redline Drawings for Asbuilt creation noting all changes and departures in red pen. Red-pen mark-up copies of the Drawings and Specifications and other design documentation showing any deviations from the specified details and requirements produced in accordance with industry good practice.
note | Standard / Specification - Downer P&G 20.1
note | Verifying Document - Redlines
note | Frequency - Post construction
note | Activity - H
note | By - PE
checkpoint | 10.01.04 - Defect, Snag and Punch List
note | Acceptance / Conformance Criteria - Update the project Defect, Snag and Punch List Register
note | Standard / Specification - Downer
note | Verifying Document - Register
note | Frequency - Post construction
note | Activity - H
note | By - PE