## Checklists
type | name | values
checklist | QA_TEM_003_Earth Electrode | .
checkpoint | Record electrode type and size (AS/NZS 3000 Table 5.2)
text | Material
text | Diameter
checkpoint | Earth electrode is driven to the minimum depth (AS/NZS 3000 5.3.6.3)
bool | Vertical type - 1.2 metres
bool | Strip type - 3 metres
checkpoint | Earth electrode is installed in a correct location (AS/NZS 3000 5.3.6.4)
label | External to the building in ground that is exposed to the weather
label | Separated from conductive enclosures of other buried services
label | Is in an accessible location
checkpoint | Earth electrode is mechanically protected and labelled in accordance with AS/NZS 3000 5.5.1.3
label | WARNING MAIN ELECTRICAL EARTHING CONDUCTOR—DO NOT DISCONNECT
checkpoint | Earth connection point to stake is protected from corrosion (i.e. painted earth clamp) (AS/NZS 3000 5.5.5.3)
checkpoint | Location of the earth electrode has been identified at the main switchboard.
checkpoint | If measurement of the resistance of the earth electrode is requested, refer to the test procedure detailed in AS/NZS 3017 clause 3.8.
checklist | QA_TEM_006_Surface Conduit Installation | .
checkpoint | Conduits are the correct type
checkpoint | Conduits are following the approved route as specified
checkpoint | Conduits are straight plumb/parallel
checkpoint | Conduits have sharp edges and burrs removed (steel)
checkpoint | Conduits have expansion joints installed where required
checkpoint | Conduits have specified support installed
checkpoint | Conduits have product branding cables removed or not visible
checkpoint | Conduits are sealed against water ingress where required
checkpoint | Conduits have equipment entries correctly sealed
checklist | QA_TEM_008_Cable Support Prior to Cabling | .
checkpoint | Cable support has correct origin and destination
checkpoint | Cable support follows correct route
checkpoint | Cable support is correct type material and not damaged
checkpoint | Cable support is correctly aligned
checkpoint | Cable support has correct type/quantity supports
checkpoint | Cable support is attached securely to supports
checkpoint | Cable support has correct type and size of fittings
checkpoint | Cable support is complete for the entirety of its length
checkpoint | Cable support has correct segregation
checkpoint | Cable support is earthed correctly
checklist | QA_TEM_009_Cable Support Post Cabling | .
checkpoint | Cable support is properly sealed at all penetrations
checkpoint | Cable support has divider strip if required
checkpoint | Cable support has cover fitted if required
checkpoint | Cable support has correct segregation
checklist | QA_TEM_010_Final Sub Circuit Installation | .
checkpoint | Cable has correct origin and destination
checkpoint | Cable has correct number of cores
checkpoint | Cable cores are of the correct cross sectional area
checkpoint | Cable type and configuration is as specified
checkpoint | Cable follows the correct route
checkpoint | Cable meets minimum bending radius requirements
checkpoint | Cable is clear of heat sources
checkpoint | Cable is clear of electronic / signal cables
checkpoint | Cable is secured as specified
checkpoint | Cable is installed in a neat and orderly manner
checkpoint | Cable is routed to minimise crossovers
checkpoint | Mechanical protection of cable is correct
checkpoint | Cable is supported correctly
checkpoint | Cable is marked with cable or circuit number
checkpoint | Cable has correct segregation
checklist | QA_TEM_011_Mains & Submains Installation | .
checkpoint | Cable is in good condition and free from damage and defects
checkpoint | Cable has correct origin and destination
text | Origin
text | Destination
checkpoint | Cable Type, Number of Cores, Size and Configuration is as specified
text | Size (mm2)
text | Cores
text | Cable Type
text | Earth Size (mm2)
text | Cores
text | Cable Type
checkpoint | Bending radius recommended by the cable manufacturer has been observed
text | Bending Radius (mm)
label | Where manufacturer’s information is not available, the following minimum internal radii may be considered suitable
label | Unarmoured sheathed cables = 6 times the cable diameter
label | Armoured sheathed cables = 12 times the cable diameter
checkpoint | Cable follows the correct route
checkpoint | Cable is clear of heat sources
checkpoint | Cable is segregated from telecommunications cables by either a continuous barrier or separated by at least 50mm - AS/NZS 3000 Clause 3.9.8.4 (c).
checkpoint | Cable is secured and mechanically protected (where required).
checkpoint | Cable is marked with cable or circuit number
checklist | QA_TEM_012_Switchboard & Distribution Board Installation | .
section | Check that the switchboard
checkpoint | Is the correct unit
checkpoint | Is located in the correct position
checkpoint | Has correct clearances on all sides
checkpoint | Is properly secured
checkpoint | Is labelled correctly
checkpoint | Is fitted with correct types, ratings and quantities of functional units
checkpoint | All escutcheons and cover plates are fitted
checkpoint | Finishes are as specified
section | Check each functional unit for
checkpoint | Correct labelling
checkpoint | Check all cable terminations are secured correctly & tensioned as per switchboard manufacturers advice
checkpoint | Check all busbar connections are secured correctly & tensioned as per switchboard manufacturers advice
checkpoint | Check cubicle has been cleaned of all rubbish, dust, filings, tools, etc.
checkpoint | Check for presence of properly completed circuit
checkpoint | Schedule/single line diagram
checklist | QA_TEM_013_Switchboard & Distribution Board Assembly | .
section | Built as per plans
checkpoint | Main Switch
text | Correct Size, Rating & Type
checkpoint | Isolators
text | Correct Size, Rating & Type
checkpoint | Circuit Breakers
text | Correct Size, Rating & Type
checkpoint | Cable Size
text | Correct Size, Rating & Type
checkpoint | CT's
text | Correct Size, Rating & Type
section | Visual Check
checkpoint | Escutcheons Fitted Correctly
checkpoint | Gland Plates Fitted Correctly
checkpoint | All Locks Fitted correctly, operation and keys incl.
checkpoint | Earth straps fitted correctly
checkpoint | Labels
bool | Main Switch
bool | Isolators
bool | Strip Labels
bool | Earthing & Neutral Bars
bool | Meters
section | Cables
checkpoint | Terminated & Tensioned
checkpoint | Neutrals - Correct terminal and number
checkpoint | Bend Radius as per AS 3000
checkpoint | Correctly Labelled
section | Testing (as per QA_FRM_005_Final Installation Test Sheet)
checkpoint | 3 ø Board @ 1000V
checkpoint | 1 ø Board @ 500V
checkpoint | Point to Point - Control Circuits
checkpoint | Correct Operation of Control Circuits
section | Cabinet
checkpoint | Correct Finish
checkpoint | Correct Size
checkpoint | Clean & damage free
checklist | QA_TEM_014_Cable Terminations | .
checkpoint | Correct type and size gland
checkpoint | Gland properly and securely fitted
checkpoint | Correct cable identification
checkpoint | Correct core identification
checkpoint | Cores loomed properly
checkpoint | Cores on correct terminals
checkpoint | Terminals properly tensioned
checkpoint | Cores correctly lugged
checkpoint | Lugs correctly insulated
checkpoint | Adequate clearances
checklist | QA_TEM_015_Accessories Installation | .
checkpoint | Accessories are the correct type
checkpoint | Accessories are located in the correct position
checkpoint | Accessories are securely fitted
checkpoint | Accessories are fitted in accordance with manufacturers recommendation
checkpoint | Accessories are plumb & level parallel
checkpoint | Accessories are sealed correctly
checklist | QA_TEM_016_Light Fitting Installation | .
checkpoint | Fitting/s are the correct type
checkpoint | Fitting/s are located in the correct position
checkpoint | Fitting/s are securely fitted
checkpoint | Fitting/s are fitted with correct lamps
checkpoint | Fitting/s accessories fitted in accordance with manufacturers recommendation
checkpoint | Fitting/s are damage free
checkpoint | Fittings/s have correct termination
checklist | QA_TEM_017_Fire Sealing | .
checkpoint | Covers are 1.6mm minimum galvanised sheet metal
checkpoint | Fire proof material is in place to comply with AS 3000 & the Building Act
checkpoint | Plastic grommet is around metal edges bearing against cable
checkpoint | Sheet metal covers are painted to match surrounds
checkpoint | Proprietary fire barriers to comply with the Building Act in lieu of above
checklist | QA_TEM_018_LCP's & Field Devices | .
checkpoint | Installation/s are the correct type
checkpoint | Installation/s are located in the correct position
checkpoint | Installation/s are properly secured
checkpoint | Installation/s are correctly labelled or identified
checkpoint | Installation/s are assembled correctly
checkpoint | Check all functions for correct operation
checkpoint | Check that the support stand or bracket is
bool | The correct type
bool | Properly secured
checkpoint | Check that all unused entries have been properly sealed against ingress of dust, solids, or liquids
checkpoint | Confirm that the whole unit/s has been installed in a workmanlike manner
checklist | QA_TEM_022_Control Cables | .
checkpoint | Type and configuration is as specified
checkpoint | has correct origin and destination
checkpoint | has correct number of cores
checkpoint | cores are of correct Cross Sectional Area
checkpoint | follows the correct route
checkpoint | meets minimum bending radius requirements
checkpoint | is clear of heat sources
checkpoint | is clear of power cables
checkpoint | is secured as specified
checkpoint | is installed in a neat and orderly manner
checkpoint | is routed to minimise crossovers
checkpoint | mechanical protection is correct
checkpoint | inter cable spacing/segregation is correct
checkpoint | cable is correctly supported
checkpoint | cable marked with cable number
checklist | QA_TEM_023_Emergency & Exit Lighting | .
checkpoint | Fitting/s are the correct type
checkpoint | Fitting/s are located in the correct position
checkpoint | Fitting/s are securely fitted
checkpoint | Fitting/s are fitted with correct lamps
checkpoint | Fitting/s accessories fitted in accordance with manufacturers recommendation
checkpoint | Fitting/s are compliant with specification
checkpoint | Fitting/s are correctly identified
checkpoint | Fittings/s are tested to AS 2293 Emergency escape lighting and exit signs for buildings
checkpoint | Log book is completed and copy on-site
checkpoint | Log book ID number and as-installed drawing/s match
checkpoint | Exit sign/s visible
checkpoint | correct operation
checklist | QA_TEM_025_Data & Communications Cabling | .
checkpoint | Check that cable to be installed matches Job Spec Requirement ie. Brand and Class
checkpoint | Check that all cable pathways comply with ACA and Vendor requirements
checkpoint | Install cables, making sure of all strain and bend radius requirements, label cables correctly
checkpoint | Bundle sizes to be checked to Specification and number of cables not exceeded
checkpoint | Cables to be tied in with Velcro as per specified distance between ties
checkpoint | All Clearances between power and other services to be maintained as per requirements
checkpoint | When cable is installed into wall cavity, Corro should be used to maintain support and bend radius
checkpoint | Corrugated conduit to be extended to outlet position if segregation is required from power in same cavity
checkpoint | Sort cables into correct Patch Panel Groups for looming into Data Cabinet/Frame
checkpoint | Loom cables into Data Cabinet being sure that they are supported properly and bend radius is correct
checkpoint | Terminate cables on Patch Panels/frames adhering to all regulations for the particular cable and Vendor
checkpoint | Label all Patch panels and Racks as required
checkpoint | Check position of outlets on Architectural plans if available
checkpoint | Terminate cables in the field as per regulations and Vendor requirements
checkpoint | Label all field outlets correctly
checkpoint | Test Cables to the relevant standards and Vendor requirements
checkpoint | Fill in record books if required, Check asbuilt plans and modify if necessary
checkpoint | Supply test results and as-installed drawing/s
checklist | QA_TEM_030_Security Inspection | .
checkpoint | Check TDCs for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Expanders for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Main Panels for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Electric Locks for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Proximity Points for correct type (T), position (P), clearances (C), & attachment (A):
bool | T
bool | P
bool | C
bool | A
checkpoint | Check Single Door Controllers for DOTL (D), Forced Doors (F), Prox operation (P), & Lock activation (L):
bool | D
bool | F
bool | P
bool | L
checkpoint | Check Two Door Controllers for DOTL (D), Forced Doors (F), Prox operation (P), & Lock activation (L):
bool | D
bool | F
bool | P
bool | L
checkpoint | Check Four Door Controllers for DOTL (D), Forced Doors (F), Prox operation (P), & Lock activation (L):
bool | D
bool | F
bool | P
bool | L
checkpoint | Check Active Panels Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check Single Door Controllers Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check Two Door Controllers Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check Four Door Controllers Timezones (T), Holidays (H), Auxilleries (AU), Automation (A):
bool | T
bool | H
bool | AU
bool | A
checkpoint | Check activation of Door Reed Switches
checkpoint | Check activation of Intruder Detectors
checkpoint | Check that all cables are the correct type, size, configuration, length & quantity
checkpoint | Visually check all terminations for correct colour codes and acceptable looming
checklist | QA_TEM_033_Control Cable Point to Point Testing | .
checkpoint | Continuity test of each & every individual core
text | Earth
text | 1
text | 2
text | 3
text | 4
text | 5
text | 6
text | 7
text | 8
text | 9
text | 10
text | 11
text | 12
text | 13
text | 14
text | 15
text | 16
text | 17
text | 18
text | 19
text | 20
checklist | QA_TEM_035_Multi-Core Point to Point Testing | .
checkpoint | Continuity test of every core
text | Earth
text | Core 1
text | Core 2
text | Core 3
text | Core 4
text | Core 5
text | Core 6
text | Core 7
text | Core 8
text | Core 9
text | Core 10
text | Core 11
text | Core 12
text | Core 13
text | Core 14
text | Core 15
text | Core 16
text | Core 17
text | Core 18
text | Core 19
text | Core 20
text | Core 21
text | Core 22
text | Core 23
text | Core 24
text | Core 25
checklist | QA_TEM_036_Power Cable Point to Point Testing | .
checkpoint | Continuity test of each & every individual core
text | Earth 1
text | Earth 2
text | Earth 3
text | Screen
text | Neutral
text | Phase A
text | Phase B
text | Phase C
checklist | QA_TEM_037_Install Field Instruments | .
section | Check that all Instruments are:
checkpoint | the correct type
checkpoint | located in the correct position
checkpoint | properly secured
checkpoint | correctly labelled or identified
checkpoint | Check that the support stand or bracket is:
bool | the correct type
bool | properly secured
section | Check that the instrument air is:
checkpoint | connected correctly to the instrument
checkpoint | connected correctly to its supply point
checkpoint | adequately secured along its length
checkpoint | Check that all unused entries have been properly sealed against the ingress of dust, solids, or liquids
checkpoint | Confirm that the whole unit has been installed in a workmanlike manner
checklist | QA_TEM_040_Multi-Core Cable Commissioning | .
section | Cable Install
checkpoint | Type, configuration, number of cores & cross sectional area is as specified
checkpoint | Cable has correct origin and destination & follows the correct route
checkpoint | Meets minimum bending radius requirements with minimal crossovers
checkpoint | Is clear of heat sources with mechanical protection fitted if required
checkpoint | Is secured properly & correctly supported as specified
checkpoint | Is installed in a neat & orderly manner with inter cable spacing/segregation
section | Origin Termination, Location
checkpoint | Gland is correct type & size, & also fitted & secured properly
checkpoint | Cable numbers fitted correctly & securely
checkpoint | Cores loomed neatly with correct identification
checkpoint | Cores in the correct terminals & correctly tensioned
checkpoint | Cores correctly lugged & insulated
section | Destination Termination, Location
checkpoint | Gland is correct type & size, & also fitted & secured properly
checkpoint | Cable numbers fitted correctly & securely
checkpoint | Cores loomed neatly with correct identification
checkpoint | Cores in the correct terminals & correctly tensioned
checkpoint | Cores correctly lugged & insulated
section | Testing
checkpoint | Point to Point, Continuity test of each core
bool | Earth
bool | Core 1
bool | Core 2
bool | Core 3
bool | Core 4
bool | Core 5
bool | Core 6
bool | Core 7
bool | Core 8
bool | Core 9
bool | Core 11
bool | Core 12
bool | Core 13
bool | Core 14
bool | Core 15
bool | Core 16
bool | Core 17
bool | Core 18
bool | Core 19
bool | Core 20
checklist | QA_TEM_042_Rough In Checklist | .
section | Inspection 1 |  | 72 Inspections available
checkpoint | Has all information been recorded and checks completed?
text | Circuit ID
text | Cable Size/Type
text | Number of Points
bool | Feeds - Visual Check - All feeds have been roughed in
bool | Feeds - Identification - All feed cables have been identified/marked
bool | 1st Rough In - Visual Check - All cable loops have been roughed in
bool | 1st Rough In - Identification - All cable loops have been identified/marked
bool | 2nd Rough In - Visual Check - All cable loops have been positioned and ready for fit off
bool | 2nd Rough In - Final Check - Ensure cable is appropriately identified and made safe, if required
checklist | QA_TEM_043_Fit Off Checklist | .
section | Inspection 1 |  | 72 Inspections available
checkpoint | Has all information been recorded and checks completed?
text | Circuit ID
text | Number of Points
bool | Fit Off - Visual Check - All points have been fit off/terminated
bool | Fit Off - Identification - Ensure cable is appropriately identified, post termination
bool | Final Check - All fit off complete, ready for switchboard termination
checklist | QA_TEM_063_Construction Distribution Boards | .
checkpoint | AS/NZS 3012:2019 - 2.3.1.1 - The distribution board is legibly and indelibly marked to identify the source of supply from which it originates. (min 6mm letters)
checkpoint | AS/NZS 3012:2019 - 2.3.1.1 - The distribution board shall be readily accessible and protected from damage.
checkpoint | AS/NZS 3012:2019 - 2.3.1.2 - The distribution board shall be positioned in a manner that eliminates the need for leads to be run between levels.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (a & b) - The distribution board is of robust construction with a minimum IP 23 rating.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (c) - Live parts are eﬀectively protected at all times against contact by personnel operating equipment located on the distribution board, including the connection or disconnection of plugs to socket-outlets.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (c) - All penetrations are closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused penetrations and pole fillers for unused circuit breaker poles.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (d) - An insulated tie bar is fitted for extension leads to prevent strain on socket/outlets.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (i) - The door or lid requires the use of tool for removal.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (ii) - The door or lid is fitted with a facility for locking.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (iii) - The door or lid shall be fitted with means of retention in the open position.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (iv) - The door or lid shall not damage leads and allow the safe entry of leads.
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (e) (v) - A clearly visible and legible sign shall be fixed on the external surface. "KEEP CLOSED - RUN ALL LEADS THROUGH BOTTOM"
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (f) - Distribution board is clearly labelled to distinguish one board from another. (by means of numbers, letters or both)
checkpoint | AS/NZS 3012:2019 - 2.3.2.1 (g) - Switchboards is marked in accordance with appendix C to indicate presence of live parts.
checkpoint | An electric shock risk sign is displayed in locations where additional attention is required in the removal of covers, e.g. covers for switchboards or cable junctions.
checkpoint | A danger sign with an additional message indicating the presence of live parts within, is conspicuously displayed on the enclosure.
checkpoint | AS/NZS 3012:2019 - 2.3.3 - Distribution board is securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
checklist | QA_TEM_041_Power Cable Commissioning | .
section | Cable Install
checkpoint | Confirm cable type, configuration, number of cores & cross sectional area is as specified
checkpoint | Confirm cable has correct origin and destination & follows the correct route
checkpoint | Confirm cable meets minimum bending radius requirements with minimal crossovers
checkpoint | Confirm cable is clear of heat sources with mechanical protection fitted if required
checkpoint | Confirm cable is secured properly & correctly supported as specified
checkpoint | Confirm cable is installed in a neat & orderly manner with inter cable spacing/segregation
section | Origin Termination / Location
checkpoint | Confirm gland is correct type & size, & also fitted & secured properly
checkpoint | Confirm cable numbers fitted correctly & securely
checkpoint | Confirm cores loomed neatly with correct identification
checkpoint | Confirm cores in the correct terminals & correctly tensioned
checkpoint | Confirm cores correctly lugged & insulated
section | Origin Termination / Location
checkpoint | Confirm gland is correct type & size, & also fitted & secured properly
checkpoint | Confirm cable numbers fitted correctly & securely
checkpoint | Confirm cores loomed neatly with correct identification
checkpoint | Confirm cores in the correct terminals & correctly tensioned
checkpoint | Confirm cores correctly lugged & insulated
section | Testing
checkpoint | Point to point / Continuity of each core
bool | Earth
bool | Red
bool | White
bool | Blue
bool | Black
checkpoint | Insulation Resistance Test (results recorded on QA_FRM_005_Final Installation Test Sheet)
checklist | Final Installation Checklist | .
checkpoint | Fit Off documentation reviewed and circuits ready for testing
NOTE: | Project Team to add pre-filled PDF to the checkpoint based on 100% IFC SLD | Q ELECTRICAL NOTE ONLY
signoff | Add Signature / Request Sign Off
checklist | QA_TEM_005_Underground Conduit Installation | .
checkpoint | Conduits are the correct type, configuration, size, quantity split and fill out
checkpoint | Conduits are the correct depth & following the correct route
checkpoint | Conduits are correctly joined
checkpoint | Layer of clean fill
checkpoint | Seal pit around conduits
checkpoint | As Built drawings completed
checkpoint | Cleaned rodded and roped
checklist | QA_TEM_007_Cast in Conduit Installation | .
checkpoint | Conduits are the correct type, size and quantity
checkpoint | Conduits are following the correct route
checkpoint | Conduits are correctly joined
checkpoint | Condutis are tied in
checkpoint | Correct concrete cover installed
checklist | QA_TEM_020(QR)_Lighting & CCTV Poles | .
section | IN-GROUND BASES (Before concrete pour)
checkpoint | Check that the excavation:
tickbox | Is in the correct location
tickbox | Has the correct length, breadth, depth
tickbox | Check that the re-inforcing materials are the correct type, size & quantity
tickbox | Check that the rag-bolt assembly is correct type and properly positioned/orientation
section | LIGHTING POLES
checkpoint | Check that the lighting pole is:
tickbox | In the correct location/orientation height
tickbox | The correct type, size and colour
tickbox | Secured/sealed correctly
checkpoint | Check that the luminaire is:
tickbox | The correct type and size
tickbox | Secured properly
tickbox | Focussed as required
tickbox | Confirm that the assembly has been installed in a workmanlike manner
tickbox | Additional accessories installed correctly
section | CCTV POLES
checkpoint | Confirm the pole has sufficient cabling pathway for Comms wiring
checkpoint | Confirm draw wires have been installed
checklist | QA_TEM_078_Cable Installation Checksheet | .
section | Inspection 1 |  | 72 Inspections available
checkpoint | Has all information been recorded and checks completed?
text | Circuit ID
text | Cable Size/Type
text | Number of Points
bool | Rough In - Feeds complete
bool | Rough In - Loops complete
bool | Rough In - All cable loops have been roughed in/identified/marked
bool | Fit Off - Field checked
bool | Fit Off - Switchboard checked
bool | Dead Testing - Complete and recorded on Final Installation Test Sheet
bool | Live Testing - Complete and recorded on Final Installation Test Sheet
bool | Layout Drawing - Checked / Marked-Up
bool | SLD & Switchboard Drawing - Checked / Marked-Up
bool | Labelling QA Complete
checklist | QA_TEM_079_Equipotential Bonding | .
checkpoint | Earthing installation as per Electrical Earthing Layout (attach drawing highlighting inspected installation)
checkpoint | Earthing networks segregated i.e., Clean Earth segregated from protective earth, intrinsically safe earth segregated from protective earth etc. (where applicable)
checkpoint | All conductors are suitably protected against mechanical damage.
checkpoint | Conductive water piping has been bonded to the earthing system (AS/NZS 3000 5.6.2.2) - (attach photographic evidence to checkpoint)
checkpoint | Conductive reinforcing within a concrete floor or wall of a room containing a shower or bath has been bonded to the earthing system (AS/NZS 3000 5.6.2.5) - (attach photographic evidence to checkpoint)
checkpoint | Swimming Pools and Spas Equipotential bonding conductor connected to the conductive pool structure, electrical equipment, conductive fixtures and fittings, and earthing conductors associated with each circuit supplying the pool or spa (AS/NZS 3000 5.6.2.6) - (attach photographic evidence to checkpoint)
checkpoint | If the telephone and telecommunication earthing system is directly connected to the electrical installation earthing system, the requirements of AS/NZS 3000 5.6.2.7 have been met and the Communications Earth Terminal (CET) is labeled "COMMUNICATIONS EARTH TERMINAL".
checkpoint | Continuity of the earthing system meets the requirements of AS/NZS 3000 8.3.5. Resistance of the main earthing conductor or any equipotential bonding conductor is not more than 0.5 Ω. (attach drawing identifying Test Points & record results below)
checkpoint | Equipotential bonding requirements as listed in AS/NZS 3000 5.6.2.1 have been completed
checkpoint | No.1 | x 10 | Will advise on projects if more required, this should cover as a maximum
text | Test Point (No.) From
text | Test Point (No.) To
text | Ohms
checklist | QA_TEM_081_Cable Pit Installation | .
checkpoint | Confirm the completion of QA-TEM_004_Trench and Backfill (all tasks prior to backfilling) has not raised any non-conformances. Photograph trench showing correct depth.
checkpoint | Confirm drainage requirements of pits
checkpoint | Check that the pit is:
tickbox | The correct type, configuration, size, quantity of access holes
tickbox | Correct depth & following the correct route
tickbox | Correctly joined with conduits
signoff | Hold Point - All above must be completed before further works proceed
checkpoint | Photograph trench detail showing correct installation method. Photograph trench showing 150mm Sand covering all conduits and installation of detectable marking tape.
checkpoint | Seal pit around conduits
checkpoint | As Built drawings completed
checkpoint | Conduits are cleaned, rodded and roped
signoff | Hold Point - All above must be recorded and signed off
checklist | QA_TEM_029_Lightning Protection | .
checkpoint | Check test electrodes have been installed
checkpoint | Check down conductors during construction
checkpoint | Check bonding to exposed metal on roof
checkpoint | Check system terminations
checkpoint | Is system fixed securely
checkpoint | Continuity test for system completed
checkpoint | Check air terminations
checkpoint | Nominate size of bonding strap and record
checklist | QA_TEM_004_Trench and Backfill | .
checkpoint | Prior to excavation:
text | Stage / Section location
tickbox | Mark out route as per electrical services drawings
tickbox | Potholing/Service Locations - mark-up all documentation identifying any service clashes Co-ordinate with other trades i.e. civil, hydraulic, comms Route and dimensions agreed with Principal Contractor
checkpoint | Obtain excavation permit from Principal Contractor
signoff | Hold Point - All above must be completed before further works proceed
checkpoint | During excavation:
tickbox | Confirm signs / safety barriers in place
tickbox | Confirm trenching is correct - Size / Alignment / Depth (Use Datum Points)
checkpoint | Prior to backfilling: Confirm the completion of QA_TEM_005_Underground Conduit Installation has not raised any non-conformances Confirm suitability of proposed backfill Check compaction and frequency requirements Confirm layers being replaced i.e., geotextile fabric, road base, general fill
signoff | Hold Point - All above must be completed before further works proceed
checkpoint | During and after backfilling, check that:
tickbox | Cable marker tape is correct (Type & Depth)
tickbox | Survey points for as built documentation has been completed
tickbox | Route markers installed
tickbox | Compaction is correct - refer to specification
tickbox | Route markers are correct
tickbox | Soil is properly removed
tickbox | Cable protection installed
checkpoint | On completion:
tickbox | Layer clean fill
tickbox | Co-ordinate compaction tests as required with Principal Contractor
tickbox | Surface reinstatement to agreed standard
checklist | QA_TEM_080_Room Body Protection Checklist | .
section | Room Body Protection Checklist details
text | Room #
text | Drawing Reference
text | Drawing Revision
button | Activity | Rough In, Fit Off
section | Item #1
checkpoint | Light Switch installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
checkpoint | Item #2
checkpoint | RCD installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
checkpoint | Item #3
checkpoint | Socket-outlet installed in ceiling
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
checkpoint | Item #4
checkpoint | Normal Supply Socket-outlet (White) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #5
checkpoint | Essential Supply Socket-outlet (Red) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #6
checkpoint | UPS Socket-outlet (Dark Blue) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #7
checkpoint | “Cleaning Purposes Only” Socket-outlet (Beige) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #8
checkpoint | Normal Supply Double Socket-outlet (White) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #9
checkpoint | Essential Supply Double Socket-outlet (Red) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #10
checkpoint | UPS Double Socket-outlet (Dark Blue) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
section | Item #11
checkpoint | Medical Services Panel installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checkpoint | Installed in compliance with AS/NZS 3003
checklist | QA_TEM_082_Room Checklist | .
section | Room Checklist details
text | Room #
text | Drawing Reference
text | Drawing Revision
button | Activity | Rough In, Fit Off
section | Item #1
checkpoint | Light Switch installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #2
checkpoint | RCD installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #3
checkpoint | Socket-outlet installed in ceiling
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #4
checkpoint | Non-essential Supply Socket-outlet (White) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #5
checkpoint | Essential Supply Socket-outlet (Red) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #6
checkpoint | UPS Socket-outlet (Dark Blue) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #7
checkpoint | “Cleaning Purposes Only” Socket-outlet (Beige) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #8
checkpoint | Non-essential Supply Double Socket-outlet (White) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #9
checkpoint | Essential Supply Double Socket-outlet (Red) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
section | Item #10
checkpoint | UPS Double Socket-outlet (Dark Blue) installed
checkpoint | Installed at correct RL
checkpoint | Installed in compliance with architectural drawing/s
checklist | QA_TEM_061_Construction Lighting | .
checkpoint | Check Light fittings are securely fitted
checkpoint | Check Emergency Exit signs visible and clear from obstructions
checkpoint | AS3012:2019 - 2.7.1 - Ensure minimum lighting levels are at least 40 lx for walkways and 160 lx for general areas, lunch rooms and site offices. Record results on layout drawing and attach to this ITC
text | Record Drawing Reference:
checkpoint | AS3012:2019 - 2.7.2 - Light fittings are the correct type for the application and are protected against Mechanical damage
checkpoint | AS3012:2019 - 2.7.3.1 - Emergency lighting is provided in designated access and egress paths
checkpoint | AS3012:2019 - 2.7.3.1 - Emergency lighting is provided directly above and in front of switchboards (if natural lighting unavailable)
checkpoint | AS3012:2019 - 2.7.3.1 Complete fields for one of the following : Item (a) or Item (b) below
tickbox | a) An average of 20 lx at 900 mm above floor level along the centre line of the corridor containing the emergency luminaires has been achieved Record results on layout drawing and attach to this ITC
tickbox | b) Emergency lighting has been installed using luminaires complying with AS2293.3:2018 luminaire classification and the mounting height and spacing, as specified in AS3012:2018 Tables 2,3,4 and 5.
text | EM Light Type or Model No.
text | Fitting Classification
text | Table No.
text | Mounting Height
text | Max Spacing between fittings (C 90, C 0)
checkpoint | AS3012:2019 - 2.7.3.1 - Emergency lighting levels are maintained for at least 60 mins following loss of normal lighting in the area.
checkpoint | Log book is completed and copy on-site
checkpoint | Emergency light fittings are correctly identified in line with log book
checklist | QA_TEM_062_Construction Main Switchboards | .
checkpoint | AS 3012:2019 - 2.3.1.1 - Switchboard is legibly and indelibly marked to identify the source of supply from which it originates. (min 6mm letters)
checkpoint | AS 3012:2019 - 2.3.1.1 - The switchboard shall be readily accessible and protected from damage
checkpoint | AS 3012:2019 - 2.3.2.1 (a & b) - The switchboard shall be of robust construction with a minimum IP 23 rating
checkpoint | AS 3012:2019 - 2.3.2.1 (c) - Live parts are eﬀectively protected at all times against contact by personnel operating equipment located on the switchboard, including the connection or disconnection of plugs to socket-outlets.
checkpoint | AS 3012:2019 - 2.3.2.1 (c) - All penetrations are closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused penetrations and pole fillers for unused circuit breaker poles
checkpoint | AS 3012:2019 - 2.3.2.1 (e) (i) - The door or lid requires the use of tool for removal
checkpoint | AS 3012:2019 - 2.3.2.1 (e) (ii) - The door or lid is fitted with a facility for locking
checkpoint | AS 3012:2019 - 2.3.2.1 (f) - Switchboard is clearly labelled to distinguish one board from another. (by means of numbers, letters or both)
checkpoint | AS 3012:2019 - 2.3.2.1 (g) - Switchboards is marked in accordance with appendix C to indicate presence of live parts
checkpoint | An electric shock risk sign is displayed in locations where additional attention is required in the removal of covers, e.g. covers for switchboards or cable junctions
checkpoint | A danger sign with an additional message indicating the presence of live parts within, is conspicuously displayed on the enclosure
checkpoint | AS 3012:2019 - 2.3.3 - Switchboard is securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
checkpoint | AS 3012:2019 - 2.4.1 - Switchboard has one isolation switch marked in accordance with clause 2.4.3. (6mm Text) ‘MAIN SWITCH’ and confirm switch interrupts supply to all downstream circuits
checkpoint | AS 3012:2019 - 2.4.2 - Isolating switches are lockable or located within a lockable enclosure
checkpoint | Current single line drawing is readily available within the switchboard
checkpoint | Switchboards have signage attached with correct Q Electrical site contact details
checkpoint | Switchboards have up to date schedules and are correctly labelled
checkpoint | All conduit entries into Switchboard have adaptors fitted and glued
checkpoint | All cables are correctly glanded into the switchboard
checkpoint | All spare penetrations are eﬀectively sealed by use of a propriety fitting e.g. screwed bung and lock ring
checkpoint | Check cubicle has been cleaned of all rubbish, dust, filings, tools, etc
checkpoint | Check all cable terminations and Bus bar connections are secured correctly & tensioned: (Attach reference documents)
text | Item or Part
text | Torque Setting
checklist | QA_TEM_064_Construction Wiring & Accessories | .
checkpoint | Check that the accessories are the correct type
text | Reference Document:
checkpoint | Check that the accessories are located in the correct position
text | Reference Document:
checkpoint | Are securely fitted and field equipment and cabling is clearly labelled
checkpoint | Are fitted in accordance with manufacturers recommendation :
checkpoint | AS 3012:2019 - 2.5.2 - Check wiring is not tied, bundled or grouped with permanent wiring; nor attached to free-standing fencing.
checkpoint | AS 3012:2019 - 2.5.3 - Check wiring is mechanically protected in accordance with previously conducted risk assessment. (QA_TEM_057_Construction Wiring Risk Assessment) Or not less than; (a) medium duty rigid or corrugated conduit of insulating material; (b) heavy-duty rigid or corrugated conduit of insulating material; (c) flexible electrical hose; (d) armoured cable; or (e) other means that provide equivalent protection against mechanical damage.
checkpoint | AS 3012:2019 - 2.5.4 - Construction wiring is readily distinguishable from permanent wiring by using cable sheath of a diﬀerent colour or by attaching iridescent yellow tape spaced at intervals not exceeding 5m and marked with the words "CONSTRUCTION WIRING"
checkpoint | AS 3012:2019 - 2.5.4 - If live permanent wiring is located where construction wiring is occurring, or its location, check that it be marked with the words "LIVE WIRING" at interval not exceeding 5m.
checkpoint | Confirm all Field wiring to Isolators, Socket outlets and point off supply has been terminated correctly
checklist | QA_TEM_020_Lighting Poles | .
section | IN-GROUND BASES (Before concrete pour)
checkpoint | Check that the excavation:
tickbox | Is in the correct location
tickbox | Has the correct length, breadth, depth
tickbox | Check that the re-inforcing materials are the correct type, size & quantity
tickbox | Check that the rag-bolt assembly is correct type and properly positioned/orientation
section | LIGHTING POLES
checkpoint | Check that the lighting pole is:
tickbox | In the correct location/orientation height
tickbox | The correct type, size and colour
tickbox | Secured/sealed correctly
checkpoint | Check that the luminaire is:
tickbox | The correct type and size
tickbox | Secured properly
tickbox | Focussed as required
tickbox | Confirm that the assembly has been installed in a workmanlike manner
tickbox | Additional accessories installed correctly
checklist | QA_TEM_058_Construction Wiring Checklist | .
checkpoint | AS/NZS 3012:2019 - Construction Wiring Checklist
text | Building # / Area / Distribution Board:
date | Date:
signoff | Signature:
checkpoint | 2.3.1.1 - Switchboard is legibly and indelibly marked to identify the source of supply from which it originates
checkpoint | 2.3.1.1 - The switchboard shall be readily accessible and protected from damage
checkpoint | 2.3.1.2 - The switchboard shall be positioned in a manner that eliminates the need for leads to be run between levels
checkpoint | 2.3.2.1 (a & b) - The switchboard shall be of robust construction with a minimum IP 23 rating
checkpoint | 2.3.2.1 (c) - Live parts shall be eﬀectively protected at all times against contact by personnel operating equipment located on the switchboard, including the connection or disconnection of plugs to socket-outlets. (All penetrations MUST be closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused holes in the bottom of the board, pole fillers and all covers to outlets).
checkpoint | 2.3.2.1 (d) - An insulated tie bar shall be fitted for extension leads to prevent strain on socket/outlets.
checkpoint | 2.3.2.1 (e) (i) - The door or lid shall require the use of tool for removal.
checkpoint | 2.3.2.1 (e) (ii) - The door or lid shall be fitted with a facility for locking.
checkpoint | 2.3.2.1 (e) (iii) - The door or lid shall be fitted with means of retention in the open position.
checkpoint | 2.3.2.1 (e) (iv) - The door or lid shall not damage leads and allow the safe entry of leads.
checkpoint | 2.3.2.1 (e) (v) - A clearly visible and legible sign shall be fixed on the external surface. KEEP CLOSED - RUN ALL LEADS THROUGH BOTTOM.
checkpoint | 2.3.2.1 (f) - Where there is more than one switchboard on the site, markings shall distinguish one board from another. (by means of numbers, letters or both)
checkpoint | 2.3.2.1 (g) - Switchboards shall be marked in accordance with appendix C to indicate presence of live parts.
checkpoint-no-status | NOTE: Locking covers required for CB's and RCD's, but not isolation switches - this is generally a state or client based requirement aimed at controlling the resetting of breakers and RCD's
checkpoint | 2.3.3 - Switchboards SHALL be securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
checkpoint | 2.3.5 - At each switchboard, a fixed secure and stable means shall be provided to support cables entering switchboards e.g. cross arm covered in non-conductive material.
checkpoint | 2.4.1 - Each switchboard SHALL be provided with one isolation switch marked in accordance with clause 2.4.3. This switch shall interrupt supply to all downstream circuits including outlets mounted on the switchboard.
checkpoint | 2.4.2 - Isolating switches SHALL be lockable or located within a lockable enclosure
checkpoint | 2.4.3 (a) - All isolating switched shall be marked - MAIN SWITCH - on main switchboards (min 6mm letters)
checkpoint | 2.4.3 (b) - All isolating switched SHALL be marked - DISTRIBUTION BOARD ISOLATING SWITCH - on distribution boards (min 6mm letters)
checkpoint | 2.5.2 (a & b) - Construction wiring shall not be tied, bundled or grouped with permanent wiring, and shall not be attached to free standing fencing.
checkpoint | 2.5.4 - Construction wiring shall be readily distinguishable from permanent wiring by using cable sheath of a diﬀerent colour or by attaching iridescent yellow tape spaced at intervals not exceeding 5m and marked with the words "CONSTRUCTION WIRING"
checkpoint | 2.5.4 - If live permanent wiring is located where construction wiring is occurring, or its location, then it SHALL be marked with the words "LIVE WIRING" at interval not exceeding 5m. Live permanent wiring SHALL be readily distinguishable from construction wiring. NOTE: Unidentified wiring is to be deemed LIVE.
checkpoint | 2.7.3.1 - Emergency lighting SHALL be provided in designated access and egress paths and directly above and in front of switchboards, (where the general lighting cannot be met using natural lighting)
checkpoint | 2.7.3.1 - NOTE: Requirement to prevent unauthorised disconnection of emergency lighting that has detachable connections (i.e. hard wired for Low Voltage). ELV control boxes to be hard hardwired at construction distribution boards.
checkpoint | Current single line drawing is readily available
checkpoint | Switchboards have signage attached with correct Q Electrical site contact details
checkpoint | All Conduits MUST have adaptors fitted and glued
checkpoint | All cables MUST have glands fitted
checkpoint | All penetrations MUST be eﬀectively sealed by use of a propriety fitting e.g. screwed bung and lock ring.
checkpoint | Table 6 - RCD's - Push button test by user - Non portable fixed - frequency monthly. (Note the RCD count in comments)
checkpoint | 2.5.3 Risk assessment should be conducted prior to the installation of cables or whenever a change occurs, as to the likelihood of any cables being exposed to mechanical damage.

## QES CONQA Admin note
**For any changes to the Checklists include the following comment in your email notification
Please ensure this change is made across all current QES CONQA Projects