## Resources
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | OSD |  | OSD | 013692fd-9905-4916-98b9-38ac9ecbd392
| section | Pre-Commencement
| checkpoint | WorkSafe notification before trenching below 1.5m deep has been submitted
5a7e9c2c-b35e-5a54-8e44-a6b711ffb039 | button | If required, trench shields are on site & ready for use | Yes, No
56bdae12-f1f6-52d1-bad0-8db11a8cbbae | button | Dig Permit completed by contractor & attached | Yes, No
0750a659-742b-5462-9fdb-6b4b0b626ad9 | button | Exclusion Zones have been erected as required (Attach photos below) | Yes, No
| checkpoint | Existing in-ground services located and verified before excavation
| section | Detail excavation
| checkpoint | Excavation depths & locations confirmed prior to detailed excavation commencing
| checkpoint | Any services (overhead / below ground) considered & isolated where required before excavation commences
| checkpoint | Approval given to contractor to commence detail excavation
| checkpoint | Excavation measurements align with drawings
5173e16e-7ac8-5fac-bef8-33f2b648b704 | tickbox | Depth, Width & Length correct
| checkpoint | Excavation works - completed to specification/drawings & Area left clean/tidy
fce3eef4-b550-5f62-a3e4-d2aaececf7ae | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| section | Tanks/ Pumps / Chambers/ Grease arrestor Installation
| checkpoint | Bedding material- correct type, grade and depth installed to support service
| checkpoint | Product delivered is in good condition and correct as per specifications
| checkpoint | Tanks/Pumps/Chambers/Grease arrestor Installed in the correct location and required depth
6a13fc4f-d8bf-5b40-a947-1e34c36a4d24 | tickbox | Items are correctly sealed
| checkpoint | Conduits installed - Provide photos
3cbd4db9-f3fc-51d7-b092-86bd79513b31 | tickbox | Cables pulled through conduit
| checkpoint | Installation 100% Completed - All final checks, documentation completed & attached - (Attach photos below)
8b858392-40c7-551c-a9fe-4ab9e6a5b896 | note | FINAL - Pass when work(s) are completed (Any issues please comment below)
| section | Backfill
| checkpoint | Tanks/ Pumps / Chambers/ Grease arrestor covered and made safe
ebf1a9d6-46a5-59a9-b85e-92aa4e45d554 | tickbox | Trench suitably backfilled and compacted
| checkpoint | Expansion lagging installed around pipes before concrete - If applicable
| checkpoint | Rissers lagging has been installed - If applicable
| checkpoint | HOLD POINT - Subcontractor QA Reviewed (Comment issues below)
583288c3-4f40-53a0-b186-ada483928363 | tickbox | Test completed by contractor and confirmed to Ryman
bd00fff1-7816-536c-bd19-8245ddbc7c79 | note | Once reviewed & approved - Please attach (if applicable)
| checkpoint | Works 100% completed to specification/drawings & Area left clean/tidy
a766c5ff-f386-592c-a355-c5af4ff394eb | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checklist | Stormwater Tanks Waterproofing (Balconies) |  | Stormwater Tanks Waterproofing | 05cd176e-6d53-4612-a1a6-56932ee0205b
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
aff3360d-5afc-572e-9dc7-dec2972c05a1 | note | Attach relevant photos
0ae70f61-c945-5574-a03d-2d2f4ef4696f | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
6ffc7e1f-bd0e-55a9-99a4-6a8505b32023 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
cc805a4e-be85-5a5d-ae9c-94324e006fa5 | tickbox | Ensure no high points or crevices are in the substrate
e39dea88-cff2-5dc2-9634-302208f3f33e | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
1e901be4-3ccc-56df-b718-e33f5b60fcf1 | note | Attach relevant photos
| checkpoint | Seal all joints and penetrations with Polybit HydraFlex FC polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
751c0522-a8c1-59c7-b01b-c3673870a3a9 | note | Attach relevant photos
| checkpoint | Dampen the surface to ensure the highest level of adhesion as required
8196a969-e72c-5636-bc0a-9ec2d48c1340 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
c7255ab6-6338-5636-b982-63985cb532f9 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
b6df9975-b617-53c4-b26c-203e16813ced | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
f7bc2bcb-c8bf-5c60-8b4e-9df45832502f | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
f20110b4-dc90-5576-bbc2-9ff0367ffb6e | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
57286a81-3d3e-5c56-bda8-076e2b411488 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Fire Sprinkler Tanks Waterproofing (Balconies) |  | Fire Sprinkler Tanks Waterproofing | 061d3687-c506-43b5-955d-188c644cf86a
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
913cb6cc-eadc-5bcc-982b-4be458bc2a53 | note | Attach relevant photos
1d96805f-87db-54eb-8107-195f4048a026 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
e53627d2-338b-5ada-8852-a00cc7046fa5 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
cf5a4848-8434-53a3-9e23-9353b851fd59 | tickbox | Ensure no high points or crevices are in the substrate
aced4f56-2d2b-588f-ab6d-ace1237c0bcb | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Fatra Fatrafol 807 PVC membrane to be used. - Apply selected membrane as per datasheet & application guidelines
8e63f652-88e4-54d2-9c58-185a1273a89f | note | Attach relevant photos
| checkpoint | Inspect for any remaining leaks and treat with HydraPlug - Apply selected sealant as per datasheet & application guidelines
108b58fb-c228-5482-916b-ee944c72f324 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
5f933494-ad61-5ed8-825a-90285b0bb71d | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
dbe44332-ff41-506b-add6-d588196c6f78 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
4416372d-f176-5c12-8def-55792cbe2124 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | MSB & Comms Room |  | MSB & Comms Room | 0752a92b-0526-4bf4-afb8-dae0bdcc1ac0
| checkpoint | Switchboards in place using suitable fixings to match mounting service No damage to external board has occurred during installation
d4be639a-ce7d-5e44-8955-7ff2d91045e3 | button | Ensure adequate pathways exist within board to accommodate all circuits and allow for future expansion | Yes, No
9c52e8ad-29ed-510a-9c09-25e92ed5d470 | button | Install and loom in all circuits into correct cabinets | Yes, No
21de70e1-e081-5fba-a84f-4446579755c1 | button | Ensure cable labels match switchboard schedule and construction drawings | Yes, No
03b36014-3ff5-59c4-8800-8124186f05e9 | button | Cables are labelled as per specified requirements | Yes, No
51b8f865-aa3e-5c09-9858-7d78f3c41f91 | button | Check all tightness of all terminals on all breakers and bars | Yes, No
ff9d13f6-6831-5a8a-b065-21a0927b637c | button | Ensure safety signage is installed and visible as per plans | Yes, No
| checkpoint | Ensure all comms has been tested & commissioned
| checkpoint | Ensure ventilation and exhaust fans are installed as per plans
| checkpoint | Ensure FCU's (if required) are installed, tested & commissioned to provide sufficient cooling within MSB & Comms room
| checkpoint | Final sign off - MSB & Comms room equipment installed as per the above ITP - Add general photos/comments below
74535d43-4a16-500c-8be0-be991953b9e4 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Caretaker Toilet |  | Caretaker Toilet | 07a65704-7003-417c-bee2-29d5af155cd2
| checkpoint | Floor wastes checked - Any issues comment/photo below
| checkpoint | All rough-in pipework is colour coded to ensure no cross connections
| checkpoint | All poly pipes located in framing to ensure no screw fixings will penetrate them
ebb3de1c-aa8f-55e3-8c02-fbfdc056dd48 | note | Any pipe running through a wall must be at 90 degrees
| checkpoint | All Water & Gas risers are complete
| checkpoint | All stacks are level/plumb
| checkpoint | Ensure all services that go through fire rated walls to be treated with collars/fire rated sealant
| checkpoint | Ensure rough in has been done as per specs
| checkpoint | Final sign off - All plumbing work completed as per the above ITP - Add general photos/comments below
b6ac658c-e57c-5abd-98c0-da76e1424a59 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Stormwater Tanks Waterproofing |  | Stormwater Tanks Waterproofing | 0b35f397-3b55-41c6-b9ba-41d365b05e1c
| checkpoint | Area barricaded off to allow no access with signs posted/ visible to include date of application, "No access waterproofing work in progress"
664a9ace-bfb6-5619-9011-b9bbfcc11717 | note | Attach relevant photos
5e8b4b62-c0be-5250-bb12-ed391dc96409 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
5c3ad098-deb1-5b3b-97d9-c69b45d0f99f | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
5149752a-770f-545a-a150-4bca7d51fa72 | tickbox | Ensure no high points or crevices are in the substrate
0f785bd3-ea47-5b28-aa2f-cae27bf52d85 | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
1d5fb49f-d0f9-5bc0-9bd7-3ddecb2ed023 | note | Attach relevant photos
| checkpoint | Seal all joints and penetrations with Polybit HydraFlex FC polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
06f5e80a-8fd9-5e55-9e13-788a0cf67848 | note | Attach relevant photos
| checkpoint | Dampen the surface to ensure the highest level of adhesion as required
4b2164b0-84c2-5a68-90d5-06709be853c9 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
049c0492-05b3-5a06-b393-1ae81e9553b9 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
6a0251fd-20b8-5374-a95f-d2f0b91cfd19 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
1a76619d-753a-51d0-8140-03981639d717 | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
a61b653d-31ac-5f6a-96f4-61ff88dfef81 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
5f92f659-d40a-5379-ad0d-709f1ed2c62d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | External Facade |  | External Facade | 0c709b76-1a2b-41fd-9787-c13119fa8c67
| section | Hebel Work
| checkpoint | Ensure hebel installed plumb & level with adjoining surfaces
| checkpoint | Ensure gap between hebel & concrete 10‐15mm (max) & consistent
| checkpoint | Ensure hebel panels are in full & not cracked
| checkpoint | Final sign off - All hebel work completed as per the above ITP
| section | Render Work
| checkpoint | Ensure to use right dulux product & system as per specification & scope of works
| checkpoint | Expansion cuts are consistent up & down & to substrate & also same cut thickness
| checkpoint | Ensure surfaces flat & level & free of imperfections
| checkpoint | Once render applied ‐ render allowed to sufficiently dry before primer coat
| checkpoint | Primer Coat ‐ even consistent coverage on render
| checkpoint | Membrane Texture Coat ‐ consistent coverage & texture, no roller marks, consistent sheen level
| checkpoint | Paint thickness test to be carried out & report to be crossed checked DGain Alands external render & paint specification schedule
| checkpoint | Final sign off - All render work completed as per the above ITP
ee7f00bd-97f4-5b46-80aa-5b9d852a6506 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | SOG |  | SOG | 0c8d4602-fc8c-4a71-9af8-67809f562211
| section | Prior to Concrete Pour
| checkpoint | Materials used complies with design documentation
| checkpoint | Datum point used & soffit RLs checked
| checkpoint | Grids marked by builder
| checkpoint | Confirm As-Built Survey of deck is complete
b3364fbd-3f18-562c-aa79-415e9114a171 | note | HOLD POINT - Attach As-Built Survey of Deck
| checkpoint | Confirm Form Worker has received As-Built Survey of deck, and has rectified errors prior to any trades commencing on deck
| checkpoint | Confirm all beams and decks constructed as per Structural Concrete Profiles
| checkpoint | Install slip joints to all load bearing walls and corbels where required
| checkpoint | Clean off decks and beams prior to pour, and ensure all exposed off-form soffits are free of any dust, stains and rust marks Hose down if necessary
| checkpoint | Check if concrete has falls, and ensure shutters, timbers, spacers are used to create folds where necessary Cross-check the following drawings
297e3be6-799b-5f3a-8dca-3204f3af8b56 | tickbox | Hydraulic Drawings
e39b8584-0f61-5f17-9796-0bbb9a33abf5 | tickbox | Architectural Concrete Outlines
6114161b-231e-5593-92ce-88a22f149700 | tickbox | Structural Drawings
| checkpoint | Check top RLs for all reinforcement, ensuring adequate concrete cover Confirm with Concreter
| checkpoint | Confirm that plastic bar chairs are used everywhere, particularly at exposed off-form soffits
| checkpoint | Attach Formwork ITP
| checkpoint | Attach Formwork Engineer sign off certificate Confirm that certificate references props, braces and compliance with design & AS3610
ec9aa51d-c8a5-5c1f-873c-b65f8d68fbd7 | note | Attach Formwork Engineer's Certificate
| checkpoint | Attach ALL Services Hydraulic ITP (for cast-in elements), include relevant mark-ups below
| checkpoint | Attach Precast ITP (for cast-in elements), including relevant mark-ups
| checkpoint | Attach Reo Fixing ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
0f91e2c9-1d4a-58e7-be21-02695ecc7e60 | note | Attached below as applicable
| checkpoint | Attach Post Tensioning Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
7d15ea9a-e9ea-545f-aafa-be0ca343296a | note | Attached below as applicable
| checkpoint | Check quantity of concrete required prior to ordering
5c197992-9f4a-5427-8f02-e218f1131b14 | textbox | Total m3 (as measured by Site Engineer)
16a3b67d-52f5-509b-aa70-4335befe92bd | textbox | Total m3 (as measured by Foreman)
| checkpoint | Confirm MPa, slump and agg size of concrete prior to ordering
4aaa9c9a-6ced-5d27-971e-0aa3ab173393 | textbox | MPa
b832f6d8-e4fd-5baf-bc67-51ce18a2acb0 | textbox | Slump
6de0347b-48b0-5c1f-97a9-b86ee455862e | textbox | Agg
| section | During to Concrete Pour
| checkpoint | Ensure concrete truck dockets have correct concrete strength, and attach delivery docket from each batch
| checkpoint | Confirm concrete has falls to drainage points in slab
| checkpoint | Ensure a representative from each of the following is on site and witnessing the pour
a9d5e0ec-09e1-5d32-a55b-fb6234599277 | tickbox | Formworker
edaa353b-1d2c-52ed-a4b8-9b74a38ed865 | tickbox | Electrician
80e334eb-f243-5744-aa91-6ecc1ab131bc | tickbox | Plumber
903dfbed-b0f1-57c6-b9b6-01b46b9cb848 | tickbox | Post Tensioner
15c8b553-5291-5d74-8828-13040f01d028 | tickbox | Precast Installer
| checkpoint | Confirm Form Worker has labour below deck inspecting all joints (particularly at columns & walls) and is immediately cleaning any slurry
| checkpoint | Confirm that all protection to precast panels is maintained at all times during concrete pour
| section | After Concrete Pour
| checkpoint | Confirm Surveyor is out next day to carry out survey of finished concrete Attach As built Survey Plan
7d21f71a-0daa-5524-8205-b7e5dd4aecb0 | note | Attached below as applicable
| checkpoint | Confirm tolerance of finished concrete surfaces are in accordance with the specifications
| checkpoint | Confirm saw joints are installed to engineers requirements
| checkpoint | Confirm finish of concrete is adequate for application (broom/trowel/helicopter finish), refer to AS3610
| checkpoint | Obtain all concrete tests at 1 day, and attach test results
372ebef1-25ef-595b-801e-7e023216e2bb | textbox | Test Strength Mpa
| checkpoint | Confirm initial stress is conducted day after the pour, after concrete has reached 10 MPa on 1 Day results
| checkpoint | Obtain all concrete tests at 4 day, and attach test results
f620b6af-179a-5122-9965-dea657511d2f | textbox | Test Strength Mpa
| checkpoint | Confirm final stress has occurred after concrete has reached 22MPa, and attach Stressing Records
a497fb62-2c2b-5ea5-9488-5bbbd04f41d6 | note | Attached below as applicable
| checkpoint | Obtain all concrete tests at 7 day, and attach test results
b432e8fe-26ec-5ded-b698-74a822465ad4 | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 28 day, and attach test results
a4dfaf86-97f4-5e8b-9be8-d666c794de78 | textbox | Test Strength Mpa
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
d4c19b4a-1b23-5822-b45b-af9899f038c3 | button | Subcontractor Sign Off | Yes, No, N/A
f4861301-32f8-58ba-afbb-93fe72c795ca | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Storage Lockers |  | Storage Lockers | 1176202c-0069-4871-aab9-10001b9f83e3
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
873e0403-863f-5cc6-8088-760503dafbdf | textbox | Drawing & revision number(s)
| checkpoint | Storage lockers installed to manufacturers instructions & standards
| checkpoint | Final sign off - All storage lockers installed as per the above ITP - Add general photos/comments below
be598164-569c-5fb2-bd26-0439cbfdf4b0 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Mechanical Rough In |  | Mechanical Rough In | 16eb636f-6518-4dba-95c2-49d0ac31cc9e
| checkpoint | All aircon has been roughed in & tested
| checkpoint | All aircon vents are in correct spot
| checkpoint | All service risers have been installed
| checkpoint | Ensure all ducting sealed & sparged
| checkpoint | All services that go through fire rated walls to be treated with collars/fire rated sealant
240481b8-13d3-5373-9eab-066ca65ed6f2 | note | Relevant photo's/register has been completed
| checkpoint | Duct work to be tear free & sealed prior to cleaning
| checkpoint | Final sign off - All mechanical work completed as per the above ITP
f29db86f-ff9b-5988-b805-fb1e1905209d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Ground Beams |  | Ground Beams | 18f67b16-8153-4088-a970-aa0edb23cf45
| checkpoint | Any services (overhead/below ground) considered & isolated if required before excavation commences
| checkpoint | Approval given to commence detailed excavation - depths and locations confirmed prior commencement
fe7de80f-426e-57ff-82e6-eac01c249ac6 | button | Footing RL Confirmed | Yes, No, N/A
417009cc-242b-52fe-8ddb-3bc0105d4b43 | button | Any services (overhead / below ground) considered and isolated where required before excavation commences | Yes, No, N/A
291f93f8-3279-5262-a75d-e9f886a7c51e | button | Approval given to commence detailed excavation | Yes, No, N/A
95ce6804-7ddb-59d0-ad20-96f90da819af | button | Excavation checked, correct and approved | Yes, No, N/A
ffcde1b6-2374-5c3a-8c2f-886bbf2e1ef2 | button | Depth correct (allow for site concrete if required) | Yes, No, N/A
ea001ac2-23bd-5749-8961-87a02b1b3003 | button | Width correct (allow for boxing if required) | Yes, No, N/A
| checkpoint | Formwork correctly Installed
2c596942-1b0d-540b-8288-b89331dcac4e | button | Set out - correct levels | Yes, No, N/A
053a6b29-9d05-53a9-953f-38f8a71ae35d | button | Inserts, pockets, fixings, rebates etc | Yes, No, N/A
0c3c0a2a-b1ee-59ca-ad59-98d9e770541e | button | Bracing, Fixing Propping & Supports | Yes, No, N/A
| checkpoint | Reinforcement installed as per plan including cover & chairs
fec4bb5a-faae-5091-87eb-f6f12e2ede45 | button | Reo spacing & grade as per specifications | Yes, No, N/A
9eef224b-0c81-5e02-8c7a-8ee6c0ec515d | button | Starter bars, dowel bars, & mesh installed as per specifications | Yes, No, N/A
| checkpoint | Concrete strength/ Slump confirmed
| checkpoint | Any waterproofing elements have been correctly installed and checked
| checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
| checkpoint | Final sign off - All ground beams completed as per the above ITP - Add general photos/comments below
61d13879-f6cd-521d-8f47-0fd3464234c3 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Capping Beam (V140421) |  | Capping Beam (V140421) | 19809baa-ed04-4b66-a82d-97b5cd862747
| section | Prior to Capping Beam Operations
| checkpoint | Confirm RL’s of capping beam
682e0dc5-7ba7-5bb8-a586-5dbab1af997e | button | Confirm excavation for capping beam has been complete and ready for formwork to commence | Yes, No, N/A
11760787-4b0b-5e79-b9a7-b853f3ee8966 | button | Set out of capping beam complete | Yes, No, N/A
850109e6-3708-5041-8539-0e8071c8e1c8 | button | Confirm engineers design of capping beam | Yes, No, N/A
fdb4f03a-cdf8-5af8-92b8-280dc3f2c03e | note | Attached/referenced below as applicable
| checkpoint | Attach structural engineer inspection prior to concrete pour (All items closed out)
24f5ef86-1917-541b-b439-4495858903d0 | note | Engineer inspections attached/referenced below
| checkpoint | Concrete pre-pour checks - As per below
937c5666-89b3-5694-bd50-dde69cc114d7 | button | Confirm mPa, slump and agg size of concrete prior to ordering | Yes, No, N/A
80ffa77f-dee0-5b70-adbd-b838d06c5269 | button | Confirm formwork faces are clean and will provide required class finish | Yes, No, N/A
00e2a77d-9fa4-5b9e-8cbf-939f8ae39f25 | button | Confirm formwork is adequately braced to reduce blow-out occurrence | Yes, No, N/A
ac05131d-13df-5b93-b6ab-0acda82429c7 | button | Confirm pile connection bars are clean and free of debris | Yes, No, N/A
| checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| section | After Capping Beam Poured
| checkpoint | Attach surveyors spot check – Confirm tolerance of finished concrete surfaces – Ensure no movement to the capping beam during pour
bd08ce92-b025-5007-8dda-2a22cc6a0133 | note | Confirm surveyor spot checks levels and attach markup
| checkpoint | Confirm stripping is complete All exposed faces are clear of formwork
6db83d0f-4d96-5d25-80ed-99c28c4debf7 | button | Confirm vibration was adequate – no air pockets, agg evenly distributed If not, comment rectification method required | Yes, No, N/A
34e770b1-a985-5c44-9005-836dafee8e65 | button | Confirm no blow-out occurred If occurred, comment rectification method required | Yes, No, N/A
33dfb269-bb98-593a-a10e-7cd88979a40a | button | Confirm finish of concrete is adequate (broom/trowel/helicopter finish) | Yes, No, N/A
| checkpoint | Obtain all concrete tests at 1 day
bdf26422-ea0d-5ac1-a870-0863807264a7 | textbox | Test Strength Mpa
46bb6174-b40c-5791-a2de-2feeb27a66e7 | note | Attach concrete test result
| checkpoint | Obtain all concrete tests at 4 days
1c0e5552-a0aa-5892-bf31-4075094b2620 | textbox | Test Strength Mpa
0450d48b-4a3b-5dc0-8c3e-768f41ff707f | note | Attach concrete test result
| checkpoint | Obtain all concrete tests at 28 days
7c7a42e6-7fba-58c0-9ed7-7dd1f796f590 | textbox | Test Strength Mpa
c9b1d99a-5475-57f3-8f2a-ba12468c5d39 | note | Attach concrete test result
| section | Sign-Off
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
805b8edd-7ed6-539c-b7e8-a9b904689225 | button | Subcontractor Sign Off | Yes, No, N/A
6bca9496-1ab6-5bb9-9fd0-535080403812 | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Commissioning Documentation |  | Commissioning Documentation | 1ae1bba6-b14a-4343-b8d2-efe6909c0b57
| checkpoint | Commissioning documentation attached below
ac1cb691-657a-590a-a2ed-a0190efaefeb | textbox | Company Documentation relates to
| checklist | Balcony & Podium Waterproofing |  | Balcony & Podium Waterproofing | 1bb6fadc-2413-4e9e-a5ff-5ddd137e53ad
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
568fb2db-69d1-5bf3-8868-1c08a27469eb | note | Attach relevant photos below
| checkpoint | Membrane system & methodology checked off AGainst Aland standard details & MSDS & guidelines
85e5a2c8-a40c-5581-8fd9-380b58e852fa | button | Surface preparation as per application guide | Yes, No
226f9bb3-d9e2-5ed3-a577-9d1db88b7ce2 | button | Substrate clean, structurally sound & ready to receive membrane | Yes, No
| checkpoint | All corners, joints, gaps & cracks to be treated with a flexible polyurethane sealant Resiflex FC ‐apply selected Membrane as per datasheet & application guidelines
fff9187a-97b0-58ed-9f34-224edea6ef86 | note | Ensure sealant has fully cured before installing membrane
bfe0c044-5cc1-594e-88b9-e63ccc5fcd46 | note | Ensure Humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to primer
7aa21f2f-e360-51e2-b5e4-0a53fc2e1d96 | note | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Ensure all floor wastes & pipes have been primed in accordance with manufacturer's recommendations
3ff6fe06-65e4-57d7-812c-6241625f50d5 | note | PrimeSeal MC to all surfaces at a rate of 3‐4m2/Ltr
e25a880d-4073-5df4-a5a4-3f80c7ac9b71 | note | Alternative primers Multiseal ‐ Primeseal SP at a rate of 5‐8 m2/Ltr
| checkpoint | Balustrade base i.e. shoe base or angle base installed & grouted with structural grout (as required)
7ba4c654-7210-5c03-81c3-18c30b6a9dca | note | Joint between bottom of base & substrate to be no greater than 10mm
| checkpoint | Overflow at the ends of balustrades in place
0c912e93-f425-5dff-8e5b-34e6f50c6ac0 | note | Approximate width of over floor to be 50mm
154ef057-ee19-55ee-8532-b0ef0c07831f | note | Height of overflow must be lower than the bottom of subsill
2c849b5e-56bc-550e-8798-93341a1c4785 | note | Angle to be installed between end of base & wall with top of angle to be at FFL
| checkpoint | First coat of selected Membrane to entire areas as per DURAM recommendations
dcff4d0a-d4fc-5c8e-9342-748706de5818 | note | Note ‐ a total dry film thickness of min 1.2mm (1200 microns) in two finished coats. As such at min. Wet Film Thickness of min 0.75mm (750 microns) per coat is required
c36db381-132c-5835-b025-f772abd61605 | note | Apply membrane at a coverage of 0.75 ‐ 1 Ltr / m2 per coat
0ceafcd0-f08a-5123-b9b8-083c9e0b99b2 | button | Allow the membrane coat to dry min 12 hours check the tackiness before applying next coat | Yes, No
713e780f-5d7d-5e95-88dc-1d4565d72446 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to second coat | Yes, No
| checkpoint | Second coat of selected Membrane to entire areas as per DURAM recommendations
28adc742-85ae-5507-b729-a652a30fc168 | note | Note ‐ a total dry film thickness of 1.2mm (1200 microns) in two finished coats. As such at min. Wet Film Thickness of 0.75mm per coat is required
46ca8fc0-27ea-5471-8f29-7abf9ade8b68 | note | Apply membrane at a coverage of 0.75 ‐ 1 Ltr / m2 per coat
34d6955f-b4de-5182-ad02-964d609cf92a | button | The membrane is to be applied in a minimum of 2 coats at a total coverage of 1.2 to 2 litres per m2. or relevant product TDS | Yes, No
0ca6bc34-074d-52b2-b868-2b10840e4f6c | button | Allow 2nd coat of Multithane UV min. 12 hours BUT no longer than 24 hours before installing Multithane ATC top coat | Yes, No
| checkpoint | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to final coat
| checkpoint | Apply final coat of Multithane ATC at a coverage rate of 3 ‐ 4 m2/lte
| checkpoint | Carry out dry film thickness test using Positector coating thickness inspection instrument
| checkpoint | Rectification of defective works for failure of flood test & works complete
| checkpoint | Ensure screed is fully dry ready for sealer application
| checkpoint | Crystoflex membrane applied (note allow sufficient time for curing minimum 24 Hours)
| checkpoint | Final sign off - All balcony & podium waterproofing work completed as per the above ITP
0a7c6371-6a07-5f4f-a6f1-7d01eae6f9c7 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Balcony Waterproofing |  | Balcony | 27b96e5d-49f8-4651-a21f-3ac2a8b0c635
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
f2b2eb57-140c-53f7-ba6b-acc5758fa00a | note | Attach relevant photos
| checkpoint | WP details listed at architectural drawings for clarifications are followed.
cb428952-c766-5693-be2c-549e4a637336 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
48929575-e054-5966-a176-8cbd12ea5fb8 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
dd31c057-b18b-5ffe-a6df-8f6cec80d946 | tickbox | Ensure no high points or crevices are in the substrate
981f9c28-223e-5415-bf80-37244042afbf | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
c4c8d504-a1b7-5147-ab96-356883e5d05f | note | Attach relevant photos
| checkpoint | Prime substrate with Polybit Hydrapoxy or PU primer - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
3d90beb4-8f7e-5772-8653-77b3994e8a1b | note | Attach relevant photos
| checkpoint | Seal all corners, joints, gaps, cracks and penetrations with Polybit HydraFlex polurethane sealant - Apply selected sealant as per datasheet & application guidelines
b9824ed1-1575-55f9-ac41-eac93fa29450 | note | Attach relevant photos
| checkpoint | Balustrade base i.e shoe base or angle base installed & grouted with structural grout (as required)
fde354a2-e5d1-5d83-b8a4-eb114094383c | note | Joint between bottom of base & substrate to be no greater than 10mm with continuous bead of caulking
| checkpoint | Overflow at the ends of balustrades in place
7e8fb74f-994c-539c-9b3d-30ab8f3af021 | note | Approximate width of over floor to be 50mm
4259cc8e-9c87-516d-836e-13999ceeafb8 | note | Height of overflow must be lower than the bottom of subsill
bf456553-40f6-5a89-acb5-c42bb93c065c | note | Angle to be installed between end of base & wall with top of angle to be at FFL
| checkpoint | Apply 1st coat of Polybit Hydraguard PU on floors with a turnup of 100mm on walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
| checkpoint | The WPM must be terminated at the specified height outlined in the wind classification report, also the WPM must be employ at the water stop angles for doors and window (if Applicable)
b453922e-0476-5374-8afc-be5094a7d8ec | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard PU on floors with a turnup of 100mm on walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
| checkpoint | The WPM must be terminated at the specified height outlined in the wind classification report, also the WPM must be employ at the water stop angles for doors and window (if Applicable)
04825787-cfd2-5cd8-88bf-866f782e9a11 | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
83cd1086-ab7b-5ba5-aa2d-c432ac210352 | note | Attach relevant photos
| checkpoint | Attach photos for the drainage conduit.
f9e088a0-adfe-51a2-b551-a81f830a520d | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
35692a9c-46ff-59d8-a4c3-d4573dc88aaf | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
0c5c6f50-7323-5c87-8936-fb10f3230fab | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Shotcrete (V140421) |  | Shotcrete (V140421) | 2863ad70-2557-419a-9b77-c9ef276d3d1a
| section | Prior to Commencing Works
| checkpoint | Ensure zone for shotcrete has been excavated
| checkpoint | Confirm reinforcement has not moved by concrete placement
7b41962c-2c40-5fc5-9720-0f800f82e195 | button | Confirm that all mesh has bar chairs tied to steel to prevent dislodgement during shotcrete works | Yes, No, N/A
b8aa579d-6da8-5e62-8b9e-d36ca678bc71 | button | Confirm that reinforcement has been installed in accordance to structural engineer details prior to arranging for site inspection | Yes, No, N/A
68d02ba0-4e8b-5e69-a392-3b919427267e | button | Where recessed column is located, confirm that reinforcement installation allows for rebated shoring zone | Yes, No, N/A
816644a6-3bea-5d47-938f-675b4e9c7d48 | button | Confirm that min 300mm lap has been provided for mesh and plastic membrane at typical horizontal control joint | Yes, No, N/A
| checkpoint | Confirm no blow-outs have occurred
| checkpoint | Confirm core drain has been installed in accordance with specifications
| checkpoint | Confirm plastic membrane to rear face of shotcrete wall has been lapped and taped at joints
| checkpoint | Confirm that structural engineer has completed inspection and provided signoff (incl defect closeouts)
5c43985a-3e4d-524a-9509-e7957ae78c2c | note | Engineer inspections attached/referenced below
| checkpoint | Confirm that inspection photos are taken and attached below
| section | Shotcrete Works
| checkpoint | Confirm that shotcrete is applied evenly in layers to avoid honeycombing
| checkpoint | Ensure that shotcrete wall is troweled to agreed finish
| checkpoint | Obtain subcontractor’s installation ITPs and shotcrete mix dockets
3ffbb78b-25d8-5ed8-a654-a27701192c95 | note | Attached/referenced below as applicable
| section | Sign-Off
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
32f69e62-7a3d-59a7-9ac5-b3b0a96da075 | button | Subcontractor Sign Off | Yes, No, N/A
78b22793-1eb5-5b4c-8029-069c95ea91e3 | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Tiling |  | Tiling | 2b8a941e-a9bc-43b4-b46d-c43bdf31b7a2
| checkpoint | Correct tiles are being used in correct areas
597ef029-ad28-55f2-9596-72c9e243e1fa | button | 5mm expansion to all junctions | Yes, No
f65f8e39-1643-5747-b69f-4e459571f4d6 | button | 1.5mm spacers being used | Yes, No
ccc08bdd-8723-5351-859c-b797eb8b73a2 | button | Tile lips are within tolerances | Yes, No
4385c9d9-8e89-51ca-96ed-399fd137c9bb | button | Correct tiles are being used in correct areas | Yes, No
41dd26cf-5b9e-5630-93e1-08ff38328ce7 | button | Angles & trims are straight & free off any defects | Yes, No
| checkpoint | All floors fall to wastes & don't hold water
f52d0030-9b02-54ac-a0e9-0b2e74f9444a | button | Floor wastes are installed & free of any defects | Yes, No
7987e6f5-c3c7-5326-bfcf-9f877bfdaeb3 | button | Wastes are free of any rubbish | Yes, No
0657948d-0e9e-5c5b-9ecf-56f55aec66c2 | button | Check all falls to floor wastes to comply with BCA | Yes, No
| checkpoint | Ensure all tiles are fixed correctly
0bdd34b9-a9e9-51d8-8e7f-6b9421db5540 | button | Check all tile lips are within tolerances | Yes, No
cfdeec66-6386-5e99-a298-d79a97c7f267 | button | Check that glue has been applied notch trowel in accordance with manufacturer's specifications | Yes, No
2769544e-34dc-590d-bb68-f7b435153514 | button | Walls have been laid straight & plumb, reveals are square | Yes, No
619bdd3e-9b13-5413-9e0c-62abc87ac071 | button | Tiles have been laid 1m below 1m offset line | Yes, No
780624a9-96f3-5281-8cb9-26086cd62a48 | button | Tiles have been laid to marker lines on mixers | Yes, No
f99020a3-cdb7-594c-8ce3-9bff2bff7502 | button | Full tile bond on door frames & work away to ensure cuts are in corners | Yes, No
964d7b68-577f-585b-8fa2-c98c0ece9be4 | button | Double check tile batch before use in area | Yes, No
3a39dc8b-0195-50bb-bb28-06a89087b4d5 | button | Check all tile lips are within tolerances | Yes, No
| checkpoint | Ensure floor wastes are clean & free from any debris, area left clean
| checkpoint | Final sign off - All tiling work completed as per the above ITP
749b01f9-ab3c-583e-86f7-ace6d278a554 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Framing |  | Framing | 2d6406cc-3e47-4b9a-af0f-e7c994b92d69
| checkpoint | All studs are set out correct, and are plumb level and square
| checkpoint | All studs are installed as per manufacturer's recommendations and the BCA
| checkpoint | All noggins are installed correctly
| checkpoint | All sarking has been installed as per manufacturers recommendations
| checkpoint | Penetration through fire rated wall have been treated
| checkpoint | Door frames have been installed plumb level, square and in wind
| checkpoint | All window and sliding door openings are as per plan and line up with above elements
| checkpoint | All studs are level and in wind
| checkpoint | All internal walls have been studded out and are as per plan
| checkpoint | Weep holes have been installed correctly and at right height
| checkpoint | Door frames to be infilled
| checkpoint | Insulation installed as per AS/BCA (party walls & external)
| checkpoint | Acoustic practices to be as per Australian Standards & BCA
| checkpoint | Final sign off - All framing work completed as per the above ITP
d03d96a5-7320-55a2-a456-c6abcc39d65d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Internal wet areas |  | Bathrooms | 3196a87f-c390-4621-88d8-1041fd6cb0de
| checkpoint | Area barricaded off to allow no access to internal wet areas with signs posted/ visible to include date of application, "No access waterproofing work in progress"
60682af5-e3a9-56f0-9f8b-dc97a4a585b6 | note | Attach relevant photos
1946f4f0-7ecd-5556-b643-af3190bfc56a | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
09f8a295-23ba-5611-9d02-9878d72d9fde | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
0c2ee4bc-a2ca-5395-a31f-0ea0c030031c | tickbox | Ensure no high points or crevices are in the substrate
de804c4f-0f28-5427-85b2-58eb158d4809 | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
d7d5a78d-8234-5d75-87c7-02b6efbf3fd5 | note | Attach relevant photos
| checkpoint | Primer substrate with Polybit Hydrapoxy/polyprime - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
| checkpoint | Install aluminium waterstops to door entries and showers as per builder's FFL.
e113ae4c-41f3-5f76-8fe4-1e595e9b25f8 | note | Attach relevant photos
| checkpoint | Seal all joints, gaps, cracks and penetrations with Polybit HydraFlex polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
8c4a3488-532e-5d76-bbd5-da634ce55d3b | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydraguard on floors - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
95aa9d4b-83d1-58b1-ab22-5143306d29b8 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard on floors - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
ac6b6a82-241e-56b0-bc2d-0ceba15d13ee | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
fc440fe2-5d6b-51e2-a637-50645ae49ae7 | note | Apply Polybit Hybrid 150 to walls where required as per data sheet and application guidelines.
| checkpoint | Flood test for a minimum of 24 hours.
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
76ede9e7-05c5-5a54-9cdb-0b00007d2751 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
238c1fe3-30d1-5265-b36b-8f55ab814241 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | NDIS |  | NDIS | 326d202d-3b61-4907-b452-df69890fc06f
| section | Planning and Pre-Commencement
| checkpoint | Confirm site setout is from the latest set of drawings, and has been approved “For Construction”
| checkpoint | Insert DWG. No
| checkpoint | Confirm meter marks have been clearly shown
| signoff | HOLD POINT
| section | General Requirements
| checkpoint | The dwelling has the following noted features on an entry level or a level serviced by a lift: One kitchen, and One laundry.
f8d5e823-ca0c-551e-90b3-ff2a8efd9224 | note | One bedroom exclusively for use of a participant,
206d6211-2ab0-5c85-89f7-a8c7c3b62e67 | note | One WC pan,
0f4bf664-1a3d-51e0-897b-a4b955044a97 | note | One shower,
f202a49f-5b78-5dff-bdb0-784651695e0d | note | One hand wash basin,
c9b6bcc5-da79-5fa2-9b19-a6badc24b8cc | note | One living area,
| checkpoint | General Requirements complete
| signoff | HOLD POINT
| section | Pedestrian entry from the site boundary
| checkpoint | A safe, continuous step-free accessway is provided from the front boundary of the site to an entry doorway of the dwelling. The accessway may include a walk way, step ramp or ramp and shall include any additional enhanced requirements of the particular design category as noted in this SDA Design Standard document.
| checkpoint | 1:20 grade is permitted as a part of the accessway and where provided has incorporate the following:
5160365a-6f6e-55a6-89e6-758ba6025a60 | note | • 1200mm length mid-landings, in the direction of travel (of the same width as walkway width) provided every 15M. Additional landing size has been provided as per AS1428.1 where a change in direction is required.
2ac924eb-be2a-59ff-8ee3-7408e7ccd8cf | note | • The floor surface abutting the sides of a 1:20 grade walkway is provided with a firm and level surface which can be a different material at the same level and grade of the walkway, and extend horizontally for an additional minimum of 600mm, from an accessway unless one of the following is provided: kerb, kerb-rail and handrail or wall (min 450mm height) to comply with the requirements of AS1428.1.
74cfb481-c307-5334-b2e6-54b746d48c12 | note | • Slip resistance shall be a minimum of P4 or R11.
| checkpoint | 1:10 grade step ramp is permitted as a part of the accessway and where provided has incorporated the following:
d08b2040-34c1-556c-81c5-4cf59b4e9287 | note | • The maximum level change or transition which can be dealt with by a step ramp is 190mm and maximum length of ramp is 1900mm
53cc09dd-d407-503f-a99a-b6d023b45ecb | note | • All features of 1:10 step ramp including landing sizes, handrails / kerbrails (if required) shall comply with the requirements of AS1428.1.
2610d34d-1928-5a2c-9926-e16cebbd168d | note | • Slip resistance shall be a minimum of P5 or R12
| checkpoint | Where the level difference is over 190mm, a maximum grade of 1:14 ramp is permitted as a part of the accessway and where provided has incorporated the following:
8ce31ac3-f951-5d91-8e38-7e16b2b2daaa | note | • 1200mm length landings, in the direction of travel (of the same width as ramp width) provided at base and top of the ramp and at maximum intervals of 9M. Additional landing spaces shall be provided at turns and changes in direction as required under AS1428.1.
c223c0e1-dbf8-5092-9893-54f070fec4c1 | note | • All features of 1:14 ramps including handrail profile, handrail extensions and kerb rails shall comply with the requirements of AS1428.1
ea85bd44-5205-5a97-bd44-99c1a3bb9561 | note | • Slip resistance shall be a minimum of P4 or R11.
| checkpoint | The minimum clear width of an accessway shall be 1200mm measured from a narrowest part of the accessway (for example skirting to skirting). This includes all ramps within the accessways.
| checkpoint | Where provided, the minimum clear width of a curved accessway is a minimum of 1500mm with a minimum radius of the curvature as specified under AS1428.1. The crossfall shall be towards the centre of curvature.
| checkpoint | Where a ramp or walkway is part of the accessway, level landings no less than 1200mm x 1200mm, exclusive of the swing of the door or gate that opens onto them, has been provided. The landing size shall increase based on the required gate / door circulation spaces or change of direction requirements as per AS1428.1.
| checkpoint | Minimum vertical clearance along all paths of travel is 2000mm.
| checkpoint | Pedestrian entry complete
| signoff | HOLD POINT
| section | Car Parking
| checkpoint | A safe, continuous step-free accessway has been provided from both; The front boundary of the site and From any car parking space associated with the dwelling (excluding staff only parking), to an entry doorway of the dwelling.
| checkpoint | If providing a car parking space, for use of the participant, it has been provided with:
20dd1279-97fb-5925-977b-0b9739881223 | note | Minimum dimensions of 3800mm (width) x 5400mm (length), An even, firm and slip-resistant surface of P4 or R11, A level surface with a maximum 1:40 gradient in any direction, and Roof over space with clear vertical clearance in accordance with AS2890.6
| checkpoint | Based on the building classification, the NCC or the local government authority may require the provision of an accessible parking space in accordance with AS2890.6, in which case the full compliance with AS2890.6 is required.
| checkpoint | Car Parking Complete
| signoff | HOLD POINT
| section | Entrance, doorways and door hardware
| checkpoint | A level landing area of at least 1500mm x 1500mm with a maximum 1:40 gradient and crossfall has been provided at the level (step-free) external entry doorway, on the arrival side of the door (i.e. the external side of the door).
10616c32-6b62-5d9f-be0c-984509a69502 | note | The level landing area has been increased to accommodate door circulation spaces as per AS1428.1
1391026c-cfa3-5451-8c46-33d576c68205 | note | Doorway threshold ramp (if required) is permitted to be within the landing area.
| checkpoint | A step-free doorway threshold has been provided to an external entry doorway. Where the threshold at an external entry doorway exceeds 5mm and is less than 35mm, a doorway threshold ramp in accordance with AS1428.1 shall be provided with a maximum 1:8 grade as shown in Figure 4 of the NDIS Specialist Accommodation Design Standard
| checkpoint | A step-free doorway threshold has been provided to external doorways leading to common or private open spaces. Where the threshold at the external doorway exceeds 5mm and is less than 35mm, a doorway threshold ramp in accordance with AS1428.1 shall be provided with a maximum 1:8 grade as shown in Figure 4.
| checkpoint | The dwelling has provided all doors to and within all areas normally used by the participants), including all external doorways with a minimum clear opening width of 950mm, when measured in accordance with Figure 5 of the NDIS Specialist Accommodation Design Standard
| checkpoint | All door circulation spaces (excluding internal door circulation spaces for bedrooms) has been provided in accordance with AS1428.1 to both sides of the door.
| checkpoint | All internal doorways have a level (step-free) transition and threshold (maximum vertical tolerance of 3mm vertical or 5mm between abutting surfaces is allowable provided the lip is rounded or bevelled).
| checkpoint | Doorways shall have door handles installed at between 900mm to 1100mm above the FFL.
| checkpoint | Door handles selection and location comply with AS1428.1 as shown in Figures 6 and 19 of the NDIS Specialist Accommodation Design Standard
| checkpoint | Doorway circulation spaces in accordance with AS1428.1 have been provided to all doorways (excluding exclusive staff use areas, non-accessible toilets and storage rooms).
6fb50eb9-b6e9-5f29-8cf1-3fedcd450c1a | note | Door automation can be provided in lieu door circulation spaces that are required as per AS1428.1 to the latch side of the door.
62c7175c-2af3-50c7-b965-f54eee88d1fc | note | Note that if door circulation is not provided as per AS1428.1 then door automation must be provided at the onset and not simply provision for door automation at a future time.
| checkpoint | Power and control cabling to head of entry doors of participant bedrooms, one external entry doorway and one external doorway to an open area (where provided) has been provided for future automation. A capped GPO at the door head may be provided to comply with this requirement.
| checkpoint | Entrance, Doorways and Door Hardware complete
| signoff | HOLD POINT
| section | Corridors
| checkpoint | All internal corridors and passageways has provided a minimum clear width of 1200mm when measured from skirting to skirting.
| checkpoint | Width of the corridors comply with the requirements of door circulation spaces as per AS1428.1 based on direction of approach.
b1d8dcd6-7bde-5f7b-8423-e7adefc302b0 | note | Note: Where AS1428.1 requires corridor width of less than 1200mm, then a minimum clear width of 1200mm shall be provided.
| checkpoint | Corridors Complete
| signoff | HOLD POINT
| section | Windows
| checkpoint | All window sills in living areas and at least one window sill in each participant’s bedroom are positioned no higher than 1000mm above the FFL.
f390a2d4-a326-5564-b135-52af2a2c9f72 | note | Note: Concession is reasonable in kitchen, bathroom and utility spaces.
| checkpoint | Window controls are located within easy reach from either a seated or standing position (between 600mm to 1100mm above FFL).
82aa78b1-be8b-5c98-aa18-b0405e1b8734 | note | Note: Concession is reasonable in kitchen, bathroom and utility spaces.
| checkpoint | Power and control cabling to windows of bedrooms and living areas have been provided for future window blind automation. A capped GPO at the window head may be provided to comply with this requirement.
| checkpoint | Provide lockable windows.
| checkpoint | Windows Complete
| signoff | HOLD POINT
| section | Sanitary Facilities
| checkpoint | The entry level, or a level serviced by a lift, have been provided with sanitary facilities that include a WC pan, a shower and a hand wash basin.
| checkpoint | The required WC pan, shower and hand wash basin referred to in Clause 7.1 have been provided within the same bathroom.
| checkpoint | At least one WC pan on the entry level, or a level serviced by a lift, is AS1428.1 compliant (as per requirements for unisex accessible toilet and not as per ambulant toilet) and has been provided with either:
edf61062-6ae6-52a7-b441-340a49d1e384 | note | c/l of WC pan at 450mm - 460mm to side wall, 800+/-10mm front edge of WC pan from back wall, Minimum 600mm clear of cistern from front edge of WC pan
837dcbf8-ea0c-5236-bef1-83cc0318bf64 | note | Minimum circulation space of 1900mm x 2300mm as required by AS1428.1
24c0df7f-b3c7-50ee-aeb5-fca99c85f0ee | note | Toilet flushing controls shall be proud of the surface
4246eaea-2158-5b08-92f4-63ae33d7d991 | note | Refer to Figure 8(a) for permissible basin encroachment zone. OR A minimum circulation space of 900mm to both sides of the WC pan for 2300mm from the back wall of the WC pan has been provided as required for Accessible Adult change facilities as noted in the NCC. Refer to Figure 8(b)
| checkpoint | At least one shower on the entry level, or a level serviced by a lift, has been provided in a corner of the room with the following provisions:
414e2870-9253-5d28-a546-19a6181372dd | note | The shower size is a minimum of 1160mm x 1100mm and provided with one of the two circulation spaces for shower as required by AS1428.1. Refer to Figures 8(c) and 8(d).
ba1f2d07-959e-5a80-9f83-b09e2d660fa6 | note | Shower curtain rail has been provided around the 1160x1100mm shower space.
8a9c17c3-6265-54df-b4e0-be2dd2376ac4 | note | Only vertical support grab rail has been provided to the shower, with provision of height adjustable shower head and hose as per AS1428.1
aa7ff17d-dbee-5dbd-9fab-af7951fb72ac | note | Lever style shower tap has been provided and located in a zone between 900mm to 1100mm above FFL and between 300mm and 800mm from the internal corner.
79572894-2eb9-5de1-ad08-103238905245 | note | Shower floor gradient is as required by AS1428.1.
| checkpoint | At least one hand wash basin on the entry level, or a level serviced by a lift, is AS1428.1 compliant and has been provided with:
207028dd-8f57-550b-b200-750bb6b56bf4 | note | A minimum basin depth of 430mm
9b884d75-3962-556d-a607-8de7e45060eb | note | Minimum circulation space as required by AS1428.1
bf2bda61-5eda-59d8-bcc2-64b28e9a3376 | note | Encroachment free knee and toe clearance space as per AS1428.1 under the basin for a minimum width of 850mm, centred on the basin.
4bfdf94e-3816-59a5-99c6-0f2a056bca84 | note | Sensor type or lever style tapware has been provided to comply with AS1428.1 and located such that the operable part of lever tap handle and water source are within 300mm from edge of hand wash basin.
db237167-5ca0-5d89-87d9-a609b5bedbd7 | note | Refer to Figures 9(a) and 9(b) of the NDIS Specialist Disability Accommodation Design Standard
| checkpoint | If providing a fixed bathtub, it is clear of the circulation space requirements of WC pan, shower and hand wash basin.
| checkpoint | Slip resistance of all floors to sanitary facilities is a minimum of P3 or R10.
| checkpoint | Except for walls constructed of masonry or concrete, the internal side of the full sanitary room with the required WC pan, shower, hand wash basin and fixed bathtub (if provided) has wall reinforcement of minimum 12mm thick sheeting, from FFL and extending to a height of minimum 2100mm from FFL.
| checkpoint | The WC pan has an adjacent side wall (on at least one side of the WC pan) with a 600mm minimum length of wall reinforcement, forward of the WC pan. In designs where the near side wall adjacent to the WC pan includes a doorway (and the wall is not available on the other side of the WC pan) then a 600mm minimum length reinforced wall is clear of the door frame.
| checkpoint | Sanitary Facilities Complete
| signoff | HOLD POINT
| section | Kitchen
| checkpoint | A kitchen has been provided with the following minimum fixtures: a fixed cooktop (with a rangehood), an in-built oven, a sink (with tap) and a dishwasher.
| checkpoint | At least 1550mm clearance has been provided in front of fixed benches and appliances (being the leading edge of the outermost bench and not from the face of cupboards or the kickplate and excluding handles). Where the appliances are not installed the recessed area provision for an appliance is a minimum of 700mm in depth.
| checkpoint | Task lighting has been provided above workspaces. A minimum level of 300 lux has been achieved when tested at maximum intervals of 1500mm, directly over the surface of the benchtops.
| checkpoint | A wall oven has been provided with features as noted below:
1886d68e-dfa1-5bec-9ba5-7f1a91ad77df | note | Side hinged door with latch side of door next to accessible benchtop.
7e9e92b0-f3cd-5dfe-ad50-30ac2a17bdbb | note | At least a part of the operable part of oven door handle is located between 600mm and 1100mm above the FFL.
9c072494-1062-5044-aca0-b4235070052e | note | At least one shelf on telescopic rails within the oven.
| checkpoint | An accessible benchtop has been provided with features as noted below:
11946f11-a0b2-534f-b15a-2f30c8dc0074 | note | A benchtop surface of minimum 600mm depth has been provided right next to the cooktop and wall oven (on the latch side of the oven door).
0d5f087d-ffbc-5d25-999a-93d4fb279011 | note | This accessible benchtop provides a minimum space of 900mm (width) x 440mm (depth) clear of any fixtures other than what is permitted under knee / toe requirements of AS1428.1 under the benchtop.
| checkpoint | One height-adjustable benchtop surface, of 600mm depth,has been provided with features as noted below:
885f9bd0-130f-5466-8f98-bf9313ce739e | note | A minimum space of 900mm (width) x 440mm (depth) clear of any fixtures other than what is permitted under knee / toe requirements of AS1428.1 under the benchtop.
53424977-d68d-578e-825a-54e36ae544e8 | note | Height adjustment capability from 720mm clear space underneath height adjustable benchtop till 1020mm clear space underneath height adjustable benchtop (from FFL).
| checkpoint | Types of appropriate mechanisms for operation of kitchen cabinetry shall be one or more of the options as noted below:
217b5dbd-2016-5eac-a7aa-db0fc5141c15 | note | D pull cupboard handles located towards the top of below-bench cupboards;
afd0d952-70b1-57d8-94c7-02078bee255a | note | D pull cupboard handles located towards the bottom of overhead cupboards;
0364ed49-3c66-5efb-9402-5c8796328a83 | note | Overhanging lip of minimum 20mm for overhead cupboards;
4add73aa-f71c-5e5b-9344-834c230048f3 | note | Push to release mechanisms for both overhead and below-bench cupboards.
| checkpoint | A cooktop shall be provided with features as noted below:
ad2a8e20-e64c-538d-8d23-258e8601feb3 | note | Either electric or induction
0554a32b-3753-5aab-b40d-3aec9335faf2 | note | Shall be located at least 300mm from any internal corner or wall, excluding the splashback.
| checkpoint | The cooktop controls shall be on the side of the accessible benchtop or near the front edge of the benchtop.
| checkpoint | Lever or sensor type tapware has been provided to sink to comply with AS1428.1 and is located such that the operable parts of the lever tap and water source is not more than 300mm from the edge of benchtop.
| checkpoint | At least one double GPO has been provided within 300mm from the front edge of the benchtop (from the edge within the kitchen area) and max height of 1100mm from FFL. GPO shall be located adjacent to a bench of minimum 600mm depth.
| checkpoint | Drawer style dishwasher has been provided.
| checkpoint | A pantry has been provided which is wheelchair accessible.
| checkpoint | Slip resistance of all kitchen flooring is a minimum of P3 or R10.
| checkpoint | Kitchens Complete
| signoff | HOLD POINT
| section | Laundry
| checkpoint | A laundry has been provided with the following minimum fixtures: a sink or tub (with taps).
| checkpoint | At least 1550mm clearance has been provided in front of fixed benches and appliances (being the leading edge of the outermost bench and not from the face of cupboards or the kickplate and excluding handles). Where the appliances are not installed the recessed area provision for an appliance has been a minimum of 700mm in depth.
| checkpoint | Basins, sinks and tubs has been provided with sensor type or lever style tap. The tap is located such that the operable parts of the lever tap and water source is not more than 300mm from the edge of benchtop/ laundry tub trough / bench.
| checkpoint | Slip resistance of all laundry flooring is a minimum of P3 or R10.
| checkpoint | Laundry Complete
| signoff | HOLD POINT
| section | Bedroom
| checkpoint | Bedroom size shall allow for a minimum Queen bed of size 1530mm x 2100mm.
e729e964-4d56-55b8-b836-9b5a58552a45 | note | Circulation spaces around the three sides of the bed (not including bed head side) includes:
2846545c-90a7-5fc4-9aba-2dddb42649fe | note | Space with minimum width of 1540mm on any one side on the bed;
85a16d26-c2e7-5910-81de-16f111e4759a | note | Space with minimum width of 1000mm to the other two sides of the bed.
| checkpoint | The following door circulation spaces for bedroom has been provided:
74493824-479b-528b-a562-79048cad03bc | note | Internal door circulation space of the door to bedroom is a minimum of 1540mm (width) and 1450mm (depth), as shown in Figure 16. This internal door circulation space is clear of the Queen bed of size 1530mm x 2100mm.
acdf6ae6-7562-54f3-aef9-49c3503ef35b | note | External door circulation space is as per AS1428.1 based on the direction of approach or a minimum of 1200mm when measured from skirting to skirting (whichever is more).
| checkpoint | A robe of 1400mm width has been provided within the bedroom, clear of the required bedroom size and with a minimum space of 1540mm in front of the robe.
| checkpoint | Following GPOs has been provided:
ef193a3c-901e-5fc4-a43a-83fb24cc4cf3 | note | Three double GPO on the wall where the head of the bed is likely to be, and At least one double GPO on the wall opposite the wall where the head of the bed is likely to be.
| checkpoint | Bedroom Complete
| signoff | HOLD POINT
| section | Living area
| checkpoint | The family/living room accommodates a free space, minimum 2250 mm in diameter, clear of furniture.
| checkpoint | Living area Complete
| signoff | HOLD POINT
| section | Switches and Powerpoints
| checkpoint | Light switches are positioned in a consistent location:
1c7909e9-27dd-5abe-8b2f-35d421dea1d2 | note | Between 900mm – 1000mm above the FFL, and Horizontally aligned with the door handle at the entrance to a room.
| checkpoint | GPOs are installed between 600mm and 1100mm above the FFL.
| checkpoint | Light and GPO switches are rocker action, toggle or push pad in design with a minimum width of 35mm.
| checkpoint | Dimmable lighting switches are provided in living areas and bedrooms.
| checkpoint | Switches and Powerpoints Complete
| signoff | HOLD POINT
| section | Flooring and Slip Resistance
| checkpoint | All internal flooring (including wet areas) are firm, even and feature a level transition between abutting surfaces of a maximum vertical tolerance of 3mm or 5mm (provided the lip is rounded or bevelled).
| checkpoint | All internal floor finishes have a minimum slip resistance of P3 or R10.
| checkpoint | Carpets if provided within the dwelling, are provided with pile height or thickness not more than 11mm and carpet backing not more than 4mm bringing the total height to a maximum of 15mm.
| checkpoint | Flooring and Slip Resistance Complete
| signoff | HOLD POINT
| section | Internal Stairways
| checkpoint | Stairways within dwellings feature a continuous handrail on both sides of the stairway.
| checkpoint | A minimum clear width of 1000mm has been provided; between the handrails and handrail profile and handrail extensions shall be as per AS1428.1.
| checkpoint | Stairway have no winders on landings.
| checkpoint | Stairway have closed risers.
| checkpoint | The stairway provide slip resistance of P3 or R10.
| checkpoint | Internal Stairways Complete
| signoff | HOLD POINT
| section | Use of Lifts
| checkpoint | Passenger lift if provided within a dwelling or for access to a dwelling is as permitted under the NCC Clause E3.6, excluding the use of stairway platform lifts.
| checkpoint | Lift door to provide a minimum clear opening of 900mm.
| checkpoint | The lift car size is a minimum 1100mm (width) x 1400mm (in direction of travel).
| checkpoint | Use of Lifts Complete
| signoff | HOLD POINT
| section | Common use external areas, private open space and landscaping
| checkpoint | All common use external stairways comply with AS1428.1.
| checkpoint | Where individual letter boxes have been provided then, they are:
a151def7-2db9-5c1f-afa7-4204c1ea9d4d | note | Situated on a hard-standing area of 1540mm x 2070mm and have a gradient and crossfall directly in front which is less than 1:40 in any direction.
26d9bea9-07e9-51d6-ba3f-ee243527b94b | note | H wheelchair access by a continuous accessible path of travel from the dwelling to the letterbox, Are lockable, The height of the letterbox is between 600mm and 1100mm above FFL.
| checkpoint | All ramps and accessways provided to all external common use and external private use areas comply with the requirements of ramps and accessways as noted in Clauses 2.4 to 2.12 as applicable to the various design categories.
| checkpoint | Common use external areas, private open space and landscaping Complete
| signoff | HOLD POINT
| section | Storage
| checkpoint | A dwelling has been provided with a storage cupboard with a minimum 600mm width and adjustable shelf heights.
| checkpoint | Storage Complete
| signoff | HOLD POINT
| section | Ceiling Hoists
| checkpoint | Bedrooms has a provision for power and inbuilt structure, capable of installation of a constant charge ceiling hoist. The hoist is capable of going across the bed and down the bed. Min load capacity of the hoist shall be 250kg. Hoist is capable of being either ceiling mounted or wall mounted.
| checkpoint | Evidence / Certification document has been provided for the building structure to be able to provide for a ceiling hoist in the future:
ae9f3d37-b400-525e-922d-9d96a3fa7c1f | note | For design stage assessments, the notation of the requirements on the assessed drawings or specifications is adequate.
ebe035b1-12fc-517e-83c9-d96fe978e6b8 | note | For final-as-built stage of SDA certification, the structure has been inspected and certified by a qualified structural engineer as being suitable for ceiling hoists with minimum load capacity of 250kg.
| checkpoint | Ceiling Hoists Complete
| signoff | HOLD POINT
| section | Heating and Cooling
| checkpoint | Reverse cycle air-conditioning has been provided to living areas and bedrooms with control panels in an accessible location between 900mm and 1100mm from FFL and not closer than 500mm to any internal corner.
| checkpoint | Where ducted air-conditioning is used, zoning of habitable rooms shall be provided.
| checkpoint | Heating and Cooling Complete
| signoff | HOLD POINT
| section | Emergency Power Solutions
| checkpoint | Emergency power solutions shall be provided to cater for a minimum 2-hour outage in no less than 2 double GPOs in participant bedrooms and any provided automated doors that are used for entry or egress.
| checkpoint | Emergency Power Solutions Complete
| signoff | HOLD POINT
| section | Assistive Technology
| checkpoint | Internet connection has been provided with the ability for high internet speeds to be maintained and stable in nature with wi-fi coverage throughout all areas of the dwelling.
| checkpoint | A video, intercom or other communication system has been provided to enable communication between the participant and their supports when not within line of sight.
| checkpoint | Assistive Technology Complete
| signoff | HOLD POINT
| section | Fire Safe Design
| checkpoint | Smoke alarms that are in keeping with a home environment has been provided in bedrooms and living spaces.
| checkpoint | Emergency evacuation plan has been provided to the occupier or their supports, which may include a path of travel to a safe place.
| signoff | HOLD POINT
| checklist | Bulk Excavation |  | Bulk Excavation | 33369d76-04b0-4a78-81a1-fc858b9102ef
| checkpoint | Confirm dial before you dig documents are onsite - If applicable and attached below
| checkpoint | Confirm correct disposal of classified material
| checkpoint | Obtain geotech report, including load bearing capacity
86439ea8-4d78-54b1-978a-8e63a292c34f | note | Geotech report referenced or attached below
| checkpoint | Collection of tip dockets - If applicable and attached below
| checkpoint | Confirm set out off boundaries & marked out
| checkpoint | Confirm Bulk RL is within detailed excavation zones/limits
| checkpoint | Civil engineer inspection carried out - Attached below as applicable
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
65273839-5817-56c9-9e7a-12c75ff81bcd | button | Subcontractor Sign Off | Yes, No, N/A
82cd7c0a-7afd-5c68-9969-3ac82944c6a4 | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Garbage Room (V90421) |  | Garbage Room (V90421) | 33528c2b-9a20-4064-a77a-59ce6b32e199
| checkpoint | Coving perimeter of the floor
| checkpoint | Epoxy floor and wall up to 15m high
| checkpoint | Hot & Cold water taps installed
| checkpoint | Check for need of hot water tank
| checkpoint | All PVC piping to be fire checked
| checkpoint | Garbage room exhaust fan installed correctly
| checkpoint | Garbage room overhead lighting installed
| checkpoint | Signage is clearly installed
| checkpoint | Magnetic door holder fitted and functioning correctly on all entry / exit doors
| checkpoint | Final sign off - All garbage room work completed as per the above ITP - Add general photos/comments below
fdb2fc92-e2b0-5ac3-a255-e40fa225f597 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Plumbing Rough-In |  | Plumbing Rough-In | 3616db28-d1c1-44cf-9193-3db12bc31ec6
| checkpoint | Floor wastes checked - Any issues comment/photo below
| checkpoint | 1m offset to floor height has been achieved
| checkpoint | Mixers are in correct position (hole allowance to work with tiles)
| checkpoint | All wall hung items have been allowed for in setout
| checkpoint | All rough-in pipework is colour coded to ensure no cross connections
| checkpoint | All poly pipes located in framing to ensure no screw fixings will penetrate them
| checkpoint | All Water & Gas risers are complete
| checkpoint | All stacks are level/plumb
| checkpoint | Ensure all services that go through fire rated walls to be treated with collars/fire rated sealant
| checkpoint | Pipework tested
| checkpoint | Ensure rough in has been done as per specs
| checkpoint | Ensure dummy fit‐out has been done
| checkpoint | Final sign off - All plumbing work completed as per the above ITP
| checklist | In-Ground Sewer ITP (V140421) |  | In-Ground Sewer ITP (V140421) | 36af0a2d-9f12-4ec6-a73a-52fe023d7c73
| section | Pits and Pipes
| checkpoint | Is Approval from Local Water Authority Required If so please provide permit
| signoff | Sign Off Required
| checkpoint | Details
3ccbfcaf-3f19-55b5-9e4c-e614ba8a360e | textbox | Engineering plan number(s)
8846502d-e599-5329-9ba2-c4564ee60480 | textbox | Name of certified drainlayer
4beb8833-601b-5a30-bd23-fe7b34eec789 | textbox | Location (pit to pit)
01c37e4c-cb11-574e-b35d-a34bade5424f | textbox | Delivery Date (Pits and Pipes)
ea087054-07a6-5c6b-9ecd-454ecac943e6 | textbox | Is work area clear and available for construction
c353ceb1-9576-54dd-919b-0a5407850d83 | textbox | Do you have the appropriate plant / equitment to perform scope of works Provide details
| section | Trench / Excavation Methodology
| checkpoint | Method
1b3c5389-dd7d-5e41-bbce-e9670c7ad075 | tickbox | Shield
21b4c5fd-3394-5a5d-884f-2b9043ac1d63 | tickbox | Bench
1827f2af-6d09-5735-be4c-2778ceac76db | tickbox | Batter
a937cdac-3358-5e51-9812-6929d8297916 | tickbox | Other
283ea4ce-3668-50fd-89fe-72ed2729938f | textbox | If other, please specify
19e3c7b8-0475-5101-83c0-498a690f8042 | tickbox | Certified / Tagged lifting Equitment
| section | Product / Material check
| checkpoint | Pits
d1962869-f976-5c46-9451-8961dfafaf39 | textbox | Type
dc82c8a6-f565-5607-aac5-8f0315e915bf | textbox | Size
| checkpoint | Pipes
cd71a23e-9391-5d88-85b0-0e8ee4172103 | textbox | Type
44e71476-44b5-5395-9521-dc5a48427db0 | textbox | Size
| checkpoint | Lot / Building Connections
00eee599-9418-516d-9909-a9a32ac10ff1 | textbox | Type
f02945f6-5821-5c9b-a9f4-6034327dcd7f | textbox | Lot number location
| checkpoint | Bends
16098d01-8447-502d-bb80-0838449ccf53 | textbox | Type
73671efd-0e21-5a24-8c90-ff0385a36883 | textbox | Size
e2032a13-5186-5687-9170-c012ebcfbaf0 | textbox | Location
| checkpoint | Quality Onsite Visual Inpection of Products/Materials - Defects to be Notified
ae85ef95-04b7-5cec-9425-7753730005b4 | textbox | Surveyors name
| checkpoint | Set out / Off Set Check
| signoff | Sign Off Required
| section | Pit Installation
| checkpoint | Pits
780670b1-0d28-51d1-a231-3336526599c3 | textbox | Bedding and backfill type as per detail
4ecfd557-640b-5f37-985a-5853dc4f4f2f | textbox | If under cutting required, note metreage and depth ( Approval Required)
3f808fb5-4108-5ea0-86db-621f1f7408c0 | tickbox | Backfill to be compacted in 150mm Layers as per detail
d6260f49-e379-563a-8fb1-882114324485 | tickbox | External Concrete Bandage
b4901173-e360-5eee-8ee5-ed67a7c4226e | tickbox | Internal Benching
de2ca51c-f784-5665-8d16-3f93270728f6 | tickbox | Internal Plastering / Render / Sealent
cfc9f160-eb22-5dbd-92a4-3107cf21b318 | tickbox | Sealant Between Riser
2b317290-6a15-5989-9fde-61f3008d9655 | tickbox | Steps Required
66cc5141-0626-5ba3-9593-7e16d1b61e80 | textbox | Have pits been secured and covered through the construction phase to elemenate debris/silt
3532c108-76dd-59e8-87b7-09c2a57e9205 | textbox | Pressure testing
| checkpoint | Pipe invert levels through pit as per design
| signoff | Sign Off Required
| section | Pipe Installation
| checkpoint | Pipes
9309b47f-9129-556d-89b0-82f980aa5736 | textbox | Are pipes free and clean of debris before installation
12c071c6-c279-57e2-bc27-eac983c5f179 | textbox | Bedding and backfill type as per detail
02c1199d-4ead-5bcc-9e85-58dcae86f754 | textbox | If under cutting required, note metreage and depth ( Approval Required)
1c877e6d-f8ee-5b50-b0f4-34a5d4e03fe9 | tickbox | Backfill to be compacted in 150mm Layers as per detail
| section | Drainage Check
| checkpoint | Backfill to be compacted in 150mm Layers as per detail
bd8f25c1-97fb-50dc-b12c-7790a8d954ac | textbox | Grade and Alignment Check
0b98479c-f63b-5fb4-8738-4bb852a46982 | textbox | As-built measurements / Pick up Recorded Before Backfilling
f562b9ec-86ba-525c-9d30-78b5281d97da | textbox | Invert/ RL check
237efe68-e874-50e6-8317-40f12faa366c | textbox | Pressure Testing
3553c3f6-927a-515a-adf4-f38d8668ef65 | textbox | CCTV Pipe Inspection / data and comments supplied
| checkpoint | Progress Photos
| section | Service Connections
| checkpoint | All Connections, Bends, Junctions installed
6985ace6-7609-55c5-b1fd-94670afb88db | textbox | As-built measurements / Pick up Recorded Before Backfilling
| signoff | Sign Off Required
| checklist | Cold Water Pump Room |  | Cold Water Pump Room | 3d0a5b51-be8b-4bfc-ba4e-3ce6c28a8b03
| checkpoint | Ensure cold water pumps are installed as per plans
| checkpoint | Pump isolation valves installed on all pumps
| checkpoint | All pipe work tested to min 1200 kpa
| checkpoint | Switchboards in place using suitable fixings to match mounting service No damage to external board has occurred during installation
ea1dd681-9809-5134-8331-0e9e83c43342 | button | Ensure adequate pathways exist within board to accommodate all circuits and allow for future expansion | Yes, No
cb5a7e58-9a10-563e-98ea-13277f72a0a0 | button | Install and loom in all circuits into correct cabinets | Yes, No
d13801cc-b0e1-5df5-9ec1-c0dcc22d66c0 | button | Ensure cable labels match switchboard schedule and construction drawings | Yes, No
9063b643-e088-589b-977f-06c09a97b708 | button | Cables are labelled as per specified requirements | Yes, No
7e33d653-440c-5c0d-9287-8f145c375638 | button | Check all tightness of all terminals on all breakers and bars | Yes, No
1a059678-e5ed-5053-ac2f-61bd99b102ff | button | Ensure safety signage is installed and visible as per plans | Yes, No
| checkpoint | Final sign off - Cold water pumps installed as per the above ITP - Add general photos/comments below
8993bbe9-c764-5076-af7a-93ca945a9f9d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Post Wall Linings |  | Post Wall Linings | 4411f321-6e9c-4f56-9002-8d221a1ceb53
| checkpoint | Insulation has been installed
| checkpoint | Insulation has been installed snug between framing members with no gaps
| checkpoint | Fire rated walls have been sheeted to the ceiling
| checkpoint | Fire rated walls have been fire caulked
| checkpoint | Bathroom walls & ceilings have been sheeted with blue watercheck plasterboard
| checkpoint | Bathroom's sheeted - Set to the floor to allow for good waterproofing junction
| checkpoint | Ensure MSDS & installation guide has been followed
| checkpoint | Final sign off - All post wall work completed as per the above ITP
56aeab57-a8d1-594a-9d62-2f4194ed724b | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Building Authority Checklist |  | Building Authority Checklist | 46828ef8-eeec-4d78-94fb-5108f9bf8dc0
| checkpoint | Ensure all Aland documentation is registered with the council - Atatched below
| checkpoint | Electrical Compliance Documentation reviewed and attached
| checkpoint | Hydraulic Compliance Documentation reviewed and attached
| checkpoint | Mechanial Compliance Documentation reviewed and attached
| checkpoint | Fire Services Compliance Documentation reviewed and attached
| checkpoint | Lifts Compliance Documentation reviewed and attached
| checklist | Basement Tanking |  | Basement Tanking | 4883a5bf-f60e-4028-859b-bea27cdb6f13
| checkpoint | PE film installed towards substrate, grey side facing installer (Blanket).
| checkpoint | Overlap of 100-200mm at ends has been installed.
| checkpoint | Substrate clean, dry & free from dust
| checkpoint | Bentoseal Paste has been used to seal all penetrations.
| checkpoint | Termination of membrane as per manufacturer's details.
| checkpoint | Waterstop RX-101 at vertical spray break with 75mm cover has been
| checkpoint | Installation of CETCO granules to perimeter floor/wall junctions.
| checkpoint | Installation of RX101 to manufacturer's details using Cetseal Bead to secure to substrate.
| checkpoint | Transition Sheet installed as per manufacturer's recommendations.
| checkpoint | Installation of RX101 to perimeter of pile cap, using CetSeal follows manufacturer's recommendations
| checkpoint | Detailing of blanket to perimeter of pile caps as per manufacturer's recommendations.
| checkpoint | All Construction joints are cleaned out and ready for membrane Application
| checkpoint | All Membrane Application is completed in accordance with CETCO Detail / ALAND SIGN OFF
| checklist | Courtyard Surfaces ITP |  | Courtyard Surfaces ITP | 4f5357bc-b764-430b-9f00-b337852ba3ed
| section | Waterproofing
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
85baf17d-ee99-564b-85c2-350dc97ade37 | textbox | Drawing & revision number(s)
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application "No access waterproofing work in progress"
708479fe-eb59-53b7-a5fe-041fd44df4ef | note | Attach relevant photos below
7f46b9d3-b899-5309-a529-59d93d380720 | button | Membrane system & methodology checked off AGainst Aland standard | Yes, No
ab684fb9-ed6e-52d3-a4a4-59270da133c4 | button | Surface preparation as per application guide | Yes, No
| checkpoint | Substrate clean, dry & free from dust
26d367f6-cf20-5c12-b669-50bfc81026e7 | button | Ensure no high points or crevices are in the substrate | Yes, No
3aa84b0c-85fe-5f5d-9545-a6cef2394e64 | button | Ensure substrate is structurally sound & ready to receive membrane | Yes, No
92000e74-afef-5d4f-b538-d7290bfcd3a1 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to primer | Yes, No
d2ca5592-1871-5fc6-92a5-d3cb75bee36f | note | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Ensure all floor wastes & pipes have been primed in accordance with manufacturer's recommendations
aaab720d-5f45-5836-8652-0e406928b14b | note | (PrimeSeal MC to all surfaces at a rate of 3‐4m2/Ltr ‐Alternative primers Multiseal ‐ Primeseal SP at a rate of 5‐8 m2/Ltr)
| checkpoint | All corners, joints, gaps & cracks to be treated with a flexible polyurethane sealant resiflex FC
19aac668-50e8-58fe-8279-c93d9ce6fe7f | note | Apply selected Membrane as per datasheet & application guidelines Ensure sealant has fully cured before installing membrane
| checkpoint | Ensure Humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to first coat
| checkpoint | First coat of selected Membrane to entire areas as per DURAM recommendations
0489b809-a2d4-563e-9712-b461eb26790d | note | Note A total dry film thickness of min 12mm (1200 microns) in two finished coats As such at min
1cabcc3f-b8da-500a-9e1f-d271c571829a | note | Wet Film Thickness of min 075mm (750 microns) per coat is required ‐ Apply membrane at a coverage of 075 ‐ 1 Ltr / m2 per coat
2a12a076-cb23-5b23-b82c-2435718e581d | button | Allowing the membrane coat to dry min 12 hours check the tackiness before applying next coat | Yes, No
60a24d70-1497-5f41-88bf-7eec66d00661 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to second coat | Yes, No
| checkpoint | Second coat of selected Membrane to entire areas as per DURAM recommendations
38f2ef59-3bd1-50af-8448-060ca66fbf32 | note | Note ‐ a total dry film thickness of min 12mm (1200 microns) in two finished coats As such at min
dd085a5d-2adc-5af9-9360-c7aede06873a | note | Wet Film Thickness of min 075mm (750 microns) per coat is required ‐ Apply membrane at a coverage of 075 ‐ 1 Ltr / m2 per coat
a4c0291a-ded6-523e-83dc-72331b8ae4c3 | button | The membrane is to be applied in a minimum of 2 coats at a total coverage of 12 to 2 litres per m2 or relevant product TDS 12 to 2 litres per m2 or relevant product TDS | Yes, No
a8657357-5701-5c3b-be1a-573932dc66fd | button | Allow 2nd coat of Multithane UV min 12 hours but no longer than 24 hours before installing Multithane ATC top coat | Yes, No
8ee12f94-3d71-5b74-9b85-e05438b2e29d | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to final coat | Yes, No
| checkpoint | Apply final coat of Multithane ATC at a coverage rate of 3 ‐ 4 m2/ltr
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instrument
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
5fc1968f-80b3-536a-8bd1-fc0d16813a9d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| section | Surface Finish & Sign Off
| checkpoint | Wastes installed correctly to specification (Correct height / level/ location)
26b06ba7-4f0f-58bd-b4e9-79e84069a220 | tickbox | Waterproofer pushes sponge down 100mm and finishes his membrane & flood test
9832bc5a-bf15-50b3-99d5-96537b4fd778 | tickbox | Waterproofer removes sponge and releases water and puts the sponge back in ensuring there are no debris left in the pipe
d4a72cea-1ffd-53c3-bef7-e29a670d30f0 | tickbox | Aland cleans and removes the sponge
| checkpoint | Waterproofing membrane completed and ready for Pebble Washed Aggregate topper
| checkpoint | Pebble surface installed to specification(s) - Correct level and finish
2f039635-22fc-5305-9945-fafd2baf16c1 | note | Attach photos /comments below
| checkpoint | Final Sign Off - All courtyard works completed to specification and as per above ITP
6bca1e49-baab-521b-a6f0-18c7659161b9 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Car Wash Bay |  | Car Wash Bay | 524af7d9-f5fc-4b41-87bb-68b9f90acd6b
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
e97590a3-32e1-5508-b528-81aae7c95767 | textbox | Drawing & revision number(s)
| checkpoint | Car wash bay installed as per manufacturer's instructions & standards
| checkpoint | Car wash bay tested as per manufacturer's instructions & standards
| checkpoint | Car wash bay commissioned as per manufacturer's instructions & standards
| checkpoint | Final sign off - Car wash bay installed as per the above ITP - Add general photos/comments below
ec81b372-eac9-55d7-8edc-9addb6bdb6eb | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | General Waterproofing |  | General Waterproofing | 54ed34e4-45bb-4b8c-a581-513bd61798c3
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application "No access waterproofing work in progress"
402e0714-cc1a-5cac-a5a3-30139a2ba291 | note | Attach relevant photos below
19c6a676-121b-5f34-92b9-2ea16498b59f | button | Membrane system & methodology checked off AGainst Aland standard | Yes, No
24426ad8-551c-5a30-a163-d5578ec6c98c | button | Surface preparation as per application guide | Yes, No
| checkpoint | Substrate clean, dry & free from dust
1c51297e-115f-5356-ac74-8c47c677c09d | button | Ensure no high points or crevices are in the substrate | Yes, No
a29198a8-289c-5dc7-9315-e1c151c6c780 | button | Ensure substrate is structurally sound & ready to receive membrane | Yes, No
f9aa0798-e60e-5ee6-91c2-cc5f479b6cb0 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to primer | Yes, No
8903894f-1fa6-55f8-8f9a-449b8eb34f1b | note | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Ensure all floor wastes & pipes have been primed in accordance with manufacturer's recommendations
3b41e2d0-be58-516d-b364-15406a7f3ca6 | note | (PrimeSeal MC to all surfaces at a rate of 3‐4m2/Ltr ‐Alternative primers Multiseal ‐ Primeseal SP at a rate of 5‐8 m2/Ltr)
| checkpoint | All corners, joints, gaps & cracks to be treated with a flexible polyurethane sealant resiflex FC
1f3a47e8-320a-5bcf-aa14-4a799e0e8459 | note | Apply selected Membrane as per datasheet & application guidelines. Ensure sealant has fully cured before installing membrane
| checkpoint | Ensure Humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to first coat
| checkpoint | First coat of selected Membrane to entire areas as per DURAM recommendations
43068084-aa77-5eef-925e-b7f8d45fe7b3 | note | Note: A total dry film thickness of min 1.2mm (1200 microns) in two finished coats. As such at min
4243013a-9247-55d2-8bc5-c966b720b8c8 | note | Wet Film Thickness of min 0.75mm (750 microns) per coat is required ‐ Apply membrane at a coverage of 0.75 ‐ 1 Ltr / m2 per coat
e6fd09b5-26ea-5120-9b96-e8a1d950ad59 | button | Allowing the membrane coat to dry min 12 hours check the tackiness before applying next coat | Yes, No
2fd6eb48-6fb8-58ad-a5b9-d652421f3b0e | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to second coat | Yes, No
| checkpoint | Second coat of selected Membrane to entire areas as per DURAM recommendations
3be521cd-d3ee-5cb3-9335-66051dcd37ab | note | Note ‐ a total dry film thickness of min 1.2mm (1200 microns) in two finished coats. As such at min
6174f1fe-c103-5835-ae3f-f5d4334d1565 | note | Wet Film Thickness of min 0.75mm (750 microns) per coat is required ‐ Apply membrane at a coverage of 0.75 ‐ 1 Ltr / m2 per coat
dae2b83b-6c11-5da0-af25-130036344c8b | button | The membrane is to be applied in a minimum of 2 coats at a total coverage of 1.2 to 2 litres per m2. or relevant product TDS 1.2 to 2 litres per m2. or relevant product TDS | Yes, No
dc6d951e-7d69-51e3-95a0-d5da79e7ef6e | button | Allow 2nd coat of Multithane UV min. 12 hours but no longer than 24 hours before installing Multithane ATC top coat | Yes, No
6bfa4ec5-cd4e-520a-9285-51a694af7045 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to final coat | Yes, No
| checkpoint | Apply final coat of Multithane ATC at a coverage rate of 3 ‐ 4 m2/ltr
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instrument
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
bb20ea45-be04-5eef-acde-f6aa6e942c99 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Grease Arrestor Room (v040521) |  | Grease Arrestor Room (v040521) | 563cd798-061b-443d-9935-cfa8b0048af8
| checkpoint | Ensure grease arrestors are installed as per plans
| checkpoint | Isolation valves installed on all grease arrestors
| checkpoint | Switchboards in place using suitable fixings to match mounting service, no damage to external board has occurred during installation
b8e5a085-193b-55f4-8ede-a0cc5dc7a847 | button | Ensure adequate pathways exist within board to accommodate all circuits and allow for future expansion | Yes, No
f80ed013-12c8-5976-84f0-5b340826d6b1 | button | Install and loom in all circuits into correct cabinets | Yes, No
d62f3bd5-df3a-5c75-8ce3-d16de14d3745 | button | Ensure cable labels match switchboard schedule and construction drawings | Yes, No
af7fc247-e513-5fdf-9501-8f792fc427b5 | button | Cables are labelled as per specified requirements | Yes, No
14a6f669-c18c-51d8-951c-8c2307f8b9f8 | button | Check all tightness of all terminals on all breakers and bars | Yes, No
88de5297-bd44-5819-80d2-fa44b2df073b | button | Ensure safety signage is installed and visible as per plans | Yes, No
| checkpoint | Ensure adequate ventilation fans have been installed and are functioning correctly
| checkpoint | Final sign off - Grease arrestors installed as per the above ITP - Add general photos/comments below
f3708f49-e941-505f-be45-dca99685edce | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Lift Pits Waterproofing |  | Lift Pits Waterproofing | 5d24df4c-8f63-4226-bb7b-967d04a982bf
| checkpoint | Area barricaded off to allow no access with signs posted/ visible to include date of application, "No access waterproofing work in progress"
4e721596-d254-5653-a1f0-caba59307248 | note | Attach relevant photos
736c8321-0c55-504e-bf81-6aa9ff4d9f37 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
86e8821c-3d10-55d4-8f91-018976a50693 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
a7b473ea-de91-50c8-a0cf-274a63a1a1a4 | tickbox | Ensure no high points or crevices are in the substrate
98a3cdaf-c903-5f91-9288-af8ccdb00904 | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Dampen the surface to ensure the highest level of adhesion
b1d837a8-d488-5057-b380-59840d0d5e44 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
bc17afa9-363f-523b-be70-b2086b6ff9fe | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
d1b6967b-16d0-5f33-a2af-9c5b5e522e73 | note | Attach relevant photos
| checkpoint | Inspect for any remaining leaks and treat with HydraPlug - Apply selected sealant as per datasheet & application guidelines
c2d8044a-4a90-5be6-abda-5e094b3b5ad5 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
4d1bd1e5-c2df-5026-ba73-bd0be2f757db | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
1fa97d28-9361-506e-ab21-6340660ac843 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
7ee87afc-02df-5bbf-8156-7db09cc9ac5b | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Lift Pits Waterproofing (Balconies) |  | Lift Pits Waterproofing | 5dbe0518-88c2-4e13-b672-b7ac35672007
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
262c532a-f1d1-5dc1-b435-3bc5d7a03377 | note | Attach relevant photos
1de039d5-6b06-526b-bc3a-e709ae6880bf | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
40edfb10-d27e-5674-bef4-e754e538459e | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
7829af99-ebd1-55dd-a38c-d714321aec27 | tickbox | Ensure no high points or crevices are in the substrate
14751be4-686e-54d0-97f2-d3bab5a8453b | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Dampen the surface to ensure the highest level of adhesion
2a8856c1-3d45-5ac7-8a01-527cd80bb922 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
69b09f41-fd05-5663-a7ef-912e57013e72 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydralastic Flex 2K on walls and floors - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines
a53ff521-2146-5b56-a6e7-a9c5f2925487 | note | Attach relevant photos
| checkpoint | Inspect for any remaining leaks and treat with HydraPlug - Apply selected sealant as per datasheet & application guidelines
c51e4a57-c5af-51fd-832e-99ef6e90a472 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
6099071b-c405-509e-a021-2bf89ef60a83 | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
cbbed169-760f-5c10-b477-c17e00e9d81d | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
2232ab23-e5f5-508b-bac7-d9a2093dafcf | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Driveways /Footpaths /Hard surfaces |  | Driveways /Footpaths /Hard surfaces | 5ec5826e-dfcc-4c7a-92a1-0f49dd3d8bfc
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
ab5ccc41-f84e-50a8-8fe5-a803a4ebdb32 | textbox | Drawing & revision number(s)
| checkpoint | All Surfaces have been poured as per specifications
| checkpoint | All Surfaces are at the correct level/falls as per specifications
| checkpoint | All Surfaces finishes are to specification
| checkpoint | Final sign off - Driveways has been completed as per the above ITP - Add general photos/comments below
2a40330b-91e1-515e-8408-55a8360686c5 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Water Connection |  | Water Connection | 63d59745-8f3e-4fd1-b740-69e5c8ca836f
| checkpoint | Water has been installed throughout complex
| checkpoint | Water has been tested throughout complex
| checkpoint | All documentation for water install has been reviewed & documented by Aland
| checkpoint | Final sign off - Water has been tested & installed as per the above ITP - Add general photos/comments below
8ef97bd7-7c07-5af4-99d7-5f323e3866b6 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Suspended Slab - FULL (V140421) |  | Suspended Slab - FULL (V140421) | 67d186b9-b95d-4d90-b816-4509272ec113
| section | Prior to Deck Handover
| checkpoint | Confirm deck is safe, handrails installed and edge protection is provided to full perimeter of deck
| checkpoint | Confirm means of access to deck
| checkpoint | Confirm Formworkers Deck Handover Certificate and ITP is received and sighted
ce2a81ab-b104-5ed6-9ca7-5ed5e0582048 | note | Attached below as applicable
5c56c4d1-0458-5547-bd4c-d115c7b8887b | button | Attach Deck Handover Certificate | Yes, No, N/A
| section | Prior to Concrete Pour
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
0baf93ff-31cf-5e7b-a348-4e6dbb001c34 | textbox | Drawing & revision number(s)
| checkpoint | Materials used complies with design documentation
| checkpoint | Datum point used & soffit RLs checked
| checkpoint | Grids marked by builder
| checkpoint | Confirm As-Built Survey of deck is complete
aa5810a6-a8aa-57b9-a6b3-0e587da00f7f | note | HOLD POINT - Attach As-Built Survey of Deck
| checkpoint | Confirm Form Worker has received As-Built Survey of deck, and has rectified errors prior to any trades commencing on deck
| checkpoint | Confirm all beams and decks constructed as per Structural Concrete Profiles
| checkpoint | Install slip joints to all load bearing walls and corbels where required
| checkpoint | Clean off decks and beams prior to pour, and ensure all exposed off-form soffits are free of any dust, stains and rust marks Hose down if necessary
| checkpoint | Check if concrete has falls, and ensure shutters, timbers, spacers are used to create folds where necessary Cross-check the following drawings
c5d3b216-076d-584a-9130-c401bf913f1c | tickbox | Hydraulic Drawings
340c9d42-5d51-51ff-95fe-6c93468ce98f | tickbox | Architectural Concrete Outlines
3a3374a8-b2f6-5f10-941e-1cb924309dd3 | tickbox | Structural Drawings
| checkpoint | Check top RLs for all reinforcement, ensuring adequate concrete cover Confirm with Concreter
| checkpoint | Confirm that plastic bar chairs are used everywhere, particularly at exposed off-form soffits
| checkpoint | Attach Formwork ITP
| checkpoint | Attach Formwork Engineer sign off certificate Confirm that certificate references props, braces and compliance with design & AS3610
320b8424-204b-5776-8728-6d867ea9e339 | note | Attach Formwork Engineer's Certificate
| checkpoint | Attach ALL Services Hydraulic ITP (for cast-in elements), include relevant mark-ups below
| checkpoint | Attach Precast ITP (for cast-in elements), including relevant mark-ups
| checkpoint | Attach Reo Fixing ITP
| checkpoint | Attach Principal Structural Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
68674972-de10-55bf-b976-ead77cced679 | note | Attached below as applicable
| checkpoint | Attach Post Tensioning Engineer Inspection Report, and confirm that all actions are closed out with photos sent to engineer
62953734-9d32-50b8-83ff-68ef88d7649b | note | Attached below as applicable
| checkpoint | Check quantity of concrete required prior to ordering
587c5a52-076f-5c93-ac63-de85052b25cc | textbox | Total m3 (as measured by Site Engineer)
a57e8b20-584a-5627-bb76-468bf32d967d | textbox | Total m3 (as measured by Foreman)
| checkpoint | Confirm MPa, slump and agg size of concrete prior to ordering
ba96cce3-8f4d-5c44-a281-2636c60e9885 | textbox | MPa
2da17568-ef8f-58bb-85c0-67a7f6b2cc48 | textbox | Slump
8df038cc-25f4-5b95-8950-a4eacf78d8a4 | textbox | Agg
| section | During to Concrete Pour
| checkpoint | Ensure concrete truck dockets have correct concrete strength, and attach delivery docket from each batch
| checkpoint | Confirm concrete has falls to drainage points in slab
| checkpoint | Ensure a representative from each of the following is on site and witnessing the pour
10f29766-edbe-5f5f-bdea-129de46bed42 | tickbox | Formworker
89acb7d2-47ce-5667-a226-10cb76886b71 | tickbox | Electrician
eba93cd6-6aad-5f0f-9c46-5d4b7d18f4b8 | tickbox | Plumber
624e3d6b-f3cb-5d67-8b58-a2c862331379 | tickbox | Post Tensioner
0743d567-be35-53b0-a627-76d85b6eadcc | tickbox | Precast Installer
| checkpoint | Confirm Form Worker has labour below deck inspecting all joints (particularly at columns & walls) and is immediately cleaning any slurry
| checkpoint | Confirm that all protection to precast panels is maintained at all times during concrete pour
| section | After Concrete Pour
| checkpoint | Confirm Surveyor is out next day to carry out survey of finished concrete Attach As built Survey Plan
ed33b7e8-6771-585f-8c7a-e807e7293f58 | note | Attached below as applicable
| checkpoint | Confirm tolerance of finished concrete surfaces are in accordance with the specifications
| checkpoint | Confirm saw joints are installed to engineers requirements
| checkpoint | Confirm finish of concrete is adequate for application (broom/trowel/helicopter finish), refer to AS3610
| checkpoint | Obtain all concrete tests at 1 day, and attach test results
3b06d852-abb5-553d-b4f7-11be0a7b5f25 | textbox | Test Strength Mpa
| checkpoint | Confirm initial stress is conducted day after the pour, after concrete has reached 10 MPa on 1 Day results
| checkpoint | Obtain all concrete tests at 4 day, and attach test results
a3d2e37c-4e44-5c9c-b3b5-9e1b1adb3121 | textbox | Test Strength Mpa
| checkpoint | Confirm final stress has occurred after concrete has reached 22MPa, and attach Stressing Records
879567ad-3b4b-5dd0-a4cb-1f852e80f32a | note | Attached below as applicable
| checkpoint | Obtain all concrete tests at 7 day, and attach test results
e7dbc640-f336-551c-b627-1c278d2d7f0d | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 28 day, and attach test results
69cbdff0-d5d7-5552-ac9b-0875e4d8d01e | textbox | Test Strength Mpa
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
cdc55010-641e-5d78-9b06-4f0710e0d516 | button | Subcontractor Sign Off | Yes, No, N/A
bc36973c-7bef-5f9b-8957-55efb6408772 | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Soft Landscaping |  | Soft Landscaping | 6842d8d5-5c7b-44c3-8694-d6f3cdc2839b
| checkpoint | Ensure all plants are planted as per drawings
| checkpoint | Irrigation installed as per drawings
e5963f65-7708-56ce-b4ef-c98f8246fe85 | button | Irrigation leak tested | Yes, No
| checkpoint | Outdoor furniture installed as per plans
| checkpoint | Final sign off - All soft landscaping completed as per the above ITP - Add general photos/comments below
619e0e5b-cbf4-5474-8ebc-6b4f005695dd | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Floor Wastes |  | Floor Wastes | 6ba1f22c-c521-4d64-9108-b055fd2a162c
| checkpoint | Plumber checks all pipes for any cracks, or imperfections
38861ccf-26a3-5ab8-8190-0da5b8898a2b | button | Plumber completes stack work | Yes, No
ad2f4760-dd2b-539a-b2d8-fa9dab75e1c3 | button | Plumber cuts waste flush with concrete and puts sponge inside | Yes, No
d16bb4b7-86e4-5a6d-b6c8-038f05b45c2a | button | Plumber caps off all other pipes | Yes, No
| checkpoint | Waterproofer pushes sponge down 100mm and finishes his membrane & flood test
| checkpoint | Waterproofer removes sponge and releases water and puts the sponge back in ensuring there are no debris left in the pipe
| checkpoint | Tiler accepts that the waste is clean and has a sponge in it
| checkpoint | Tiler completes his works (i.e sand cement & tile)
| checkpoint | Aland cleans and removes the sponge
| checkpoint | Final sign off - All floor wastes completed as per the above ITP
be201806-9a51-5b9d-bc19-3dc7a08bd860 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Fire Pump Room (V90421) |  | Fire Pump Room (V90421) | 6c91df38-ed4b-49c2-a10a-ddf25e05dfb1
| checkpoint | Fire pump isolation valves installed on all pumps
| checkpoint | All pipe work tested to min 1200 kpa
| checkpoint | Pour concrete plinth for each fire pump
7d519572-ee25-5627-93fd-8988226ed148 | note | Check height and dimensions as per drawings/specifications
| checkpoint | Switchboards in place using suitable fixings to match mounting service No damage to external board has occurred during installation
2c2492a5-4c11-5dde-a22f-2dc8fd9186bb | button | Ensure adequate pathways exist within board to accommodate all circuits and allow for future expansion | Yes, No
ad420682-95e2-5795-b6be-5b4aafc8707e | button | Install and loom in all circuits into correct cabinets | Yes, No
30254168-1660-58d9-aee5-984b826fcdaa | button | Ensure cable labels match switchboard schedule and construction drawings | Yes, No
1ebe5844-f4cf-5d67-908e-262e16fc522a | button | Cables are labelled as per specified requirements | Yes, No
ff45423e-07a7-5760-af37-1a2e7f1e880f | button | Check all tightness of all terminals on all breakers and bars | Yes, No
| checkpoint | Ensure 1m Clearance around fire pumps
| checkpoint | Ensure minimum 2m Height clearance - To floor or finish above
| checkpoint | Ensure safety signage is installed and visible as per plans
| checkpoint | All PvC pipes to be fire rated within pump room
| checkpoint | FIP commissioned & is recognising fire pumps within the system
| checkpoint | EWIS speakers installed as per manufacturers instructions
| checkpoint | Final sign off - Fire pumps installed as per the above ITP - Add general photos/comments below
81d12469-8946-5b9c-b257-fca487f46a0b | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Garbage Chutes Waterproofing |  | Garbage Chutes Waterproofing | 707b2e46-6ee2-465c-9922-3c2a81e47709
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
7e2ee46a-4139-52c1-acd5-7c1ca0c45700 | note | Attach relevant photos
578a1bc5-2a4a-5396-aa8a-34520ad50ede | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
02f2c09a-ca87-56a5-b5d1-543e295c690a | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
8f2916af-6d0e-55b4-ba0b-5aaa8de8fdaf | tickbox | Ensure no high points or crevices are in the substrate
c81044bc-8dc2-5574-be11-ca3a40fa88a8 | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
8369c111-d48f-5cd2-9aba-717a17468b89 | note | Attach relevant photos
| checkpoint | Primer substrate (walls and floors) with Polybit Hydrapoxy - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
ffec79eb-92e1-5273-9aeb-0ac7aa7c8a62 | note | Attach relevant photos
| checkpoint | Apply angles to builders FFL as required.
cf4f96f7-a105-5360-84a9-e7b772df9a5b | note | Attach relevant photos
| checkpoint | Seal all joints, gaps, cracks and penetrations with Polybit HydraFlex polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
f944b767-abe2-52ff-9437-a30d0cf13b97 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydraguard PU on floors with a turnup of 250mm on walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
90a61847-1614-5296-82ce-a65efe9c27b3 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard PU on floors with a turnup of 250mm on walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
5e738ed9-06e8-5797-b8c4-0ac918151a19 | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
74a8b01e-1175-5bb2-bac6-737a1ac131a2 | note | Attach relevant photos
| checkpoint | Apply 2 coats of Polybit Hybrid 150 waterbased polyurethane membrane on walls as required. - Apply selected membrane at a rate of 1.0 litres/m2 per coat as per datasheet & application guidelines
a7cd0dab-7d0a-5a76-9e54-8f86b6d3a3c1 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
204eca86-ef38-5a87-bcc1-cca5775e3a39 | note | Attach relevant photos
| checkpoint | Conduct a flood test to garbage chute area.
2c01ef80-c223-589e-9103-09b04d20dbb2 | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
8066cba7-142c-58b5-a60e-e8c3f11e3c70 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
7f904454-dabb-566d-8287-1051e42c948c | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Fire Sprinkler Tanks Waterproofing |  | Fire Sprinkler Tanks Waterproofing | 70af7417-a2d9-4ef8-afc9-f3dafc945a4a
| checkpoint | Area barricaded off to allow no access with signs posted/ visible to include date of application, "No access waterproofing work in progress"
6a237308-4bb2-59fe-97f7-bdac5e5f346c | note | Attach relevant photos
6dbb0fe8-4056-5d8e-b2ef-536dfcb5e0ad | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
015a6a33-5b9e-5c71-bdda-6c01d21565c7 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
1adb6eb8-37d2-5458-97af-8037a74a9967 | tickbox | Ensure no high points or crevices are in the substrate
0ed98412-2d56-54a5-9664-8910f8ba808f | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Fatra Fatrafol 807 PVC membrane to be used. - Apply selected membrane as per datasheet & application guidelines
5189d739-890d-5a79-b268-798e8007375d | note | Attach relevant photos
| checkpoint | Inspect for any remaining leaks and treat with HydraPlug - Apply selected sealant as per datasheet & application guidelines
4db8831d-f1fc-5cfa-8f1a-d68529baf9a8 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
6ce83aaf-aa37-52e2-bf4f-37c9f344353b | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
b2c9966c-beb4-56a7-8df6-e69a4ffa8aca | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
4e565c0a-929a-5318-a01a-2eff5440fbe3 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Planter Box Waterproofing |  | Planter Box Waterproofing | 71089875-20ba-488a-8635-ec3d645abe5a
| checkpoint | Area barricaded off to allow no access with signs posted/ visible to include date of application, "No access waterproofing work in progress"
8847a929-9285-566b-87f0-6d1ec12a6eaf | note | Attach relevant photos
| checkpoint | WP details listed at architectural drawings for clarifications are followed.
| checkpoint | All floor should be with proper falls towards the floor waste with a min. 1:100 slope.
4f09ea72-d3a2-5e59-8b20-fcf0659ac56e | note | Attach relevant photos
2f93aeae-f775-552d-afaa-420b998bb68f | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
ee42fe3a-4f84-58e9-b010-930fb9d549b5 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
652d2814-9948-56d8-800f-a88b47e26eaa | tickbox | Ensure no high points or crevices are in the substrate
41b083ed-27d0-5837-8a65-6c95cb44e40e | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
ae63613e-2692-555b-ad7d-87879fc8a758 | note | Attach relevant photos
| checkpoint | Primer substrate with Polybit Hydrapoxy - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
9ef50ae9-fd0d-5c7b-8521-0677e9d22b6c | note | Attach relevant photos
| checkpoint | Seal all joints, gaps, cracks and penetrations with Polybit HydraFlex polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
b78d180b-4434-5f64-a00f-b58b2a0c8b3c | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydraguard AR100 on floors and walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
16ad4e31-73d2-5159-a576-29b5275c2bbf | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard AR100 on floors and walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
9592acbd-364c-56ae-9e4f-955a44f75350 | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
| checkpoint | Attach photos for the drainage conduit.
22d2c760-e19e-5c89-af2c-f49d1a98fcef | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
d36e4172-09a3-5420-ab00-e37cfcfe0623 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
21ab3d2c-db95-50c4-9b8e-8298676bfdd2 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Garbage Rooms Waterproofing |  | Garbage Rooms Waterproofing | 74f1454d-8fc8-4e7d-965e-1795b01b63b7
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
aecac3cf-6b83-5d39-b56d-9ae03d74c24e | note | Attach relevant photos
86e4f8f5-6be7-5a15-899c-23b07cb8e5d0 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
eccffbce-b41b-53b6-81b0-c8ab0fe0b5ca | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
850250c1-1232-5494-b0da-c0befe40c9ca | tickbox | Ensure no high points or crevices are in the substrate
858bdcd1-581d-50f5-8555-2aa075f52e99 | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply 1st coat of Duromix Hibuild WBE epoxy primer to walls and floors - Apply selected primer at a rate of 1.5m2/L as per datasheet & application guidelines
48ab4488-b5d4-5a2e-a91a-a93db29daf95 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Duromix Hibuild WBE epoxy primer to walls and floors - Apply selected primer at a rate of 1.5m2/L as per datasheet & application guidelines
a423ec5f-002c-56b1-814c-65917d195bb8 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Duropoxy SLR100 epoxy top coat to walls and floors - Apply selected top coat a a rate of 6.6m2/L as per datasheet & application guidelines
70d66891-a6e1-593b-8963-af91e600b32f | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Duropoxy SLR100 epoxy top coat to walls and floors - Apply selected top coat a a rate of 6.6m2/L as per datasheet & application guidelines
bfad7ddc-8641-59f8-b541-6ab8e97c820d | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
4a7fe84d-c5ad-5681-aef7-06768141781a | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
57a022ea-ffbd-54c3-af6d-550ba1ab658c | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
f84acf2e-1f36-5047-bfa8-30180a6d8226 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Services Fit Out |  | Services Fit Out | 786a8105-a26a-47fc-9888-f3fe559f4328
| checkpoint | All plumbing fitout have been tested & commissioned
| checkpoint | Final running test of all plumbing items
| checkpoint | All electrical fitout have been tested
| checkpoint | All intercom points are installed & are level & in correct location
| checkpoint | All security systems have been installed & tested
| checkpoint | NBN has been tested & commision
| checkpoint | Air con has been final tested & commissioned
| checkpoint | Test fire doors install as per code closing & gapping around door
| checkpoint | Fire door hardware test holes, closers & locks
| checkpoint | Final sign off - All services fit out work completed as per the above ITP
84f3b768-75f7-5fbc-b96e-263b2d586e3e | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Hydraulic Groundwork |  | Hydraulic Groundwork | 79b47a0e-1435-4650-917f-6bb581530b32
| section | Pre-Commencement
| checkpoint | WorkSafe notification prior to trenching below 1.5m deep has been submitted
8a8fdedd-902c-51b6-aae0-91bb913b354f | note | If notification is required attach documents below
871b0d6a-47ac-5f91-9377-ac019574513e | button | If required, trench shields are on site & ready for use | Yes, No
5468355e-3ba6-51cb-b90e-6a63e99495fb | button | Dig Permit completed & attached | Yes, No
adc9f29a-f8c7-5ad7-9f7c-2872f9d7e988 | button | Exclusion Zones have been erected as required (Attach photos) | Yes, No
| checkpoint | Works have been coordinated with other trades
| checkpoint | Excavation depths & locations confirmed prior to commencement
| checkpoint | Approval given to Trade Contractor to commence stormwater installation
| section | Excavation Works
| checkpoint | Excavation Checked, Correct & Approved
d20ea241-1ba6-5c51-9ef1-63ca1c7fea9f | tickbox | Depth Accurate
a4511b2b-13dd-5c6c-885c-324bd27a7bd1 | tickbox | Width Accurate
| checkpoint | Excavation works - completed to specification/drawings & Area left clean/tidy
d921aff5-a38b-5e82-bcc4-9047a30c3101 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| section | Stormwater Installation
| checkpoint | Pit installation correct
4daa0cef-1cbf-5cbd-a26f-0cabfca677e1 | button | Pit size correct | Yes, No
c94e1076-e1a7-5ac1-ab68-610c309791f2 | button | Pit location correct | Yes, No
914af939-e6cf-54ce-a207-6c66aa78950c | button | Pit invert levels correct (In & Out) | Yes, No
99633e78-4867-5c10-8cca-2b7347c47c53 | button | Pit finished RL correct | Yes, No
c7789472-5590-5c31-b5f1-fe6c653dceed | button | Pits covered & made safe | Yes, No
| checkpoint | Bedding material is installed & correct to support service
| checkpoint | Pipe installation correct
fbaca336-3e0a-560a-801b-078be015bc32 | button | Pipe size correct as documented | Yes, No
8cf8ca45-dc81-53b8-b1a0-a3dceb777674 | button | Trenches have been backfilled & compacted correctly | Yes, No
a7d7a654-47e0-5fc2-8aa0-ef71f5ae7595 | button | Service location tape Installed (if applicable) | Yes, No
| checkpoint | Provisions for Aggie Pipe Connection installed as documented
| checkpoint | Expansion Lagging has been installed where service will be cast into concrete
| checkpoint | Stormwater install completed to specification/drawings & Area left clean/tidy
cbf1d00e-7a11-5025-963b-007f87c3b952 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checklist | Shotcrete |  | Shotcrete | 7db0d099-1916-4760-8487-ba259ce69298
| section | Pre - Spray
| checkpoint | Ensure services/drainage correctly installed
| checkpoint | Location of spray & heights checked and confirmed
| checkpoint | Starter bars installed correctly
| checkpoint | Correct mesh installed to meet required specification
| checkpoint | Covers checked and acceptable for respective area
| section | Shotcrete Spray
| checkpoint | Correct concrete delivered, attach delivery dockets
| checkpoint | Spray application correct & spoil removed
| checkpoint | Spray completed and required finish achieved - correct heights achieved
| checkpoint | Final sign off - All shotcrete completed as per the above ITP - Add general photos/comments below
aae66644-6729-589f-9161-0d0d0eb0f552 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Gas Connection |  | Gas Connection | 8a4f3ba7-3906-4ccb-9c5b-65b99c6641a5
| checkpoint | Gas has been installed throughout complex
| checkpoint | Gas has been tested throughout complex
| checkpoint | All documentation for gas install has been reviewed & documented by Aland
| checkpoint | Final sign off - Gas has been tested & installed as per the above ITP - Add general photos/comments below
153eec2f-4fa1-52ab-a4ba-0c4a5cc8ea9f | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Sheet Pile ITP |  | Sheet Pile ITP | 8f32f146-50e7-41f4-adbe-eb2335e7617d
| section | Foundation Pile Information
| checkpoint | Pile Diameter
391a030b-6900-5e4b-8bf3-43aee267e3b4 | textbox | Diameter (mm)
| checkpoint | Approval of Socket
185e23bc-dee2-5d21-a229-f91fd43c1a17 | textbox | Designed Pile Socket Length (mm)
1b4a42b8-fec2-59ef-9499-fecb5de03649 | textbox | Actual Pile Socket Length (mm)
| checkpoint | Pile Details
5488e7dc-0f5e-5c39-8f24-6cc758f205a6 | textbox | Top of Steel RL (m)
f04273e5-8643-5333-8006-25a23d0d6ed8 | textbox | Length of Pile (m)
e055efbc-35d1-5298-b841-47160b096081 | textbox | Top of Concrete RL (m)
| checkpoint | Check of excessive water in hole
| section | Pile Reinforcement & Pre Pour
| checkpoint | Reinforcement information
9fa08c68-84c6-5ac1-bb3c-050338e2c3e1 | textbox | Main Bars
ee353170-7904-5f45-a91c-632cd76e45f6 | textbox | Ligs
03e55353-d31e-5497-a588-82895382775c | textbox | Cage Length
| checkpoint | Engineer/Building Surveyor Sign off
| checkpoint | Commencement of Pour – Ok to pour
| section | Pile Concrete Placement
| checkpoint | Date of Pour
| checkpoint | Concrete Delivery Docket
| checkpoint | Pile Concrete Details
c5d5c4d2-ce6b-5bc8-a590-0efd72ecac04 | textbox | Concrete Strength (MPA)
d0b4ad3b-c75c-5ad6-845e-98cb33f6e399 | textbox | Cover (mm)
| section | Pile Post Pour- Sign off
| checkpoint | Post Pour requirement
d4129860-f5c9-5ff9-8e65-709ed9158c8a | textbox | Concrete Test Certificate number
cab8b1c1-b55d-5c84-911b-8d72af533dbb | textbox | 28 /56-day Concrete Compressive Strength (MPA)
| checkpoint | Post Pour Signed off
| checklist | Pad Footings, Strip Footings, Lift Pits & Piles (V140421) |  | Pad Footings, Strip Footings, Lift Pits & Piles (V140421) | 90ecf608-dd34-4db3-8785-444ca93136fc
| section | Prior to Concrete Pour
| checkpoint | Attach mark-up plan
| checkpoint | Confirm RL of sub-base
| checkpoint | Confirm position of footing is in accordance with architectural setout design
| checkpoint | Confirm starter bars to columns and walls installed in correct location
| checkpoint | Check for reinforcement cover as per structural documents (especially at steps and ramps)
| checkpoint | Obtain certificate from Structural Engineer and Geotechnical Engineer prior to concrete pour Attach certificates
| checkpoint | Confirm waterproofing details installed as per manufacturer's specifications Attach waterproofer completed ITP (Applicable to Lift Pit Only)
| checkpoint | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
7445f82d-f77c-5f57-b00a-17e82b00bfc0 | note | Attach photos prior to concrete pour
| section | After Concrete Pour
| checkpoint | Confirm tolerance of finished concrete surfaces
2953a4ac-1970-5f6d-aa26-b59651ed95ea | tickbox | 50mm +/- in correct plane
e3976c4c-f6bb-5bbf-afb0-952fbd2a8e64 | tickbox | 50mm +/- from 30m straight edges
| checkpoint | Obtain all concrete tests to be carried out on all concrete pours
779064a6-80df-55bd-bd73-75da167469b4 | note | Attach Concrete Docket/results below
| checkpoint | Check concrete strength results complete with specification
9011b34a-a151-53ea-89f3-20d3e257532e | note | Attach results below as applicable in line with specifications
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
d77e00a4-b62d-567f-b697-6368f17b9dc0 | button | Subcontractor Sign Off | Yes, No, N/A
591f19b9-e9de-5020-a419-777bd8e57943 | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Electrical Rough In |  | Electrical Rough In | 93854234-c196-41fa-8e74-3f9762c93f98
| checkpoint | Power points have been installed as per the electrical plans including shaving cabinet strip light
| checkpoint | All points & switches are in a functional area
| checkpoint | All comms are installed to allow for good detailing around
| checkpoint | GPO's are correct for air conditioning & functional
| checkpoint | NBN provision conduits (draw‐wire) 1mm installed
| checkpoint | Fire rating peno's completed in lobbies
0a712df0-8c69-5e9e-9fb5-8799e6fea801 | note | Relevant photo's/register has been completed
| checkpoint | Final sign off - All electrical work completed as per the above ITP
83cc493d-f3f0-5519-9e90-78243be661a3 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Stairs |  | Stairs | 93f9d448-5ff4-4600-8e3d-9bcf29871f2d
| checkpoint | Land stringers & backdrops secured
| checkpoint | Datum RL supplied by surveyor pour height marked
| checkpoint | Couplers & rebate boards installed
| checkpoint | Riser heights confirmed
| checkpoint | Going lengths confirmed
| checkpoint | Correct Class of Finish
| checkpoint | Couplers & rebate boards installed
| checkpoint | Riser heights confirmed
| checkpoint | Going lengths confirmed
| checkpoint | Ensure lighting has been installed in stairwells as per plans
| checkpoint | Final sign off - All stairs completed as per the above ITP
a3a90b7b-4205-534e-86f7-52f73970a2fe | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Excavation & Shoring |  | Excavation & Shoring | 9e21872e-99f4-45fd-ba3f-bb0e81809d65
| section | Shoring
| checkpoint | Locate all existing services
| checkpoint | Confirm set out - Ensuring piling/spring remains within inside boundary
| checkpoint | Confirm any vibration limitations/requirements
| checkpoint | Confirm boundary set back to shoring wall
ebd40d17-6afd-5605-ac1e-0d16c8e64509 | button | RL levels to top of shoring wall confirmed | Yes, No, N/A
| checkpoint | Confirm de-stressing procedure for anchors with engineer
0e2faf87-80ae-5f19-9ebe-7badd5dcc41c | note | Engineer procedure notes added below
| checkpoint | Confirm level of excavation aligns with shoring wall levels/location
| section | Excavation - Pre-Commencement
| checkpoint | Confirm dial before you dig documents are onsite - If applicable and attached below
| checkpoint | Confirm correct disposal of classified material
| checkpoint | Obtain geotech report, including load bearing capacity
4d9d3d55-aecb-5f5d-a05c-ec88d4be888a | note | Geotech report referenced or attached below
| section | Excavation Works
| checkpoint | Collection of tip dockets - If applicable and attached below
| checkpoint | Confirm set out of boundaries & marked out
| checkpoint | Confirm actual RL is within design tolerance
4a3b1ddc-048e-5db8-a9d9-885537625c72 | button | Confirm set out of footings and pads | Yes, No, N/A
f433b594-78c8-5558-9b23-8c15ba49a5e4 | button | Confirm set out of in ground drainage | Yes, No, N/A
731fd64b-0aae-5f9e-ac76-5067a26fefe3 | note | Excavation of footings not to exceed size as detailed on structural drawings
| checkpoint | Certifier to inspect foundation in accordance with specifications
| checkpoint | Geotech inspection of footings etc
6a4fc736-68b9-59e6-899f-227b0390ec50 | note | Geotech report referenced or attached below
| checkpoint | Confirm top of concrete footings is below surrounding finishes
| checkpoint | Confirm sub-base is in line with engineers specifications/requirements
76d8e1e9-ad45-5f34-9a35-4683aa683dd1 | textbox | Minimum thickening (MM)
| checkpoint | Civil engineer inspection carried out - Attached below as applicable
| section | Sign-Off
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
b1ec5327-a78f-5100-acde-cf2f68363bc2 | button | Subcontractor Sign Off | Yes, No, N/A
74ac8c30-9a8b-59e7-9862-5c15b609b93e | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Rain Water Pump Room (v040521) |  | Rain Water Pump Room (v040521) | a11fb9f1-7f1b-4e43-ae7e-ec5fb0792b8c
| checkpoint | Ensure rain water pumps are installed as per plans
| checkpoint | Pump isolation valves installed on all pumps
| checkpoint | All pipe work tested to min 1200 kpa
| checkpoint | Switchboards in place using suitable fixings to match mounting service, no damage to external board has occurred during installation
36eee77f-626b-5469-aefe-ccf1bfe22746 | button | Ensure adequate pathways exist within board to accommodate all circuits and allow for future expansion | Yes, No
0cf6a292-e351-5979-a098-4cf00f39bcea | button | Install and loom in all circuits into correct cabinets | Yes, No
18e6feda-b953-5b00-ad9c-27ba62155daf | button | Ensure cable labels match switchboard schedule and construction drawings | Yes, No
89089400-6c38-5259-88fb-4af98b279c44 | button | Cables are labelled as per specified requirements | Yes, No
31d43597-7048-5bd3-a7a6-856cac29a648 | button | Check all tightness of all terminals on all breakers and bars | Yes, No
9dcb657f-6bd3-56a6-b0eb-33621a41aad1 | button | Ensure safety signage is installed and visible as per plans | Yes, No
| checkpoint | Final sign off - Rain water pumps installed as per the above ITP - Add general photos/comments below
7e2c92aa-43fb-5b17-b334-c0529e0e6000 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Detailed Excavations |  | Detailed Excavations | a21c80f8-b30d-4274-bb8d-131623ab6a53
| checkpoint | Excavation depths and locations confirmed prior to excavation commencing
| checkpoint | Any batters formed correctly
| checkpoint | Any trenches/ pits / hazardous areas appropriately isolated
| checkpoint | Any soft spots identified and appropriate remedial completed
| checkpoint | Excavation checked, correct and approved
| checkpoint | Bulk Excavation completed, reviewed and approved
| checkpoint | Relevant inspections completed and attached
| checkpoint | Final sign off - All detailed excavations completed as per the above ITP
0cf9c33b-33b9-589e-86a4-584c2c59bed2 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Power Connection |  | Power Connection | a21ddcd8-2db3-4c2c-b0d2-b1beb7dd7221
| checkpoint | Power has been installed throughout complex
| checkpoint | Power has been tested throughout complex
| checkpoint | All documentation for power install has been reviewed & documented by Aland
| checkpoint | Final sign off - Power has been tested & installed as per the above ITP - Add general photos/comments below
277ba132-575f-5b05-b5d4-4357ae82395d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Internal Wet Area (Bathrooms & Laundries) Waterproofing |  | Internal Wet Area (Bathrooms & Laundries) Waterproofing | a4d176a2-8e48-4faf-9a1d-8012c770d695
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
dbc8daa9-7f98-5eb5-9c23-308d6a70f586 | note | Attach relevant photos
7ec79f64-a54f-5255-b0c4-4b37f6cdc280 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
bbe622b0-5024-53d0-be06-ceffb17e5cc0 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
8ed5610f-d75b-5cf6-8d13-4384099bed4c | tickbox | Ensure no high points or crevices are in the substrate
feba587f-b11b-5608-8551-ead38718327e | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
9ae71bd7-5401-54ee-9908-eec154f9dd28 | note | Attach relevant photos
7f7edbfe-49ea-5a5d-9072-5496770d2b4f | tickbox | Ensure all floor wastes & pipes have been primed in accordance with manufacturer's recommendations
dbf61ea5-99f2-57cd-93c3-a5755138b0be | tickbox | Shower Angles in correct position & level
1da26b9c-8a8f-5d87-8e49-90297b7ae982 | tickbox | Door Angle is in correct position & level
3d031938-830b-5916-a345-04b5614c6db6 | tickbox | Door & Shower Angle are 3mm gauge aluminium
39ab1f0a-bdf8-527f-b49a-6e5d3b97c243 | tickbox | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations
| checkpoint | Primer substrate (walls and floors) with Polybit Hydrapoxy - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
2f8a99fe-2347-55b9-a9f0-5392ce224e9d | note | Attach relevant photos
| checkpoint | Apply angles to builders FFL as required.
cc02b115-9436-5f64-9320-17cf15673154 | note | Attach relevant photos
| checkpoint | Seal all joints and penetrations with Polybit HydraFlex polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
36b74959-df08-54ac-991c-f71dcc0f49f5 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydraguard PU on floors with a turnup of 250mm on walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
c763003c-eb1b-5f78-b4bf-8fd45648ce6c | note | All floor wastes membranes to be turned down into floor waste
| checkpoint | Waterproof walls of shower section up to ceiling. Seal taps & the like. 2x coats required.
00872616-614c-5fcf-9c83-fef283eebc4f | tickbox | Min 150mm kicker has been waterproofed (do width of roller 230mm)
d87b41c4-7f83-5570-abf1-1ecb5738cb71 | tickbox | Min 1500mm past shower screen has been waterproofed.
5ec4dba6-5930-51b1-aa38-9905b25a1197 | tickbox | Waterproof all shower & adjacent walls
1c942318-9dc2-5c74-b298-444557e0440f | tickbox | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations
cfad9a5d-3449-5db8-a173-d8bafea15bf7 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard PU on floors with a turnup of 250mm on walls - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
5544714f-2172-516e-9b4c-190ae5282a96 | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
a72c6ce0-ae15-5f66-93e9-80ca34204de6 | note | Attach relevant photos
| checkpoint | Apply 2 coats of Polybit Hybrid 150 waterbased polyurethane membrane on walls as required. - Apply selected membrane at a rate of 1.0 litres/m2 per coat as per datasheet & application guidelines
1b0251ce-7bc2-5ca2-b7a2-a47acfbaf084 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
99e49f35-c699-5c01-b676-4f5fc2ac1fc5 | note | Attach relevant photos
| checkpoint | Conduct a flood test to internal wet area.
7d55c241-d4bb-5b6d-a12f-879a4418b01b | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
29c2984d-3538-5880-b0b4-438d5f51f3f4 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
31698fb0-535a-5190-a3f5-9782b6ae9c40 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | NBN Connection |  | NBN Connection | a6d38751-b79f-4377-9b63-836b56188b03
| checkpoint | NBN has been installed throughout complex
| checkpoint | NBN signal has been tested throughout complex
| checkpoint | All documentation for NBN install has been reviewed & documented by Aland
| checkpoint | Final sign off - NBN has been tested & installed as per the above ITP - Add general photos/comments below
33870dcd-3399-51e1-b332-e5a4f8de4edd | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Waste/bin rooms |  | Waste/bin rooms | aab86d63-23db-465c-848e-21c7ce461e2c
| checkpoint | Area barricaded off to allow no access with signs posted/ visible to include date of application, "No access waterproofing work in progress"
71237afc-36c0-5c48-a94e-7a4ee7fca05a | note | Attach relevant photos
5aeb91ce-7fc1-5c60-b621-2016722a8599 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
b920adcf-ceca-552d-bdb4-c44092e45a40 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
692ce4f9-421a-50dd-87a5-5cf859b23381 | note | Attach relevant photos
| checkpoint | Primer substrate with Polybit Hydrapoxy- Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
c7c6cf50-df02-5c5f-b903-4948e5da29b1 | note | Attach relevant photos
544ad343-99b7-5e96-b343-fc8868fe9c7e | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydrapoxy flooring on floors and walls as per datasheet & application guidelines
13a7b423-7c89-57ab-9d8d-9a8fdc685819 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydrapoxy flooring on walls and floors - Apply selected membrane as per datasheet & application guidelines
dd779845-a267-581d-b380-c6cd63f41a66 | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
ab7d643b-82ba-59f0-b01f-8122f14d4577 | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
b6c97615-d168-5fed-9c31-e56cdbcd25be | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | KONE - Lifts |  | KONE - Lifts | ab3e3402-b73a-40eb-b05e-352e7104582a
| section | Details
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
bf63164f-c945-5274-a8bc-7d2ad714c73e | textbox | Drawing & revision number(s)
| section | Complete before KONE starts on site
| checkpoint | Waterproof the pit & shaft
| checkpoint | Weather & water protect lift lobby areas on all floors
| checkpoint | Complete all penetrations as per KONE drawings
| checkpoint | If steel construction - provide fixing points for rail brackets & lift doors according to KONE drawings
| checkpoint | Provide accurate grid, datum & RL lines
| checkpoint | Provide lighting in the lift lobbies & stairwells
| checkpoint | Provide permanent access stairs to all floors
| checkpoint | Provide public access to top floor life door with the control cabinet Control cabinet must not be in a private dwelling space
| checkpoint | Build in all lifting points por beams as shown on KONE's drawings
| checkpoint | Provide access so that equipment can be installed into the lift well Special holes may be required Guide rails are 5m long
| checkpoint | Guard lift door openings in accordance with AS 4431
| checkpoint | Provide space for our site personnel accommodation that is safe, clean & dry
| checkpoint | Provide on site water, lighting & sanitation
| checkpoint | Provide adequate space for storage of all lift equipment & all tools near the site accommodation that is secure, safe & dry (approx 50 sqm per lift)
| checkpoint | Remove all builders equipment, materials & rubbish from the lift well & lobby areas in front of the lift well doors
| checkpoint | Install permanent sub mains & dedicated telephone line to the top floor served terminating at the location nominated by KONE & provide 415V (5%) 3 phase + neutral + earth power supply Max fault level of 6kA
| section | Complete while KONE is working onsite & prior to practical completion
| checkpoint | Protect lift doors, architraves & lift fixtures from damage prior to lift hand over
| checkpoint | KONE to place rubbish & excess packaging into bins on site provided by Aland
| checkpoint | Security sub contractor to finalise security interfacing & operation
| section | Complete at any time that is suitable for Aland
| checkpoint | Supply & install any associated wiring that is required external to the lift shaft
| checkpoint | Install any fire control equipment if required
| checkpoint | If a lift is required to operate during a fire, then isolate those lift lobbies from fire & smoke in accordance with the BCA part E2 & recommendations of EN811 appendix G & Fig 2
| checkpoint | Make good & clean up where lobby finishes meet architraves & lift call buttons etc
| checklist | Formwork & Reinforcing |  | Formwork & Reinforcing | ac3816f8-befd-43d2-b233-59ea73bf9649
| section | Formwork
| checkpoint | Confirm Class of formwork to all faces, as per the latest specifications
| checkpoint | Confirm RL's of soffit & beams
| checkpoint | Confirm any penetration sizing for any hoist/crane penetrations
| checkpoint | Ensure formwork frames installed to enable clear & labelled access under deck for other personnel & for inspections
| checkpoint | Ensure all formwork surfaces are cleaned & no rubbish remains on any soffits,sides,base of work
| checkpoint | Ensure bases of all columns/walls are cleaned out prior to pouring
| checkpoint | Check formwork is completed as per specified Class
| checkpoint | Ensure no rubbish or excess water is present prior to concrete pour
| section | Reinforcing
| checkpoint | Size and type correct to specification
| checkpoint | Reinforcing spacing and location correct
| checkpoint | Specified covers checked/correct
| checkpoint | Reinforcing installed correctly to specification and ready for concrete to be placed
| section | Post concrete pour
| checkpoint | Formwork stripped in a safe manner
| checkpoint | All timbers de - nailed
| checkpoint | Final sign off - All formwork & reinforcement completed as per the above ITP
b4241cb3-c017-599e-b902-40f90086942e | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Slab Edges Waterproofing |  | Slab Edge | b2f834c5-f4c9-47bc-95ea-39a45dac872f
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
4d51256e-1723-52f9-b0bf-cdbd78e02274 | note | Attach relevant photos
605fe18f-a06d-58c1-9069-180fc6bea2f0 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
2600a894-0251-5635-a790-8342723bb4a7 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
4b38f4c8-857f-5272-92d7-32fdf0f1d035 | tickbox | Ensure no high points or crevices are in the substrate
45d5f955-7ec1-52bf-96cc-cf323f9f622d | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Dampen the surface to ensure the highest level of adhesion as required
22bcc6a1-7427-5b67-8529-dc73454c4ac2 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydralastic Flex 2K - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines & ensure WPM to be extended and terminated inside the drip groove.
55fffd99-9f13-573b-9f85-3177cf1c4e68 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydralastic Flex 2K - Apply selected membrane at a rate of 1.6kg/m2 for 1.0-2.0mm thickness as per datasheet & application guidelines & ensure WPM to be extended and terminated inside the drip groove.
4c3f7e94-1122-56c7-a615-3784e3be6354 | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
5bfe02fb-3bc5-5e5a-9abd-9e8e11f9b09f | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
4fd26684-ca87-5fb4-8a3c-1059df84ce5a | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
9db0d4d3-407c-52f6-ad7f-888a94f71783 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Pad Footings |  | Pad Footings | b730866a-2929-4661-aef2-74595def3938
| checkpoint | Excavation depths and locations confirmed prior to detailed excavation commencing
484541b8-e204-5b08-b648-3307dc0dd44f | button | Footing RL Confirmed | Yes, No, N/A
4dc458bb-1fc6-5c2a-8669-951685ee0bcc | button | Any services (overhead / below ground) considered and isolated where required before excavation commences | Yes, No, N/A
0f3af2f0-f201-598c-8916-26459170a063 | button | Approval given to commence detailed excavation | Yes, No, N/A
c45d6c2e-e96a-5693-b384-b79a09cb19bf | button | Excavation checked, correct and approved | Yes, No, N/A
4f446aee-0895-537c-9b5a-fa9eb6bbdea6 | button | Depth correct (allow for site concrete if required) | Yes, No, N/A
74c5644c-f0f3-5dde-917e-10d4c6e700d0 | button | Width correct (allow for boxing if required) | Yes, No, N/A
| checkpoint | Pads/ footings battered/ edges left free of spoil
| checkpoint | Detailed excavation spoil removed and work area left clean and tidy
| checkpoint | Blinding installed and documented if required/ Dockets and photos scanned
| checkpoint | Formwork - location, height, falls and dimensions checked and accurate
82719b0b-2b90-5c94-9ca6-c932442d1f67 | button | Formwork sufficiently fixed and braced | Yes, No, N/A
f062700c-3469-5ae3-a515-40b786864b2e | button | Any rebates/ nibs / cast in items are correctly positioned, sized and appropriately fixed in place | Yes, No, N/A
62d327de-3488-5da8-a5f9-2602c5ea8b76 | button | Service penetrations formed correctly and locations checked/correct | Yes, No, N/A
5b7ae2ba-4f6f-583f-8008-6663a4dfe51f | button | Any control joints/ stop ends installed accurately and correctly braced | Yes, No, N/A
| checkpoint | Reinforcement installed as per plan including cover & chairs
799e19c2-7373-511b-b46d-97caedd7b1c1 | button | Reo spacing & grade as per specifications | Yes, No, N/A
| checkpoint | Starter bars, dowel bars, & mesh installed as per specifications
| checkpoint | Concrete strength/ Slump confirmed
| checkpoint | Any waterproofing elements have been correctly installed and checked
| checkpoint | Concrete Pour completed - All final checks and documentation completed and attached
| checkpoint | Final sign off - All pad footings completed as per the above ITP
a4daf18d-e191-5765-b52a-5bc23b256a52 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Carpark & Line Markings |  | Carpark & Line Markings | be9bd016-0d7f-4902-8d83-7c4aa4e0db17
| checkpoint | Ensure all emergency lighting in car park has been installed as per plan
| checkpoint | Check that all boom gates have been installed & tested
| checkpoint | Check that all security systems within car park have been installed & tested
| checkpoint | Check that all garage doors in car park have been installed & tested
| checkpoint | Ensure all safety bollards in car park has been installed as per plan
| checkpoint | Ensure all signage in car park has been installed as per plan
| checkpoint | All line markings are completed in correct colour/Area according to specifications
| checkpoint | All Numbering completed in correct colour/Area according to specifications
| checkpoint | Final sign off - All line markings completed as per the above ITP - Add general photos/comments below
b795a612-0cce-551f-84be-c8042de8a782 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Pre Wall Linings |  | Pre Wall Linings | c0193683-d66e-4919-8ecf-b667af5a4ae9
| checkpoint | Ensure FER, FEBQ & alternate solution reports have been read & requirements complied with
e68a5bf2-5902-5ee0-9f3c-936502f94c40 | button | Ensure all penetrations have been installed at a 90 degree | Yes, No
1a4f5f1c-5822-5f6f-927f-e7333cc93208 | button | Ensure all penetrating pipes fire collars are installed in accordance with C3.15 of the BCA | Yes, No
baa19b4a-4ef8-54d7-856e-37da0afd73bb | button | Ensure all penetrating floor waste pipes have floor waste fire collars installed in accordance with C3.15 of the BCA | Yes, No
8a89be50-5e62-55de-89d4-9ad1cae1315b | button | Ensure that penetrations around fire hydrant pipes have been filled | Yes, No
b8ef40b0-d53b-550e-aec6-d4e051958c20 | button | Remove redundant fire collars | Yes, No
edcf96f8-2864-5e3f-8f9d-3e0009ca6bd5 | button | Fill redundant Penetrations with concrete (min 200mm Thick) | Yes, No
| checkpoint | Ensure all copper pipes & hydrant pipes have been insulated when passing thru a fire collar in accordance with clause C3.15 of the BCA
| checkpoint | Ensure all fire collars have been installed in accordance with manufacturer's specifications & clause C3.15 of the BCA
| checkpoint | Ensure that mechanical ductwork is suitably sealed when passing through firewalls
| checkpoint | Ensure that suitable access is provided to mechanical fire dampers in accordance with clause C3.15 of the BCA
| checkpoint | Ensure that services within the fire stairs are boxed out with a two way fire rated system (where required)
| checkpoint | Ensure electrical cables have been suitably sealed when passing through a fire element in accordance with clause C3.15 of the BCA
| checkpoint | Ensure that NBN collars have been installed with grafitex on both sides of the hebel walls in accordance with clause C3.15 of the BCA
| checkpoint | Check that PEX pipes are adequately sealed in accordance with clause C3.15 of the BCA
| checkpoint | Check that fire doors have been filled
| checkpoint | Final sign off - All pre wall linings work completed as per the above ITP
f4e1d54d-3c77-5e4c-8e05-0962311dbd82 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Bathroom & Laundry Waterproofing |  | Bathroom & Laundry Waterproofing | c4cf7cef-ca5e-4006-af8e-8aff8332fbfe
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application "No access Waterproofing work in progress"
ab90e87c-7b91-5f54-be3f-29cb146d6b22 | note | Attach relevant photos below
1b2fa85c-40b8-59a4-a9f7-b3e430bfb544 | button | Membrane system & methodology checked off AGainst Aland standard details & MSDS & guidelines | Yes, No
204429cb-f20e-5d98-8d34-22f17b83fe4d | button | Surface preparation as per application guide | Yes, No
5139c964-85f0-5748-a966-6b25ee2bdc2e | button | Substrate clean, dry & free from dust. | Yes, No
9ff305b7-eef5-5d73-bd84-95673c0e9274 | button | Ensure no high points or crevices are in the substrate | Yes, No
8c01e01f-9821-5690-b7da-305edbb9f3f7 | button | Ensure substrate is structurally sound & ready to receive membrane | Yes, No
ddbbd4ef-f5f6-58ac-a953-da721ce46d80 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to primer | Yes, No
b6110024-e35e-5ce8-964a-ac595b6d5fda | button | Do not proceed if above has not been signed off | Yes, No
| checkpoint | Apply primer
772450b2-d24d-5d31-9c5a-70cc6c3706f1 | button | Ensure all floor wastes & pipes have been primed in accordance with manufacturer's recommendations | Yes, No
3f6e15f2-d36b-58d0-8412-713cfc3bc37c | button | Shower angle in correct position & level | Yes, No
b21b033d-9269-540b-814d-d356a19ecea8 | button | Door angle is in correct position & level | Yes, No
0b8928ed-1a5e-5209-9a6e-f8ecb8bd4a62 | button | Door & shower angle are 3 mm gauge aluminium | Yes, No
0c92b756-2648-5413-87fc-1d8e7039df17 | button | All corners have polyurethane bond breaker installed with min 15mm radios | Yes, No
d3ffdb2f-990c-5991-90f7-951a52bdbf42 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to first coat | Yes, No
| checkpoint | Apply first coat of membrane & turn membrane up the walls / pipes as required.
664a50c8-2ffe-5860-a641-0f3b8192c93e | note | All floor wastes membranes to be turned down into floor waste
| checkpoint | Waterproof walls of shower section up to ceiling. Seal taps & the like. 2x coats required
ef2848dd-3bca-5ca4-84aa-62b86b1ebe35 | button | Min 150mm kicker has been waterproofed (do width of roller 230mm) | Yes, No
0ad269c9-75f8-50d2-bee3-f26508e089cb | button | Min 1500mm past shower screen has been waterproofed | Yes, No
ac3c7107-e56a-51a5-905e-5568cb7956a0 | button | Waterproof all shower & adjacent walls | Yes, No
2655d542-bd0b-53c2-a0c0-0b5ca6d76450 | button | Ensure humidity, temperature & moisture are in accordance with manufacturer's recommendations prior to final coat | Yes, No
| checkpoint | Apply final coat of membrane
e7b10b99-3d73-518d-98c6-17c92579c31e | button | Allow curing in accordance with manufacturers specification 24‐48 hours min | Yes, No
| checkpoint | Carry out dry film thickness test using Positector coating thickness inspection instrument
2c15f407-b744-57f6-be8e-863bf3f0dbaa | note | Total dry film thickness of 1.2mm (1200 microns) in two finished coats. As such at min.
268d6f11-68c0-548d-b5e1-b5bf6eb209e9 | note | Wet film thickness of 0.75mm per coat is required ‐ Apply membrane at a coverage of 0.75 ‐ 1 Ltr / m2 per coat
| checkpoint | Rectification of defective works for failure of flood test & all works completed
| checkpoint | Final sign off - All bathroom & laundry waterproofing work completed as per the above ITP
20509fd1-1dab-54a8-a9cd-fa7482136bc8 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Toilet |  | Toilet | c6bf494e-0462-4b28-ba6e-638327c937b1
| checkpoint | Floor wastes checked - Any issues comment/photo below
| checkpoint | All rough-in pipework is colour coded to ensure no cross connections
| checkpoint | All Water & Gas risers are complete
| checkpoint | All stacks are level/plumb
| checkpoint | Ensure all services that go through fire rated walls to be treated with collars/fire rated sealant
| checkpoint | Ensure rough in has been done as per specs
| checkpoint | Final sign off - All plumbing work completed as per the above ITP - Add general photos/comments below
6de2d11a-ee94-5f81-a088-d0d7b5fb8775 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Mechanical Fan Room |  | Mechanical Fan Room | c817a8ef-1605-4753-b817-7e024cbf3eac
| checkpoint | Ensure all mechanical fans have been tested & commissioned
6fb48696-4f95-57a9-9700-4bd839227a16 | button | Switchboards in place using suitable fixings to match mounting service No damage to external board has occurred during installation | Yes, No
5abcd6d8-00b6-5938-8d34-769790618d7c | button | Ensure adequate pathways exist within board to accommodate all circuits and allow for future expansion | Yes, No
261e25b2-78fe-58ed-882b-6827886faa6e | button | Install and loom in all circuits into correct cabinets | Yes, No
0482ae87-e740-55c3-b5d8-b2dee450335d | button | Ensure cable labels match switchboard schedule and construction drawings | Yes, No
3aa27a68-be9a-500d-b19c-873ea456b0d4 | button | Cables are labelled as per specified requirements | Yes, No
bc34217a-fb95-5718-8872-e9c543feea24 | button | Check all tightness of all terminals on all breakers and bars | Yes, No
| checkpoint | Ensure safety signage is installed and visible as per plans
| checkpoint | Final sign off - All mechanical fans are installed as per the above ITP - Add general photos/comments below
5d3a3e28-1aaf-50cd-bdfe-ec62ca5ef1f4 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Precast |  | Precast | cb161b0c-e212-4458-868d-bfe19d432d9f
| section | Pre - Erection
| checkpoint | Latest drawings include bracing design
| checkpoint | Precast Panels certification obtained
| checkpoint | Set up of exclusion zone - Off-loading area
| checkpoint | Set up of exclusion zone - work area
| checkpoint | Crane slewing zone checked
| checkpoint | Survey datum and grids checked
| checkpoint | Support structure as per engineer design
| checkpoint | Precast element set-out complete
| section | Precast Element Erection
| checkpoint | Shims set to levels & within limits
| checkpoint | Dowel preparation complete as per drawings
| checkpoint | Crane positioned as per chart check
| checkpoint | Panel's lifted off truck as per SWMS
1f20b85a-0fd9-5162-822a-834f0fa14755 | button | Panels lowered into position | Yes, No
| checkpoint | Dowel alignment checked
617268f6-912c-5d1f-9eb8-218bd6b85ba3 | button | Horizontal alignment checked | Yes, No
420e23d0-bbf4-5d5c-8728-23f7013dbe79 | button | Vertical alignment checked | Yes, No
| checkpoint | Bracing installed, pins, locks & bolts in place
| checkpoint | Panels dowels grouted
| checkpoint | Dry pack grout to panels underside
| checkpoint | Brackets installed and grouted
| checkpoint | Braces removed
| checkpoint | Caulking internally as per approved spec
| checkpoint | Caulking externally as per approved spec
3abc1f78-9a73-563f-8492-1e0de5c66778 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| signoff | All work completed as per ITP
| checklist | Basement Fire System |  | Basement Fire System | cf7c4371-7d0e-4ca4-bc01-374cd0c8cbef
| checkpoint | Confirm any pipework and cabling penetrating partition walls are sealed through penetration with Intumescent fire mastic
| checkpoint | Sprinkler rough in complete
| checkpoint | Sprinkler droppers / heads installed
| checkpoint | Sprinkler floor isolation valve assembly installed
| checkpoint | Sprinkler valves installed
| checkpoint | Sprinkler tested to min 1200 kpa
| checkpoint | Feed hydrant installed
| checkpoint | Feed hydrant commissioned
| checkpoint | All hoses installed as per plan
| checkpoint | All hoses installed as per manufacturer's instructions
| checkpoint | Pipework tested - Test results attached below
| checkpoint | EWIS speakers installed as per manufacturers instructions
| checkpoint | Magnetic door holder fitted and functioning correctly on all fire exits
| checkpoint | Final sign off - Fire system installed as per the above ITP - Add general photos/comments below
3b9056e8-3216-5ead-8dba-8184a4538373 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Hobs |  | Hobs | d15c189c-2458-47ea-a186-3d1b7211b8aa
| checkpoint | Area barricaded off to allow no access to balconies with signs posted/ visible to include date of application, "No access waterproofing work in progress"
3747e8d8-0fa7-54b9-b9f7-1265ad85d078 | note | Attach relevant photos
22d4f1ce-4904-5ffe-8130-a52cd21cfaee | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
132eba57-d32f-57b3-9f44-7cb5633da6b5 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
5c216376-44d7-5a5d-a033-9f98c77f21cc | note | Attach relevant photos
| checkpoint | Primer substrate with Polybit Hydrapoxy/polyprime - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
b252086a-e5c4-5c9a-ab73-189222543e1e | note | Attach relevant photos
| checkpoint | Seal all joints, gaps, cracks and penetrations with Polybit HydraFlex polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
12948a13-083b-5b67-9fa8-2ec0a504356f | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydraguard - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
6035fa01-3b66-524f-b0f0-6a51d81551f3 | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
7b2aa2b4-cec9-5600-b93f-f7e34e62fbac | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
a58e44b4-ee88-54a9-b0e7-9e1cea5e3d1a | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
62338ade-6db8-567e-bdda-c9bb8b97f070 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Columns |  | Columns | d52f7dd5-5f83-45d9-a51f-e9eb730e96e2
| section | Pre-Column Pour
| checkpoint | Survey points given for 2 points
| checkpoint | Datum RL supplied by surveyor, pour height marked
| checkpoint | Blockouts, couplers, cast-in elements installed
| signoff | Request Sign Off from Site Engineer
| checkpoint | Column box cleaned & oiled
| checkpoint | Placement of column box over cage
| checkpoint | Bracing props secured
| checkpoint | Column plumbed
| checkpoint | Correct class of finish
| checkpoint | Final sign off - Columns completed as per the above ITP - Add general photos/comments below
98819f33-3777-5676-8760-79d1548c8ef4 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| section | After Column Pour
| checkpoint | Confirm Surveyor is out next day to carry out survey of finished concrete Attach As built Survey Plan
6f96d071-1fd3-5506-99cc-2ac25270bb45 | note | Attached below as applicable
| checkpoint | Confirm tolerance of finished concrete surfaces are in accordance with the specifications
| checkpoint | Confirm saw joints are installed to engineers requirements
| checkpoint | Confirm finish of concrete is adequate for application (broom/trowel/helicopter finish), refer to AS3610
| checkpoint | Obtain all concrete tests at 1 day, and attach test results
78fcf0a7-4c34-54f8-ae26-550b5bf0aec4 | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 4 day, and attach test results
c9c29beb-13d2-597d-aeb0-0e446bd96e01 | textbox | Test Strength Mpa
b66bb6d9-d41b-50e8-aa26-ad5ce916c808 | note | Attached below as applicable
| checkpoint | Obtain all concrete tests at 7 day, and attach test results
60d14f7c-09f8-5628-aa94-ed5616e21264 | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 28 day, and attach test results
a6d4fc3e-47e2-5749-9f05-e54620f8b9eb | textbox | Test Strength Mpa
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
bab2f29c-7286-5a0b-93b0-636625c85d70 | button | Subcontractor Sign Off | Yes, No, N/A
fe9e5288-df17-5c0f-9d31-6adf62a89c8e | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Bike Rack |  | Bike Rack | dac9afe0-d3f9-4865-80dc-9899c6b7f2aa
| checkpoint | Bike rack installed to manufacturers instructions & standards - Attach photos below
ca3ebe32-6fab-5c95-96b4-b4d76242cb82 | note | Ensure adequate fixings have been used & are tight
| checklist | Storage Room |  | Storage Room | dc275439-ca48-4068-9873-61175b4ebbd3
| checkpoint | Storage lockers installed to manufacturers instructions & standards
| checkpoint | Final sign off - All storage rooms installed as per the above ITP - Add general photos/comments below
6e1801b0-50e4-5b7a-988c-a43f727704e5 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Apartment Fire System |  | Apartment Fire System | dc8a48db-4d8e-4ab9-9541-61b1224e6e4e
| checkpoint | Smoke detectors & Sensors rough in completed
| checkpoint | Smoke detectors & Sensors fit off completed
| checkpoint | Smoke detectors & Sensors tested as per manufacturer's instructions
| checkpoint | Sprinklers rough in completed
| checkpoint | Sprinklers fit off completed
| checkpoint | EWIS speakers installed as per manufacturers instructions
| checkpoint | All fire signage installed correctly and visible - If applicable
| checkpoint | Final sign off - Fire system installed as per the above ITP - Add general photos/comments below
64d4d66d-7c8a-5223-8522-36bcbe5ba367 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Roof, Terraces & Walkways Waterproofing |  | Roof, Terraces & Walkways Waterproofing | dd4ba79d-9aa6-4687-bc48-acdfec010b60
| checkpoint | Area barricaded off to allow no access with signs posted/ visible to include date of application, "No access waterproofing work in progress"
5fbfaaf3-1fa3-5b06-8ccf-f545144da304 | note | Attach relevant photos
| checkpoint | WP details listed at architectural drawings for clarifications are followed.
| checkpoint | All floor should be with proper falls towards the floor waste with a min. 1:100 slope.
484b7282-4298-5b10-9aaf-fd8ac44465a0 | note | Attach relevant photos
| checkpoint | WPM must be applied around the linear drains (grated drains) before adding the leveling screed.
4e1018c3-f56e-5ef8-83c2-ca3fcc0587dd | note | Attach relevant photos
a37c35bb-32b1-50ff-ae7f-034485466ee3 | tickbox | Membrane system & methodology checked off against Aland standard waterproofing details & MSDS
8d14dca4-b52b-5345-8a0d-1e3fc74ee404 | tickbox | Substrate clean, structurally sound & ready to receive membrane as per application guidelines of specified waterproofing system.
5408ff34-e7b8-5a26-babe-4845b1eff49e | tickbox | Ensure no high points or crevices are in the substrate
e33bf9e9-65f5-5cfe-b949-9cc55a22b502 | tickbox | HOLDPOINT - Do not proceed if above has not been signed off
| checkpoint | Apply Polybit PVC primer to all PVC drains and pipes - Apply selected primer at a rate of 100ml/m2 as per datasheet & application guidelines
bb605e28-0233-571e-aeb2-397990c208d9 | note | Attach relevant photos
| checkpoint | Primer substrate with Polybit Hydrapoxy or PU primer - Apply selected primer at a rate of 150-200 gr/m2 as per datasheet & application guidelines
6066dcee-8431-50b9-a598-ea08b9f8f1fe | note | Attach relevant photos
| checkpoint | Seal all joints, gaps, cracks and penetrations with Polybit HydraFlex polurethane sealant. - Apply selected sealant as per datasheet & application guidelines
6dae6f89-3da0-5e95-a74d-f641255672e9 | note | Attach relevant photos
| checkpoint | Apply 1st coat of Polybit Hydraguard PU on floors with a turnup up and over external hobs. - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
d2076dd4-f089-5ec1-9320-7f6ce82adc9a | note | Attach relevant photos
| checkpoint | Apply 2nd coat of Polybit Hydraguard PU on floors with a turnup up and over external hobs - Apply selected membrane at a rate of 1.5kg/m2 as per datasheet & application guidelines
3f309ace-f19a-5ff2-8a6b-a2ce1f4760d2 | note | Attach relevant photos
| checkpoint | Dry day for second coat (if required).
b3c7c0cb-fcdf-5f31-bec5-677589b56924 | note | Attach relevant photos
| checkpoint | Apply PolyGuard protective UV top coat. - Apply selected top coat at a rate of 0.2-0.6 kg/m2 in one or two coats, depending on traffic conditions as per datasheet & application guidelines
| checkpoint | the WPM must be terminated at the specified height outlined in the wind classification report Via saw cut reglet or other WPM termination method specified at AS 4654.2, or can be overlap by approved elastomeric weather-resist coating by min. 150mm.
f277cd9d-5fe9-53ac-8118-6f514ece6fca | note | Attach relevant photos
| checkpoint | Carry out dry film thickness test using positector coating thickness inspection instruction. - Review result against datasheet & application guidelines
38521c18-89ed-5779-919b-7f7d2696dcc0 | note | Attach relevant photos
| checkpoint | Attach photos for the drainage conduit.
82c6d44c-297b-5e70-bc9f-591651a8537e | note | Attach relevant photos
| checkpoint | If required - Rectification of defective works for failure of flood test/thickness test & all works completed.
a86596a0-ff1a-5c44-8a43-5eb034c1fa9a | note | Attach relevant photos
| checkpoint | Final sign off - All general waterproofing work completed as per the above ITP
36760ae3-3b6b-5ae9-8af6-41615ce7caa1 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Inspection Checklist |  | Inspection Checklist | e28b816d-8218-4ff5-8150-b9ca7e5724fc
| checkpoint | Inspection Details
3279ea90-8ed6-54fa-a633-cdbcab73f20e | textbox | Date of Inspection
7e3798e3-5701-53b7-8971-07b2099171d5 | textbox | Inspection Type (Code)
ceb956c3-787d-5906-a86b-d42a3da1792e | textbox | Person/Company Inspecting
0c250f07-0736-500a-b62e-a32e7b89ca81 | textbox | Area inspection relates to
| checkpoint | Inspection outcome
3c3ebc6a-95f1-5ca1-8677-79749addffed | dropdown | Inspection Result | Pass, Partial Pass, Fail, N/A
ed73bda7-d014-59a9-b7fc-bb6bdc4522a7 | textbox | Reason if Partial Pass or Failed
625b5519-7eaa-5640-9bdc-add5dd0bf23a | tickbox | Inspection report attached below
4911a68d-be8e-552b-9613-66134fccd7d3 | note | Remedial items to be photographed & Commented below
| signoff | Request Sign-Off (3rd Party)
| checkpoint | All Relevant Observation(s) Closed-Out & evidence attached - if applicable (Pass once completed)
| signoff | Request Sign-Off (3rd Party)
| checklist | Suspended Slab |  | Suspended Slab | e2f73502-7c15-4082-8e4e-033ca79a782b
| checkpoint | Materials used complies with design documentation
| checkpoint | Datum point used & soffit RLs checked
| checkpoint | Grids marked by builder
| checkpoint | Surveyor points given for outside of building
| checkpoint | Fillet & drip mould installed
| checkpoint | Check set down position & RL
| checkpoint | Check penetrations installed
| checkpoint | Column blockouts installed
| signoff | Request Sign Off from Site Engineer
| checkpoint | Check back propping as per design
| checkpoint | Blow off deck
| checkpoint | Engage external consultant (engineer inspection)
| checkpoint | Correct Class of Finish
| checkpoint | Stripping, cleaning & materials removed
| checkpoint | Final sign off - Suspended slab completed as per the above ITP - Add general photos/comments below
| checkpoint | Obtain all concrete tests at 1 day, and attach test results
ac0bc984-6d8a-5e99-bafb-d9fe615d7afb | textbox | Test Strength Mpa
| checkpoint | Confirm initial stress is conducted day after the pour, after concrete has reached 7MPa on 1 Day results
| checkpoint | Obtain all concrete tests at 4 day, and attach test results
731ca016-5873-530d-87aa-ec6b5798c9c7 | textbox | Test Strength Mpa
| checkpoint | Confirm final stress has occurred after concrete has reached 22MPa, and attach Stressing Records
450eaa21-0cb0-5832-8600-0e9d49f20e47 | note | Attached below as applicable
| checkpoint | Obtain all concrete tests at 7 day, and attach test results
0721004e-7038-53e6-894b-dbc91bc36779 | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 28 day, and attach test results
ecd1edba-d304-5d73-91e9-bd3a73c67cd9 | textbox | Test Strength Mpa
61f3243b-8842-5cb2-b247-0214aceae912 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Underground Gas Checklist (V140421) |  | Underground Gas Checklist (V140421) | e50ce4aa-c85c-4f2d-9a5e-30edc4092f89
| checkpoint | WorkSafe notification prior to trenching operations @ 15M deep or greater
| checkpoint | Existing in-ground services located and verified before excavation
| checkpoint | Site survey and confirm extent of works
| checkpoint | Confirm area of work is accessable and acceptable to commence
| checkpoint | Exclusion zone erected
| checkpoint | Trench shoring/shield is on site
| checkpoint | Excavation depths and locations confirmed prior to detailed excavation commencing
| checkpoint | Bedding material is correct type, grade and depth
| checkpoint | Gas service installed to correct depth of cover
| checkpoint | Service indicator tape installed
| checkpoint | joints are correct
| checkpoint | Risers are in correct location - provide photos
| checkpoint | Gas service tested to AS/NZS 56012013 Provide Photos
| checkpoint | Trench suitably backfilled and compacted
| checkpoint | Expansion lagging installed around pipes prior to concrete
| checkpoint | clean up of work area
| checkpoint | General photos, comments & observations during Cold Water Rough-In (Add below)
| checkpoint | Underground Gas completed to specification/drawings & Area left clean/tidy
5d72bec2-2810-50fb-8fc2-94aeb9aed24a | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checklist | Jump Form |  | Jump Form | e6367cff-014b-4841-a3c0-5acb1dfc73a8
| checkpoint | Confirm Class of formwork to all faces, as per the latest specifications
| checkpoint | Confirm RL's of soffit & beams
| checkpoint | Confirm any penetration sizing for any hoist/crane penetrations
| checkpoint | Ensure formwork frames installed to enable clear & labelled access under deck for other personnel & for inspections
| checkpoint | Ensure all formwork surfaces are cleaned & no rubbish remains on any soffits,sides,base of work
| checkpoint | Ensure bases of all columns/walls are cleaned out prior to pouring
| checkpoint | Check formwork is completed as per specified Class
| checkpoint | Ensure no rubbish or excess water is present prior to concrete pour
| checkpoint | Size and type correct to specification
| checkpoint | Reinforcing spacing and location correct
| checkpoint | Specified covers checked/correct
| checkpoint | Reinforcing installed correctly to specification and ready for concrete to be placed
| checkpoint | Formwork stripped in a safe manner
| checkpoint | All timbers de - nailed
| checkpoint | Obtain all concrete tests at 1 day, and attach test results
1a6e363e-1187-54ac-940f-877a607bdc59 | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 4 day, and attach test results
20370f6b-0edc-5079-88dc-d5b3353aa343 | textbox | Test Strength Mpa
5152d4ad-2afc-5b77-af8a-1feef3f6157f | note | Attached below as applicable
| checkpoint | Obtain all concrete tests at 7 day, and attach test results
bfebb350-02e1-53ca-a1f5-43a0264c32f0 | textbox | Test Strength Mpa
| checkpoint | Obtain all concrete tests at 28 day, and attach test results
3287da17-e572-5b31-a63a-79e816053701 | textbox | Test Strength Mpa
| checklist | In-Ground Stormwater ITP (V140421) |  | In-Ground Stormwater ITP (V140421) | e8f96f10-c136-4c58-9da7-ba2d47f65b01
| section | Pit and Pipes
| checkpoint | Is Approval from Local Water Authority Required If so please provide permit
| signoff | Sign Off Required
| checkpoint | Details
48127aa5-43c4-5726-aafa-44ea964fdf14 | textbox | Engineering Plan Number(s)
b3209950-c9d3-5ff6-9580-a928b74a2581 | textbox | Name of certified drainlayer and registration number
e4b9040a-56c4-52e7-9e53-fb3f532a72ba | textbox | Location (Pit to Pit)
99a05c09-bbca-5353-bbad-d3d5d4fc9fa7 | textbox | Delivery Date (Pits and Pipes)
d74484fe-44fc-57a8-b4b0-31fc98e57c88 | textbox | Is work area clear and available for construction
242b2042-a8a8-5003-a8f4-3bee8c1839a9 | textbox | Do you have the appropriate plant to perform scope of works Provide plant details
| section | Trench/Excavation Methodology
| checkpoint | Method
c7f06da1-d4f7-5bf7-8c53-aa138daeb9ae | tickbox | Sheild
67055d81-1d55-55eb-91b0-9b7534afc8c5 | tickbox | Bench
8b431399-17f4-59a1-b854-a89afb1146dc | tickbox | Batter
603f5464-153b-5c77-869f-4fa9cc5b5849 | tickbox | Other
87bb5d09-c23f-5fc5-94cf-f11b1bf0c595 | textbox | If other please specify
ff1fee5c-eff3-5a39-83dc-ace408448655 | tickbox | Certified / Tagged lifting Equipment
| section | Product / Material check
| checkpoint | Pits
f0e05536-21a4-5661-9acf-532a564862d3 | textbox | Type
fd6a4562-fb0e-5cb1-8199-34f03ceee6d5 | textbox | Size
| checkpoint | Pipes
d3180144-51c0-57c2-8ee1-3db30f79cccf | textbox | Type
b2ac6d54-c741-5e06-b6cc-dc4e4be7ea72 | textbox | Size
| checkpoint | Lot Connections
ee6bd475-8c50-56b8-aa98-7c4126a95f8f | textbox | Type
e7f0f7f3-f2c9-598a-9255-ce92bf015340 | textbox | Lot number Location
| checkpoint | Bends
c9037a09-fa6f-5e18-b900-b00f76e78e22 | textbox | Location
08c7ff02-63a2-56e7-a815-4cfb805dc8f4 | textbox | Type
c7fae1d4-004a-5a01-8445-a0d660f809f9 | textbox | Size
| checkpoint | Quality Onsite Visual Inpection of Products / Materials - Defects to be Notified
cae2636d-4db2-5fb8-b296-9e1aa522681a | textbox | Surveyors name
| checkpoint | Set out / Off Set Check
| signoff | Sign Off Required
| section | Pit Installation
| checkpoint | Pits
6a820800-b875-53b7-8da6-38742144091a | textbox | Bedding and backfill type as per detail
5ace1d0c-54cb-5d5a-b1e8-d0204211a29d | textbox | Undercut weak unsuitable subgrade note chainage and depth ( Approval Required)
f3572820-65e1-5736-9e58-27c26ee703db | tickbox | Backfill to be compacted in 150mm Layers as per detail
b92566fe-2d3c-5025-9d5b-3a792c280cba | tickbox | External Concrete Bandage
485534f8-150b-561d-ab16-7e3831190c18 | tickbox | Internal Benching
1dde161c-2111-5952-8bbe-ee1df76b759f | tickbox | Internal Plastering / Render / Sealant
3fea5960-87e5-5a23-976d-8cde7cf4bad7 | tickbox | Sealant Between Riser
52817937-1d01-563d-869b-91359440caa5 | tickbox | Steps Required
a7b28fd1-8c0d-5b39-99a6-ecfae5005ec1 | textbox | Have pits been secure and covered during installation to reduce debris/silt
| checkpoint | Pipe invert levels through pit as per design
| signoff | Sign Off Required
| section | Pipe installation
| checkpoint | Pipes
90aecfb4-7f4e-5feb-8700-ce9fe20cec30 | tickbox | Are pipes free and clean of debris before installation
6402c56f-bddf-5cc0-86fd-946bca1cd994 | textbox | Bedding and backfill type as per detail
0f08c38f-def1-530a-aeda-0b0d6dce6e61 | textbox | Undercut weak unsuitable subgrade note chainage and depth (Approval Required)
0faec27b-373c-55f2-89c9-d93d13758156 | tickbox | Backfill to be compacted in 150mm Layers as per detail
| section | Drainage Data
| checkpoint | Backfill to be compacted in 150mm Layers as per detail
cb9564c6-4065-50ca-9d06-14a62eb328f9 | textbox | Grade and Alignment Check
a823603f-2668-55c9-9ca8-a48562ef47ce | textbox | Invert / RL Check
3b92eb6c-4d23-5c24-853e-ab1f663cb17d | textbox | CCTV pipe inspection data and comments supplied
| signoff | Sign Off Required
| checkpoint | Progress Photos
| section | Service Connections
| checkpoint | All Connections, Bends, Junctions installed
f95dd6e9-63d0-5931-ac62-0c575f410913 | textbox | As-built measurements / Pick up Recorded Before Backfilling
| signoff | Sign Off Required
| checklist | Detailed Excavation (V140421) |  | Detailed Excavation (V140421) | ec3598a8-8a6a-4be0-acf2-d8af27c9a4ff
| section | Excavation - Pre-Commencement
| checkpoint | Confirm dial before you dig documents are onsite - If applicable and attached below
| checkpoint | Confirm correct disposal of classified material
| checkpoint | Obtain geotech report, including load bearing capacity
6ea0966d-674a-565d-ac26-ca17ef6eeb87 | note | Geotech report referenced or attached below
| section | Excavation Works
| checkpoint | Collection of tip dockets - If applicable and attached below
| checkpoint | Confirm set out of boundaries & marked out
| checkpoint | Confirm actual RL is within design tolerance
2f8b1b6d-6198-5793-972d-789c0d988a62 | button | Confirm set out of footings and pads | Yes, No, N/A
cb6e5829-75a6-58c7-9bbe-6279dfa8306e | button | Confirm set out of in ground drainage | Yes, No, N/A
02497b06-d821-59fa-a986-acf4d5227aae | note | Excavation of footings not to exceed size as detailed on structural drawings
| checkpoint | Certifier to inspect foundation in accordance with specifications
| checkpoint | Geotech inspection of footings etc
779b6f3d-600f-558b-bc4f-d30685b1da8b | note | Geotech report referenced or attached below
| checkpoint | Confirm top of concrete footings is below surrounding finishes
| checkpoint | Confirm sub-base is in line with engineers specifications/requirments
cfdf2094-7355-566b-9621-5aca486406b6 | textbox | Minimum thickening (MM)
| checkpoint | Civil engineer inspection carried out - Attached below as applicable
| section | Sign-Off
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
1d7c33a6-91d0-58f0-ad91-a1d5d0a6de35 | button | Subcontractor Sign Off | Yes, No, N/A
adffe30a-8d39-5ae5-a238-9514fb328ddf | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Carpet |  | Carpet | ed71bb96-afd3-4a69-86ca-27699f17b3bb
| checkpoint | Correct underlay installed to specification(s)
| checkpoint | Correct carpet (Colour & Type) installed to Specification(s)
| checkpoint | Carpet installed as per manufacturer's instructions
dca1cfd9-b214-502c-b35d-8550a4f76494 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Rock Anchoring |  | Rock Anchoring | ee05135b-25f0-41dc-a0bf-c8562e1f2fe4
| section | Prior to Works Commencing
| checkpoint | Locate all existing services
| checkpoint | Confirm set out and RL
| checkpoint | Confirm type of anchor to be used
| checkpoint | Confirm the working load of the anchor/ tendon
| checkpoint | Confirm minimum depth for anchors
| checkpoint | Confirm angle of anchors
| checkpoint | Confirm strength of grout required
| checkpoint | Confirm de-stressing procedure for anchors with engineer
e1af3978-8920-51bd-a977-21a540b72de4 | note | Engineer procedure notes added below
| section | During Works
| checkpoint | Confirm anchors are not damaged during insertion into bore hole
| checkpoint | Confirm number of strands is in accordance with engineer drawings
| checkpoint | Confirm bore hole is being flushed clean – water/ air
| checkpoint | Confirm grouting is taking place same day
| checkpoint | Confirm bond and free lengths have been met in accordance with engineer drawings
| checkpoint | Confirm grout testing is taking place (results to be returned 28 days later)
| checkpoint | Confirm design boreholes design depth has been reached and do not require re-drilling
| section | After Works
| checkpoint | Confirm grouting is reaching required strength after 7 days
| checkpoint | Confirm stressing works have been completed
| checkpoint | Confirm testing has been completed and passed loading test
| checkpoint | Confirm anchors have not moved during testing
| checkpoint | Confirm if additional anchors are required
| section | Sign-Off
| checkpoint | Attach Subcontractor ITP - Attached below as applicable
c22ba754-09fe-513e-9d34-08e94a7f3c85 | button | Subcontractor Sign Off | Yes, No, N/A
a2be0f77-1685-5fda-873a-80efefcd79f6 | button | Aland Sign Off | Yes, No, N/A
| signoff | Click to add Sign-Off Signatures
| checklist | Underground Fire Service Checklist (V140421) |  | Underground Fire Service Checklist (V140421) | eef1fa01-b16d-42fc-8008-3d27f1a735bc
| checkpoint | WorkSafe notification prior to trenching operations @ 15M deep or greater
| checkpoint | Existing in-ground services located and verified before excavation
| checkpoint | Site survey and confirm extent of works
| checkpoint | Confirm area of work is accessable and acceptable to commence
| checkpoint | Exclusion zone erected
| checkpoint | Trench shoring/shield is on site
| checkpoint | Excavation depths and locations confirmed prior to detailed excavation commencing
| checkpoint | Bedding material is correct type, grade and depth
| checkpoint | Fire service installed to correct depth of cover
| checkpoint | Service indicator tape installed
| checkpoint | joints are correct
| checkpoint | Risers are in correct location - provide photos
| checkpoint | Fire service tested to AS/NZS35002018, AS24192017 Provide Photos
| checkpoint | Trench suitably backfilled and compacted
| checkpoint | Expansion lagging installed around pipes prior to concrete
| checkpoint | clean up of work area
| signoff | Completion sign off
| checkpoint | Independent inspection and testing complete
| checkpoint | General photos, comments & observations during Cold Water Rough-In (Add below)
| checkpoint | Underground Fire Service completed to specification/drawings & Area left clean/tidy
ee435b22-32f1-5d6e-b59a-555d347c34dc | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checklist | Joinery Fit Out |  | Joinery Fit Out | f009b5ef-4ded-4f18-89d4-c946ce462165
| checkpoint | Shower screen has been installed level & tested
| checkpoint | Door hardware has been installed & tested
| checkpoint | Window & slider frames have been installed & fixed correctly
| checkpoint | Sliders have visibility decals installed
| checkpoint | All kitchen joinery & installed
| checkpoint | Final sign off - All joinery fit out work completed as per the above ITP
6d5cda96-c507-5b2c-a794-803775d42e5d | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Corridor/Common Area Fire System |  | Corridor/Common Area Fire System | f04f362a-685d-46f3-b3d8-f53918f7b6af
| checkpoint | FIP installed as per manufacturer's instructions
| checkpoint | FIP tested & commissioned
| checkpoint | Smoke detectors & Sensors rough in completed
| checkpoint | Smoke detectors & Sensors fit off completed
| checkpoint | Smoke detectors & Sensors tested as per manufacturer's instructions
| checkpoint | EWIS speakers installed as per manufacturers instructions
| checkpoint | All fire signage installed correctly and visible
| checkpoint | Magnetic door holder fitted and functioning correctly on all fire exits
| checkpoint | Final sign off - Fire system installed as per the above ITP - Add general photos/comments below
| checklist | Add Blade Walls |  | Blade Walls | f4c2d55c-ef7c-42bb-9cba-7f7ab8f9f53c
| checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
| checkpoint | Setout & alignment as per drawing (include revision below)
8a49a7e8-677b-55fb-b240-501dca912245 | textbox | Drawing & revision number(s)
| checkpoint | Survey points given for 2 points
| checkpoint | Land shutter bracing props secured plumb shutter
| checkpoint | Datum RL supplied by surveyor pour height marked
| checkpoint | Blockouts steps penetrations marked & installed
| checkpoint | Steel tied & clear from Z bar holes
| checkpoint | Couplers & rebate boards installed
| checkpoint | Base of walls cleaned
| checkpoint | Leave a piece of AFS out every 6 m where a stock length of reo will lap in order to ensure horiztontal bars are tied, lap is maintained & compaction can be physically viewed at this point
| checkpoint | Closing shutter installed
| checkpoint | Z bars secured wall straight & plumbed
| checkpoint | Correct Class of Finish
| checkpoint | Final sign off - Walls completed as per the above ITP - Add general photos/comments below
f37788d5-b88e-532e-a30f-66e378995315 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Internal Painting |  | Internal Painting | f4ef3b92-2386-4b73-8bd8-d96819bcd262
| checkpoint | Ensure to use right product & system as per specification & scope of works
| checkpoint | Provide adequate ventilation & removal of waste disposed correctly
| checkpoint | Final sign off - All internal painting work completed as per the above ITP
e2091e72-dec6-5f4e-86a2-e775ff01e565 | note | HOLDPOINT - Once all above items have been signed off work may proceed
| checklist | Underground Water Checklist (V140421) |  | Underground Water Checklist (V140421) | f910b911-772c-42f6-8cae-bca48c6c2347
| checkpoint | WorkSafe notification prior to trenching operations @ 15M deep or greater
| checkpoint | Existing in-ground services located and verified before excavation
| checkpoint | Site survey and confirm extent of works
| checkpoint | Confirm area of work is accessable and acceptable to commence
| checkpoint | Exclusion zone erected
| checkpoint | Trench shoring/shield is on site
| checkpoint | Excavation depths and locations confirmed prior to detailed excavation commencing
| checkpoint | Bedding material is correct type, grade and depth
| checkpoint | Water service installed to correct depth of cover - Provide photos
| checkpoint | Service indicator tape installed
| checkpoint | joints are correct - Provide photos
| checkpoint | Risers are in correct location - provide photos
| checkpoint | Water service tested to AS/NZS 35002018 Provide Photos
| checkpoint | Trench suitably backfilled and compacted
| checkpoint | Expansion lagging installed around pipes prior to concrete
| checkpoint | clean up of work area
| checkpoint | General photos, comments & observations during Cold Water Rough-In (Add below)
| checkpoint | Underground Water completed to specification/drawings & Area left clean/tidy
e879f806-9b0e-5f4d-a790-ae54eb9dd4eb | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
| checklist | Mandatory Inspections |  | Mandatory Inspections | ff0e9c04-d305-4267-92fd-4563e84e1cdd
| checkpoint | Consent
f194aa92-76de-50b9-a7b1-a7da7a1d9dbe | textbox | DA/CDC No
0c6a678e-5ba3-5a5e-81f2-3f1a7d7ce4f5 | textbox | CC No
92149130-b2f9-5592-941d-e642e3badb37 | note | The Following are Critical Stage Mandatory Inspections - They are required pursuant to Section 65 (b) of the Act & Clause 162A of the Regs
bfc15b02-a031-5c3e-82be-5b50e8a4246c | note | In the case of a class 2, 3 or 4 building
| checkpoint | (a) after the excavation for, and prior to the placement of, any footing, and
| checkpoint | (b) prior to covering of fire protection at service penetrations to building elements that are required to resist internal fire or smoke spread, inspection of a minimum of one of each type of protection method for each type of service, on each storey of the building comprising the building work, and prior to covering the junction of any internal fire-resisting constructions bounding a sole-occupancy unit, and any other building element required to resist internal fire spread, inspection of a minimum of 30% of sole-occupancy units on each storey of the building containing sole-occupancy units, and
| checkpoint | (c) prior to the covering of waterproofing in any wet areas, for a minimum of 10% of rooms with wet areas, and
| checkpoint | (d) prior to covering any stormwater drainage connections, and
| checkpoint | (e) after the building work has been completed and prior to any occupation certificate