## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0375-ITP-026 Sewerage System - Rev.2 | itp |  |  |  |  | INF-HSEQ CC0375-ITP-026 Sewerage System - Rev.2 | c91096fc-3d3f-4a60-9f47-6e6b4bf49f6e
section | 1.0 Preliminaries
checkpoint | 1.1 - Documentation
label | Ref docs - Issued drawings / Site copy drawings
label | Acceptance criteria - Check that you have the latest site and engineering drawings BEFORE starting each task/set of tasks.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.2 - Lot Traceability
label | Ref docs - Spec. 0161 Quality [Cl 7.3]
label | Acceptance criteria - Prepare a lot map for traceability of the work area
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Lot map
checkpoint | 1.3 - Pipe Material
label | Ref docs - Drawings
label | Acceptance criteria - Has the correct class & type of drainage pipe been supplied and free of defects?
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material conformance certificate
checkpoint | 1.4 - Underlying Lot Conformance
label | Ref docs - Underlying Lot ITP
label | Acceptance criteria - Underlying services and/or assets have been installed prior to commencing works over and/or above.
label | ○ Refer underlying lot ITP(s)
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.5 - Embedment Material
label | Ref docs - ASNZS_3500.2-2021 Plumbing and drainage Part 2: [cl drainage 5.4.2]
label | Acceptance criteria - Filling materials used for bedding of drains shall be one of the following:
label | (a) Gravel screenings or similar recycled materials of nominal size between 7mm and 10 mm.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 1.6 - Set out
label | Ref docs - Drawings
label | Acceptance criteria - Setout Culvert inlet/outlet and drainage structure positions to the location and levels on the drawings. This shall be presented for inspection by the superintendent.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
section | 2.0 Excavation and Pipe Laying
checkpoint | 2.1 - Excavation
label | Ref docs - Hydraulic Specification HPP-AEC-CIV-BL-GEN-SPT-8001 6.21 -GRADES 6.7 -Trenches.
label | ○ In Accordance with IFC Drawings
label | Acceptance criteria - All trenches shall be excavated as per Drawings otherwise directed by HPP.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 2.2 - Pipe Laying and Joint Fitting
label | Ref docs - Drawings Manufacturer Specifications
label | Acceptance criteria - Have correct pipes (size and type) been laid and jointing installed as per manufacturer specifications
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.3 - Encasement Backfill
label | Ref docs - Spec. 1352 Pipe Drainage [Cl 5.1, 5.2]
label | Acceptance criteria - DICL & Flexible Pipes:
label | – – – – – – – – – – – – – – – –
label | Table 5.2 Trench and embedment dimensions
label | Dia (De)mm ¦¦ Min. dimensions (mm): x ¦¦ Min. dimensions (mm): s ¦¦ Min. dimensions (mm): o ¦¦ Min. dimensions (mm): y
label | – – – – – – – – – – – – – – – –
label | ≥ 75 ≤ 150 ¦¦ 75 ¦¦ 100 ¦¦ 100 ¦¦ Pipe dia.
label | > 150 ≤ 300 ¦¦ 100 ¦¦ 150 ¦¦ 150 ¦¦ Pipe dia.
label | > 300 ≤ 450 ¦¦ 100 ¦¦ 200 ¦¦ 150 ¦¦ Pipe dia.
label | > 450 ≤ 900 ¦¦ 150 ¦¦ 300 ¦¦ 150 ¦¦ Pipe dia.
label | > 900 ≤ 1500 ¦¦ 150 ¦¦ 350 ¦¦ 200 ¦¦ Pipe dia.
label | – – – – – – – – – – – – – – – –
label | ○ Compacted with handheld equipment to point of refusal.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 2.4 - Tank Installation (supplied by HPP)
label | Ref docs - Drawings Manufacturer Specifications
label | Acceptance criteria - Install as per manufacture specifications and HPP instruction.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT
section | 3.0 Filling and Compaction
checkpoint | 3.1 - Obtain Certificate of Compliance
label | Ref docs - Hydraulic Specification HPP-AEC-CIV-BL-GEN-SPT-8001 Cl.10.3
label | Acceptance criteria - Certify on completion of each component or stage that the works comply with the requirements of the BCA certifier and/or other authorities. Department of Fair-Trading Inspection to Sewer Pipe.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Certificate of Compliance
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Marker Tape
label | Ref docs - Design Drawings
label | Acceptance criteria - Detectable Marker Tape to be installed a minimum of 300mm above the pipe.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
checkpoint | 3.3 - Backfill & Compaction above embedded Sewer Pipes
label | Ref docs - Earthworks (Roadways) Cl 4.13, 7.1 Spec. 1352 Pipe Drainage [Cl 5.4]
label | Acceptance criteria - Each layer to be compacted to a density that is no less than the density of the existing adjacent material. If the existing material density is unknown, minimum relative compaction to be: -
label | ○ 92% for general fill areas
label | ○ 95% for pit and conduit bedding
label | ○ 97% for select fill areas and sections of the trench above the overlay zone and within 1.5m of top of pavement.
label | – Layers not to exceed 150mm compacted thickness.
button | Acceptance | Yes,No,N/A
label | Key - S
label | HPP CON Key - S
label | HPP QA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
section | 4.0 Conformance check
checkpoint | 4.1 - Carry out CCTV Inspection
label | Ref docs - Hydraulic Specification HPP-AEC-CIV-BL-GEN-SPT-8001 Cl.9.3
label | Acceptance criteria - Inspection of all in-ground drainage systems after installation and prior to practical completion.
label | ○ All defects disclosed during the tests shall be remedied immediately and, if required fresh tests shall be carried out
button | Acceptance | Yes,No,N/A
label | Key - R
label | HPP CON Key - R
label | HPP QA Key - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Inspection Report
checkpoint | 4.2 - Hydrostatic Test
label | Ref docs - ASNZS_3500.2-2021 Plumbing and drainage Part 2: [cl 15.2]
label | Acceptance criteria - The sanitary plumbing and sanitary drainage shall be filled with water:
label | (a) for sanitary drainage, to a height of not less than 1 m above the soffit level at the highest point of the section being tested;
label | (b) for sanitary plumbing, to the spill level of the highest fixture or to the flood level of the lowest sanitary fixture, whichever is higher; and
label | (c) in either case, not exceeding 3 m at the lowest point of the test section.
label | ○ The pressure shall be maintained without leakage for at least 15 min. The source of any leak shall then be ascertained, and any defects repaired. The section under test shall then be retested.
button | Acceptance | Yes,No,N/A
label | Key - R
label | HPP CON Key - R
label | HPP QA Key - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Inspection Report
checkpoint | 4.3 - Survey Report
label | Ref docs - Spec. 0161 Quality [Cl 3.13]
label | Acceptance criteria - An as-built survey of the drainage system been completed to ensure all pipes are within construction tolerances.
label | ○ Plan: +/- 200mm
label | ○ Level: +/- 20mm
button | Acceptance | Yes,No,N/A
label | Key - R
label | HPP CON Key - R
label | HPP QA Key - R
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey report
checkpoint | 4.4 - Acceptance and closure of non-conforming items
label | Ref docs - Spec. 0161 Quality [Cl 3.8]
label | Acceptance criteria - NCRs to be opened for non-conforming items and closed prior to closing construction lot.
label | HOLD POINT
button | Acceptance | Yes,No,N/A
label | Key - H
label | HPP CON Key - H
label | HPP QA Key - H
holdpoint | AUTHORITY HOLDPOINT