## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | INF-HSEQ CC0398-ITP-035 Concrete Pile Cropping Rev A | itp |  |  |  | Yes | INF-HSEQ CC0398-ITP-035 Concrete Pile Cropping Rev A | 4c4a6751-f535-4b4a-a697-a5d955c6f6ee
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Starter Bars
label | 8ae24b3d-abce-5ec3-a865-da3d22f551ae |  | note | Acceptance criteria - Are starter bars (if exposed) in suitable condition:
label | 26aae61d-2e11-5bc2-8468-d6ce6b5c6b60 |  | note | – Straight
label | 012b3866-40be-52a2-8ae8-c5bba30a2dfa |  | note | – Free from excessive rust
label | da809df4-11ed-55ca-9580-ad82b8752848 |  | note | – Correct height projections
button | f747c67d-98e0-5e95-b947-4f033c769e31 |  | button | Acceptance | Yes,No,N/A
label | b648de6a-d547-58ea-aa33-9dc2bb839aab |  | note | Frequency - Once per Pile
label | 8bf1e468-0fd0-5880-873b-68e44c04f331 |  | note | Key - S
checkpoint-group |  |  | section | 2.0 Pile Cropping
checkpoint-status |  |  | checkpoint | 2.1 - Set out
label | 547f3e8a-9c95-53c6-9279-ec3ac70702f9 |  | note | Ref docs - DWG No. GRN-92002-030002 – 10
label | 7a97ffcd-c497-5834-ab89-9a8989418304 |  | note | Acceptance criteria - Pile cut off has been marked by survey
button | 16891ff0-f0d8-5aca-a0b4-ea99bd4bdea6 |  | button | Acceptance | Yes,No,N/A
label | 32415fad-52df-55de-9551-5d7437b240d9 |  | note | Frequency - Once per pile
label | ea87b81d-777d-5230-beec-105541b3cec9 |  | note | Key - W
checkpoint-status |  |  | checkpoint | 2.2 - Pre-Cutting (if required)
label | e49d1463-e486-50ab-9dcd-8ba4792b90cb |  | note | Acceptance criteria - Has the pile been pre-cut along survey marked level i.e. ring cut method
button | 87296c93-4e49-505e-837e-62f45d55a68a |  | button | Acceptance | Yes,No,N/A
label | 6f185c69-5e93-501e-b2a8-f79cc06c5f79 |  | note | Frequency - Once per pile
label | 00abd880-eecb-5802-9f7e-6875a3e1f36f |  | note | Key - S
checkpoint-status |  |  | checkpoint | 2.3 - Irregular Concrete
label | 764a1a55-27f2-5386-9703-ac4da874dcc8 |  | note | Acceptance criteria - Large uneven/jagged concrete sections to be removed to create flat concrete cut off level
label | d90861ba-1252-5b52-98d7-e507ecc8f546 |  | note | Frequency - Once per pile
label | 10c8b0f0-c2ca-5cac-8a90-7fb2aad3a8dc |  | note | Key - S
checkpoint-group |  |  | section | 3.0 Conformance check
checkpoint-status |  |  | checkpoint | 3.1 - Tolerance
label | a730d33a-9f35-5641-bde1-b78330e193fa |  | note | Ref docs - DWG No. GRN-92002-030002 – 10, As per civil (235929) drawings
label | a4970c45-9438-592d-b7aa-d90ca2f68587 |  | note | Acceptance criteria - Survey to check actual pile cut off level is within +-+-25mm of cut off level.
button | e469f67c-a8e9-53ff-bcad-9e7658341987 |  | button | Acceptance | Yes,No,N/A
label | 1beded09-da3b-5934-9a83-5b8f9e0da0e0 |  | note | Frequency - Once per pile
label | 94c247b9-392e-570c-b7ca-c0cb7b147bc4 |  | note | Key - S
checkpoint-status |  |  | checkpoint | 3.2 - As Builts
label | 8fe34c38-2987-583d-9455-7320780f7cba |  | note | Acceptance criteria - Survey to pick up cut off levels for as-builts
button | 69d2f9bd-cbaa-5645-9baa-4cfcb2c102f5 |  | button | Acceptance | Yes,No,N/A
label | b57b76f9-0680-5eb7-94a2-6e5c4eb6ff82 |  | note | Frequency - Once per pile
label | eb59b1ea-608a-5ad2-ac26-b338b34c4cd4 |  | note | Key - S
checklist-flat |  |  | checklist | [Rename] Document Upload Checklist |  |  |  |  | Yes | [Rename] Document Upload Checklist | 76c6cdce-e3d9-41a3-8540-d3cda204792b
checkpoint-status |  |  | checkpoint | Document Uploaded Below
checklist-sectioned |  |  | checklist | INF-HSEQ CC0398-ITP-032 GRE Installation Rev 1 | itp |  |  |  | Yes | INF-HSEQ CC0398-ITP-032 GRE Installation Rev 1 | 89d4c807-6fd7-47cb-ab95-9fa653e64bf6
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Set out
label | 30713abf-c728-50b9-be2b-6ed4b4a9e9d2 |  | note | Ref docs - Drawings
label | 786e257b-6d88-5f96-94c1-2ea430fa376d |  | note | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
button | 3b23c7b9-71f8-5b57-a725-40fe12f52f8c |  | button | Acceptance | Yes,No,N/A
label | 4cf31203-4eee-51d6-9509-a70825913db4 |  | note | Key - H
label | e413c664-690d-5106-b782-861b88454577 |  | note | MDR/VIVA - W
label | 65d4218c-b18d-5ae5-8445-1dcdeeee490d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | e2899be5-b8d7-58b5-84bf-564a010beee8 |  | textbox | Drawing No.
text | b405ebfc-9fbe-5046-b9cd-df742066b028 |  | textbox | Rev
checkpoint-status |  |  | checkpoint | 1.2 - IFC Submission & Approval
label | f96de24c-a172-59b5-81b7-e8d30660ffd6 |  | note | Ref docs - Drawings
label | 1993cee6-53af-5cdf-914a-2a07012ec46d |  | note | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | 00df8c37-fe2a-5b97-bbf3-5323ec4dcbbf |  | button | Acceptance | Yes,No,N/A
label | 588c79be-bedf-5ff9-a61a-09045614bcfe |  | note | Key - W
label | 239d854c-89d2-57f5-b7e9-6b1b122f3c5f |  | note | MDR/VIVA - W
checkpoint-status |  |  | checkpoint | 1.3 - GRE pipe confirmation
label | ba7e2e4d-dbad-5f0e-92b7-ea558b642845 |  | note | Ref docs - Drawings, QF-108-01 Material Receipt Initial Inspection
label | 936cd6f9-24e6-5ed5-aca3-7df2086375d0 |  | note | Acceptance criteria - Has the correct class & type of GRE pipe been supplied and free of defects?
label | b52e2cad-3baf-5e11-93f5-bf50dfda8077 |  | note | ○ Verification of material tag (heat) number
button | 54e1cb37-b599-5877-ac4e-d086997d692a |  | button | Acceptance | Yes,No,N/A
label | de104475-90b8-5af3-8ec7-309b331a5bfa |  | note | Key - H
label | eb5c0fc7-f264-5168-824f-f7e78a91288a |  | note | MDR/VIVA - W
label | fe2dca5e-38b0-54a9-a1c8-c7323eda5c20 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 97378374-0cce-5b5b-ae85-b1843024c635 |  | tickbox | Material Inspection Checklist
checkpoint-status |  |  | checkpoint | 1.4 - Permits
label | facfa38f-1cd7-58f0-a248-1fb4e787f1d0 |  | note | Ref docs - Symal Safety Procedure
label | 25f4168a-d062-5e3b-aa57-b46b9db0948e |  | note | Acceptance criteria - Have the below permits been created as required.
label | e80a82e8-381a-531d-bcea-0134343b8a00 |  | note | – GPP
label | e47e8d71-7556-5d5f-8ed5-4e7b509a2c12 |  | note | – Working at Heights
label | b664ff73-05f5-51df-99d4-216f445adade |  | note | – Hot Works
label | cee09680-e01f-552a-aa6d-7b3e898cab09 |  | note | – Confined Space
button | 15b6ba1d-3c9e-5ded-8ab0-30aa5438e010 |  | button | Acceptance | Yes,No,N/A
label | f8c19699-76b6-5e43-a329-cab66101b23e |  | note | Key - H
label | 0ef20b02-7e86-5f25-9348-87e9cc93d093 |  | note | MDR/VIVA - W
checkpoint-status |  |  | checkpoint | 1.5 - Determine Lot Size
label | e21f428f-a0bc-5753-8bb3-35c1d7d4868f |  | note | Acceptance criteria - What is the lot size?
button | 2663c145-56ab-5646-b24c-8286a8e0e071 |  | button | Acceptance | Yes,No,N/A
label | 19d3046e-c7cb-57bb-bb39-8b3e3fc79912 |  | note | Key - S
label | be91c779-2273-528c-8cab-08fae293e146 |  | note | MDR/VIVA - W
label | 48a2fae0-d4d3-52d5-91d3-e3757a3f64f7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 0e5fb777-fbc3-5563-9810-4fdb69d32e65 |  | tickbox | Lot Map
checkpoint-status |  |  | checkpoint | 1.6 - Joint Pre-Qualifications
label | 1da3b421-5826-5393-84df-468965e8b937 |  | note | Ref docs - Qualified technician qualifications and this ITP
label | b89d1b2b-6593-5bf4-b701-1e0fa94ca9e1 |  | note | Acceptance criteria - Technician qualifications submitted to client for approval
label | 6c601e05-23e8-57e0-9dbd-3f2e7ca6d618 |  | note | ○ Welding Qualifications Equipment Calibrations
button | 0320eb26-4f89-5952-9e5a-12a6042e28ec |  | button | Acceptance | Yes,No,N/A
label | 06ae4ce3-f304-53b7-92f6-27013394d5c9 |  | note | Key - H
label | f23d664f-473f-5e88-887c-df62ed7d6583 |  | note | MDR/VIVA - H
label | 693d66bf-e7ff-5a87-acd9-365576b0e6bf |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 733e509e-ab28-5d1a-8831-c6361343a3b3 |  | tickbox | Certifications provided to client
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.7 - Material Approval
label | 4f5ffb21-a37b-5c66-987d-32a2250ad910 |  | note | Acceptance criteria -
label | 7979c967-4c4d-5c97-8fc2-40445dcac3e5 |  | note | Have all materials been approved for use
text | 684403d9-1876-58f4-af5a-3db3e7715e9d |  | textbox | Bedding/Haunching Material
text | 5b25a19d-79c4-5f1a-a4cf-f6ae4256c98a |  | textbox | Backfill Material
label | ecff2fb0-fee7-5349-92fe-09c4c47939e5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | 30197b59-df69-54e2-beb4-cc07e29b22c1 |  | textbox | Material Approval Reference
checkpoint-group |  |  | section | 2.0 Excavation and Bedding
checkpoint-status |  |  | checkpoint | 2.1 - Service Locating
label | cf29ad10-f86e-50dc-9540-73ee4d504b63 |  | note | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
label | 9cdd3930-cd3c-5455-a906-8d4d841d96f9 |  | note | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | 44c97db5-6c6d-55a7-b059-b5b01305bef3 |  | button | Acceptance | Yes,No,N/A
label | 74b04a3e-3017-5527-a473-10ae7f2b9fa6 |  | note | Key - H
label | 32df1a5b-1a2a-5b6c-a049-a9911ebd6328 |  | note | MDR/VIVA - S
checkpoint-status |  |  | checkpoint | 2.2 - Excavation
label | 16fbca72-4794-519e-a9fa-4e1de14d41bb |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALLSect ion 12.1.12
label | 62155c81-3b03-5392-b137-1d0fd014cd4d |  | note | ○ SUN_ENG_P RO_015 Bondstrand Piping UG Installation Procedure Section 3
label | bb9363e7-048f-5d7f-9c6a-127e57cd2445 |  | note | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth.
label | a53247f9-7304-595a-8b9c-353ff3bfc137 |  | note | ○ Width of excavation to be 1.25 * OD + 300mm
text | a82df1b2-f768-53a0-a213-1f4d37bb5124 |  | textbox | Pipe Diameter
label | 5fa84543-4642-5d7d-bb14-07e154d9c9df |  | note | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
label | 92fc4509-5166-59ea-96b5-f0bbd04d6c99 |  | note | ○ Trenches to be benched and battered as required (if trench >1m deep). Benches/batters to be 1:1. No material/plant to be placed within zone of influence.
button | de1d88cb-9936-5a9a-a462-b08004b2418a |  | button | Acceptance | Yes,No,N/A
label | ca7decc9-bd3d-5b95-875b-90d1d27d6afc |  | note | Key - W
label | c277ddbc-ba32-52ba-9e7c-e0bab806a685 |  | note | MDR/VIVA - W
checkpoint-status |  |  | checkpoint | 2.3 - Bedding
label | 54faa16d-8371-5b8b-bec7-391dde68b4e2 |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8.
label | f386c04f-2692-5e15-b5d1-61a2ab2612c2 |  | note | ○ 239529- MG1668- 15740-0400- SD-000010- NOV Bondstrand pipe installation guide - GRE
label | be5c67d8-a9c2-5bf9-a44c-859551ed1361 |  | note | ○ SUN_ENG_P RO_015 Bondstrand Piping UG Installation Procedure Section 3
label | 307f42ad-853d-598d-b7ce-168ed0d96f2c |  | note | Acceptance criteria - 150mm Bedding to be placed & compacted at the base of the trench.
button | a6732c34-6ebb-5d32-8ae0-4b8821ec0739 |  | button | Acceptance | Yes,No,N/A
label | c9d859d5-68ae-5fc6-9df0-e89bfe051a13 |  | note | Key - S
label | 5428a919-e1c4-57f0-9e89-a65ea123f96a |  | note | MDR/VIVA - S
label | a6dd7323-79be-573b-af5a-b1975bfa15b0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 0b8e0979-7ff9-5f98-9748-6f5c29201350 |  | tickbox | Delivery docket
checkpoint-group |  |  | section | 3.0 Bonding & Laying
checkpoint-status |  |  | checkpoint | 3.1 - Above ground fabrication
label | ac128511-4058-54f3-abc5-477770663af0 |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
label | 24c01a29-bf81-5ec9-a0c0-e9381b39454f |  | note | Acceptance criteria - Has works been conducted as per Sunrise ITP SUN_23_003?
button | e1039a33-f996-56f4-9ac0-6c7ef7b6b1bc |  | button | Acceptance | Yes,No,N/A
label | 7c318ffc-084a-5803-97d2-23e993a23be9 |  | note | Key - W
label | ad16aebf-dfd2-560a-9ad7-19d2b80f5f7f |  | note | MDR/VIVA - S
label | 149682e8-cca6-5aff-8df3-e93af23b1f9c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | ce8994a6-7625-5ba1-ade7-29640d9d99f7 |  | tickbox | QF-068-18 – GRE Bonding Joint Record
checkpoint-status |  |  | checkpoint | 3.2 - Lifting into trench
label | 8e861b5d-2860-52e7-8cf5-69cf6dbd59c6 |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
label | 7c1c5b9d-26fe-5349-8623-42f0eb01bdce |  | note | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
label | 0ae23950-b10e-5318-afc9-b6c1442dd3a4 |  | note | ○ Have pipes been laid to true line and level?
label | c65b0773-d204-5979-80bb-ff6a3629d952 |  | note | ○ Has MDR been notified before the laying of pipework?
button | 86849bfc-cf35-5ada-b8b9-2f6ac00abff1 |  | button | Acceptance | Yes,No,N/A
label | 61838248-ac87-5356-a463-5bfd1bfff234 |  | note | Key - W
label | d94489fc-0488-594b-8b37-2bcb1844d20c |  | note | MDR/VIVA - S
checkpoint-status |  |  | checkpoint | 3.3 - In ground fabrication
label | dd92a3d5-6faf-55a8-88ab-3d2e1b31ef42 |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
label | 72f09452-57bf-51ff-960b-702c99a35d79 |  | note | Acceptance criteria - Has works been conducted as per Sunrise ITP SUN_23_003?
button | 741c6690-04de-5cc0-83bc-66718277384d |  | button | Acceptance | Yes,No,N/A
label | debd8762-a75c-54cb-8faa-652eba5c170e |  | note | Key - W
label | 2afe1bed-fd29-5200-9503-285e0c55a3c5 |  | note | MDR/VIVA - S
label | 9b72c91b-ca8e-5082-bb73-53d305b34568 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | f0f767ce-8ab1-5fcc-8ac6-8ce53bd3aaa0 |  | tickbox | QF-068-18 – GRE Bonding Joint Record
checkpoint-status |  |  | checkpoint | 3.4 - Haunching
label | 0b2e9937-b249-51fa-8f22-89fcf2e2d0be |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL
label | 57ddd853-6e4a-58ce-b5bb-6c5d199d68b6 |  | note | Acceptance criteria - Has the pipe been haunched?
label | 0fb8dd1a-6b10-5d5b-9199-ff5784090173 |  | note | ○ Have voids been removed from haunching material?
button | ae52b1d8-8849-5f4d-bac9-d89e53d43c2a |  | button | Acceptance | Yes,No,N/A
label | 7f6caa72-8b13-5cf2-ae14-d7b7e35fec87 |  | note | Key - W
label | d2485979-e57a-59e8-bbc2-455441c4159a |  | note | MDR/VIVA - S
checkpoint-status |  |  | checkpoint | 3.5 - Survey Pickup
label | 8f6a8730-4ed1-5d87-9e55-365b105e9f06 |  | note | Acceptance criteria - Has the pipe been picked up by the surveyor? Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
button | 89542738-7ef5-526f-8dab-702b999f512b |  | button | Acceptance | Yes,No,N/A
label | d8c1fafc-8cc4-5772-87f5-147a8d20f6a3 |  | note | Key - H
label | 5bc1259f-2ac4-5069-9458-305c5e040340 |  | note | MDR/VIVA - S
label | 2be8cae6-4c17-5bfd-88f3-4504bac1dc0f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 9060a391-0bcb-5407-b7d7-e5964bc20d1b |  | tickbox | Survey as-built report
checkpoint-group |  |  | section | 4.0 Testing and Conformance Check
checkpoint-status |  |  | checkpoint | 4.1 - Test Pack
label | 02a3257c-afbb-5eef-8166-5ca6f887ca65 |  | note | Ref docs - SUN_ENG_P RO_010 R0 GRE Hydrotesting procedure
label | bc78c93e-6e45-57fc-9b6e-c941fadc02d4 |  | note | Acceptance criteria - Has the test pack been reviewed and accepted prior to Hydrostatic Testing?
label | d828e2cb-e953-54ab-9fab-95395747e17f |  | note | Test Pack to include:
label | 77abd582-cab0-5f60-b942-9da198e90dea |  | note | – Pipe Runs/Location of testing
label | 09dbcddd-e90b-5e47-9782-1eab54dcf140 |  | note | – Materials initial inspection
label | 52d47666-02c6-5293-9aef-fd5a0c513019 |  | note | – Joint Inspections
label | 66a26b63-0d3e-5c48-94d4-93cc42915f80 |  | note | – GRE Bonding Joint Record Form
label | fa1782ea-204f-5d5e-b4b4-93018f62be9f |  | note | – Flange Record Sheet
button | 9b008a47-6087-5db9-84bb-2b399b318c99 |  | button | Acceptance | Yes,No,N/A
label | 594d641b-f31f-53d2-9650-4887a27fdc83 |  | note | Key - H
label | 72732447-ad9c-5613-9abc-7a3344f4ea3f |  | note | MDR/VIVA - H
label | fe18d6be-516e-55cd-8164-bbfd7b7fb75d |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 71a52ff0-e8af-5f42-b8a2-e22fbdf19b9d |  | tickbox | Test Pack
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.2 - Hydrostatic Testing
label | 377786da-0344-56ed-ae85-34d86deb3eff |  | note | Ref docs - 235929-000- CV-SP-00006 UG PIPE FAB and INSTALL Section 13.2
label | 3f8e3e78-d038-5d16-8891-a41a6d3be94d |  | note | ○ SUN_ENG_P RO_010 R0 GRE Hydrotesting procedure
label | 175a3580-8587-54d9-b551-621f8f9fac8c |  | note | Acceptance criteria - Has the pipework been tested as per the manufacturer’s specification for the required duration?
label | ad4363f6-0a97-58ab-8bb3-b84209370b72 |  | note | Integrity Test
label | 4d8896da-f11c-5d62-b634-f9b2deb7288a |  | note | ○ 2-hour test –1.5 x design pressure for 2 hour hold (Refer to Hold Point in Subcontactor ITP below). Visual Inspection required of joints upon completion.
label | 6572c86f-e9b9-542a-992e-5072b69ab849 |  | note | Leak Test
label | f860c02e-2245-53ce-bb0f-17bd2c97f9f6 |  | note | ○ 1.1x design pressure.
boolean | 189b96c2-4484-5e24-a500-0822a6c0c2a6 |  | tickbox | 2-hour test – Visual Inspection required of joints upon completion to verify no leaks.
label | 99b677ce-3a69-5618-9cb3-8d950b6accad |  | note | ○ Has the pipework passed the testing requirements with no leaks?
label | 3c19647f-14c1-54e8-8424-e903ef5c1f99 |  | note | ○ If no, proceed to item 4.2.
button | e2e2f63b-f74b-5a15-9eee-308e9e06edd7 |  | button | Acceptance | Yes,No,N/A
label | 6f821ff9-9060-5765-ab6f-560a9fba9052 |  | note | Key - H
label | 6e86834a-8065-5c43-a7d6-05be3b28e5df |  | note | MDR/VIVA - H
label | 316e3ad5-587e-59f0-ab2e-d6e82b29dad5 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | b9d2fc37-606a-5c5b-905a-abc5b048c9b7 |  | tickbox | QF-129-01 – Hydrostatic Test Log Sheet
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 4.3 - Repair
label | 76ebf9bc-9f0c-5353-97b6-81e62e150b3d |  | note | Ref docs - SUN_ENG_P RO_012 Re-condition of Adhesive Bonding Socket - Joint repair
label | 4982ab20-9b71-511e-9fcf-8bfa8f129a95 |  | note | Acceptance criteria - Has the leak been identified?
label | ddb97047-c6f4-5989-b4e6-6d4ad2e63cf4 |  | note | ○ Has the leak been repaired as per the manufacturer’s specification/approved methodology?
label | ab4bcf9b-2a34-5864-9dda-0b49b0a58063 |  | note | ○ Has the pipework passed subsequent testing requirements?
button | bc56fd7c-f5fc-5a1c-a2ad-8f6169dc4193 |  | button | Acceptance | Yes,No,N/A
label | 47ba2257-e7b2-55d3-9318-726f18079f40 |  | note | Key - H
label | a4976d72-cb61-5eb1-bda6-83420e623f3b |  | note | MDR/VIVA - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 5.0 Backfill
checkpoint-status |  |  | checkpoint | 5.1 - Sand Backfill
label | c73ab87a-ddf7-53c1-9bcd-9b7a6328c7f7 |  | note | Ref docs - 239529-MG1668-15740-0400-SD-000010-NOV Bondstrand pipe installation guide - GRE
label | 37bd37a6-3cca-5f49-9e40-8152b6cd09fb |  | note | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
label | 52c71583-3096-5df8-968a-cd4929f34c93 |  | note | ○ No compaction equipment to be used until 300mm above pipe.
button | cf90d740-9af1-5b79-8f95-37f85efb4662 |  | button | Acceptance | Yes,No,N/A
label | 73ab7897-12ca-5d7a-9e13-1e3cc0df075e |  | note | Key - S
label | 4a6cc8a8-0e9a-5bad-92e6-94065a7f614e |  | note | MDR/VIVA - S
checkpoint-status |  |  | checkpoint | 5.2 - Select Fill Backfill
label | e91066dc-0e6c-5b32-8276-c12854580abc |  | note | Ref docs - 239529- MG1668-15740-0400-SD-000010-NOV Bondstrand pipe installation guide - GRE
label | 5a994ac1-8485-565a-af1e-6dee59842d6e |  | note | ○ 235929-000- CV-SP- 00002 – Earthworks
label | 425834b3-f996-5194-b8ff-7a9e2c56ffbe |  | note | Acceptance criteria - Has select backfill been placed in layers not exceeding 150mm loose thickness?
label | 1206039d-ad40-50fe-82eb-dacb2d265088 |  | note | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm above pipe.
button | 8cf2ea21-09f4-5b4d-888e-b8681c961a36 |  | button | Acceptance | Yes,No,N/A
checkpoint-status |  |  | checkpoint | 5.3 - Compaction Testing
label | b8c3c111-55dd-5f8b-b0bf-9c40019ff2c1 |  | note | Ref docs - 235929-000- CV-SP- 00002 – Specification for Earthworks
label | cce24e23-ed0f-543e-8737-69745b54ced2 |  | note | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density
label | f05cbe95-f09e-501a-9b58-cab4516c9116 |  | note | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
label | 979d99c5-d0c6-57df-9e61-69b0d4ceaa25 |  | note | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
button | 2d893ed4-9f1a-558e-b36c-d9c3abd5c61b |  | button | Acceptance | Yes,No,N/A
label | a9038a37-5466-5ad8-9d01-42daedc1b920 |  | note | Key - W
label | 97e07f3c-cad4-5768-a95a-4170bd1b5a21 |  | note | MDR/VIVA - S
label | 6b97d6dd-7c8d-503d-85a4-ede8245822e7 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | e623dfe5-be91-5fff-ab70-3b9655ae2815 |  | tickbox | Geotechnical Test Report
checkpoint-group |  |  | section | 5.0 Documentation Submission
checkpoint-status |  |  | checkpoint | 5.1 - Subcontractor ITP
label | 4fbaa0db-e332-57d3-b0f9-d61e4069d772 |  | note | Acceptance criteria - Has the subcontractor ITP been signed off and accepted by relevant parties?
button | f2826119-88c4-5752-87e8-e9589ef4dcac |  | button | Acceptance | Yes,No,N/A
label | 4a5daf6f-e66f-596a-866d-7e3d078b8bd0 |  | note | Key - W
label | 23ffdd2c-1a5c-500c-9d7e-bb535b963b4e |  | note | MDR/VIVA - W
label | 0e078a37-2b29-5edb-bc64-6eec0d5b6636 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 5f7bb4d0-975c-5f3b-b789-fe4f6a6012fe |  | tickbox | ITP_SUN_23_ 003
checklist-sectioned |  |  | checklist | INF-HSEQ CC0398-ITP-002 Bulk Earthworks REV D | itp |  |  |  | Yes | INF-HSEQ CC0398-ITP-002 Bulk Earthworks REV D | c49b5c58-0a77-4f97-93e4-48886035b4bf
checkpoint-group |  |  | section | 1.0 Preliminaries
checkpoint-status |  |  | checkpoint | 1.1 - Determine lot size
label | 17c2ed7f-6649-5816-b0d9-c9f08c804f2d |  | note | Acceptance criteria - What is the lot size?
text | 939eeafe-eea4-5169-8369-1b238759f0fb |  | textbox | Acceptance |  |  | m2
label | d7856abb-22da-55e1-ac94-131e27f59581 |  | note | Key - S
label | 3f5c9f41-ba36-59f3-aa3e-d7d953263178 |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 1.2 - Survey set-out
label | 95c23751-464a-5c23-8c42-6c4475203c53 |  | note | Ref docs - 235929 IFC Drawings
label | a003dc98-8074-5f09-bf30-347080541f43 |  | note | Acceptance criteria - Has the work area been set out for line and level?
button | 414fc0b9-d0aa-503a-8b72-1acc0142d5e7 |  | button | Acceptance | Yes,No,N/A
label | 244e5a50-04fe-53a3-996b-948074e374a1 |  | note | Key - S
label | 87ade986-a2da-519e-a4d5-964d14d3564b |  | note | MDR/VIVA Key - S
label | 93a9bdc1-186a-52b6-a29c-66d2021e49f0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | 5feb5bf7-0aac-5792-a0c4-02653b7d41cf |  | textbox | IFC drawing number:
text | 9f62bc1b-b9a8-564c-a937-859df44285e6 |  | textbox | Rev:
checkpoint-status |  |  | checkpoint | 1.3 - Excavation material classification
label | a386b8ef-731d-5cf5-85fd-d2db39fe7f49 |  | note | Ref docs - 235929-000- CV-SP-00002
label | 475ed1a0-a607-5f85-825b-1cafb9b13c08 |  | note | Acceptance criteria - Has the material being excavated been inspected with category agreed upon by Superintendent and/or Superintendents Environmental Representative?
label | 39dfcc38-a132-502d-b61c-e070d7fa269c |  | note | Tick category below:
boolean | 16d27692-38e0-575c-8923-9bee94e3c519 |  | tickbox | Common Fill (CF1)
boolean | c9acafa7-2d96-5355-b866-959295f39c36 |  | tickbox | Sand Fill (S1)
boolean | dc14a3b9-f0b4-5abf-89ce-46bb6222f428 |  | tickbox | Structural Fill (SF1)
boolean | 48594622-3c27-5471-b593-1cc677bff502 |  | tickbox | Topsoil (TS1)
boolean | fdd39b43-d498-582a-af44-4616da946bd2 |  | tickbox | Reuse of Site Won material
boolean | c00254ca-c049-53a1-a7b8-1884a2c653d2 |  | tickbox | Rock
boolean | a54318c8-52cd-539d-88c0-f050911d3d4f |  | tickbox | Contaminated Material
button | 1183bc04-d025-5e22-9ecb-27f15ba52dff |  | button | Acceptance | Yes,No,N/A
label | d2efc44e-4948-521c-a787-b6633d9f67ce |  | note | Key - H
label | 7b586300-13bb-5686-abd2-dfda87b38f31 |  | note | MDR/VIVA Key - W
checkpoint-status |  |  | checkpoint | 1.4 - Material Submission / Approval
label | a0176bd7-d038-5164-97ec-68460346314a |  | note | Ref docs - 235929-000- CV-SP-00002 Sec 11.1 Aggregate report
label | 881c9d6c-e129-5c59-9257-eb9855179d9b |  | note | Acceptance criteria - Has any imported material (to be used as permanent fill) been approved by MDR for usage on site.
button | 5d547fea-255f-56da-91aa-79525e69c8df |  | button | Acceptance | Yes,No,N/A
label | 3be45e37-2c04-58b9-a4c2-d8753b2f82f5 |  | note | Key - H
label | 0ab96b98-a950-5ce1-be24-24bc7efc1d34 |  | note | MDR/VIVA Key - H
label | 4f0825b1-5d2f-581d-b3fe-bebcc0e8520c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 42e5086d-e728-57fb-b1df-376f7a475cd9 |  | tickbox | Material mix design
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 2.0 Bulk earthworks – cut
checkpoint-status |  |  | checkpoint | 2.1 - Subgrade preparation
label | 079f5e68-cd67-56df-b0cd-3c707fbe5dc2 |  | note | Acceptance criteria - Has the area been excavated to top of earthworks layer.
label | 7d15c849-32c2-5dd2-8314-4b8a1a458e35 |  | note | ○ Note: Existing surface material is approximately 200-300mm of crushed rock.
label | ded8d32c-22b4-56d2-978e-5e1449224d11 |  | note | ○ Is the surface evenly graded and free-draining.
button | 443106d1-8ecc-5b77-8c79-0478f9a1e8f8 |  | button | Acceptance | Yes,No,N/A
label | a53716f1-44f3-559b-9222-3b3f49b71e3e |  | note | Key - S
label | 543f0d46-93a3-5fb4-8c5b-c7498753c251 |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 2.2 - Material Export / Stockpiling
label | 743366f3-681d-5363-9d44-c0b79f0b780e |  | note | Ref docs - SMP 20359156-211-R-Rev
label | e8031a82-714d-5411-b201-9f3e72df01b8 |  | note | Acceptance criteria - Adherence to Soil Management Plan.
button | e142d24b-eeab-5ed9-9a2e-7c11f2d83c71 |  | button | Acceptance | Yes,No,N/A
label | b4742af9-5605-57e9-bd5d-53ecc9238a6b |  | note | Key - S
label | 2e09c9db-4dc1-5810-8cda-c8b97f430d49 |  | note | MDR/VIVA Key - S
checkpoint-group |  |  | section | 3.0 Bulk earthworks - fill
checkpoint-status |  |  | checkpoint | 3.1 - Preparation of surface
label | 247b5235-85c8-5547-b733-127f326c7585 |  | note | Acceptance criteria - Has surface been cleared of all loose material visible on surface.
button | 94210f34-239e-5a10-859b-1ba3ee25fd17 |  | button | Acceptance | Yes,No,N/A
label | 6d2f2968-c8a7-58ae-b197-1ea0492a2235 |  | note | Key - S
label | 5986627b-044d-5721-98fc-f156ab469f1f |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 3.2 - Compaction Trial for Blended Material
label | 600de072-e43d-5d8a-8b29-310d6c0f9dd1 |  | note | Ref docs - 235929-PE- WI-000009 - Backfill Specification
label | 6ef316aa-259f-5d74-990d-2ad22aa91172 |  | note | Acceptance criteria -
button | 3265b67a-9766-5a39-8ece-21c60a190621 |  | button | ○ Is the material to be used for backfill blended material. | Yes,No,N/A
label | 00f6c107-39d5-5e67-9602-24b0ca652853 |  | note | If No, go to item 3.3.
button | 87ff2c05-68f2-5396-a1f1-7eb495a3802a |  | button | ○ Has the compaction trial been undertaken? | Yes,No,N/A
button | 356fb490-cdc6-5a1b-b546-9af580793365 |  | button | ○ Did the compaction trial achieve the appropriate design backfill requirements of 70kPa? | Yes,No,N/A
button | 3339ed77-d485-5166-a70b-2d70228c0523 |  | button | ○ Does MDR approve usage of site blended material for backfill purposes? | Yes,No,N/A
button | 8f4995db-6b67-5ad9-b136-cd0a4dbb8d5c |  | button | Acceptance | Yes,No,N/A
label | 7e239d07-0614-5b34-b811-48925eaf4a53 |  | note | Key - H
label | e5fd72dd-8075-5ba8-a67a-0ecc5afc56e7 |  | note | MDR/VIVA Key - W
label | 5dfb2fbb-bad2-58e2-a061-7784fedb11df |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
text | a51ec0d1-a2fb-5fd1-b764-ceb991274e3f |  | textbox | MDR approval:
text | 0b7b470a-f52a-5f02-b88c-e9edcad8ceaa |  | textbox | (correspondence reference number)
checkpoint-status |  |  | checkpoint | 3.3 - Fill Placement
label | 119184bd-f636-5039-a4bc-8c3367637c5b |  | note | Ref docs - 235929-000-CV-SP-00002 Sec 12.2, 235929 IFC Drawings
label | 8fe5cde6-7b3f-5a72-8946-3885580a2681 |  | note | Acceptance criteria - Has fill been placed in maximum 200mm compacted layer thickness?
button | e434c6a8-d8c4-59f1-8425-5c6dcfa01fdd |  | button | Acceptance | Yes,No,N/A
label | e1ba56e0-6c97-5bc7-8eb9-5cfd038ffa44 |  | note | Key - W
label | 319a9a92-6fef-5c4c-a011-4dad984f2936 |  | note | MDR/VIVA Key - W
label | 8238465d-3205-5dbd-8a22-5814f173459c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
checkpoint-status |  |  | checkpoint | 3.4 - Moisture
label | bdf9774c-c3d0-504f-841f-a11c1fdddcfe |  | note | Acceptance criteria - Has the material maintained at +/- 3% modified moisture content, with additional water being added if required during compaction?
button | 0f4d56a2-bda2-532b-9091-eafaab18f2b2 |  | button | Acceptance | Yes,No,N/A
label | bb7fa767-0045-5e73-a054-4da887129cfa |  | note | Key - S
label | 34a0df43-7447-5733-ad0b-0dd2d99083ce |  | note | MDR/VIVA Key - W
label | 28c50542-a9e3-515e-9348-931f076e399c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | fd4397c8-78db-561f-9d22-ae417982ce64 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.5 - Compaction
label | 8dd9625d-58f3-5dee-9a01-ee1f6a3e57f4 |  | note | Ref docs - 235929-000- CV-SP-00002 Sec 13 & Sec 14.2
label | 2c1c660f-8f9f-5b23-be56-388e897a363d |  | note | Acceptance criteria - Has the layer been adequately compacted achieving a mean value of minimum 98% MDD?
label | 1992ca89-242d-5eb6-84a4-40644a7ed472 |  | note | ○ Density test to be completed on first backfill to verify procedure. Procedure assumed to be equal henceforth (Inspector may request additional test upon insufficient density or compaction).
label | 53ea1341-e06d-547d-9811-a95dfe9944cd |  | note | Acceptance -
boolean | 546263c4-daee-50e1-b864-598846089603 |  | tickbox | Small Foundations
label | d51e168c-162f-5adf-bf72-52fdea3e663f |  | note | (1 test per foundation)
boolean | 23220f2a-3f3c-57c2-b1d0-57f60b977850 |  | tickbox | Large Foundation
label | 01aa0de9-31c1-5d45-aeb4-b608cb4902ed |  | note | (larger than 10m2) minimum 3 tests per lift
boolean | 6436025b-dd51-55ff-9291-3dc905aa5e84 |  | tickbox | Fill Areas minimum 2 tests per 185m2 but not less than 3 tests per area
label | 2ab8f6fe-1eb4-561d-84f5-4aa65506abc0 |  | note | Key - H
label | 52be4b23-9644-5961-8d24-4cc6ca25475a |  | note | MDR/VIVA Key - W
label | acbbca5f-8ef6-587f-bf83-cd62e724f47a |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | a7f397a5-8ecc-560c-856b-3123b1ee5078 |  | tickbox | Test reports
checkpoint-status |  |  | checkpoint | 3.6 - Fill layer – test rolling
label | fa9b9cb2-6e5c-5ab7-ae3e-35fcfc6dd76f |  | note | Ref docs - 235929-000- CV-SP-00002 Sec 12
label | c71e2bf6-058c-503c-b18a-b7a318ffa9a9 |  | note | Acceptance criteria - Does the layer withstand test rolling without visible deformation or springing?
text | a9285242-a497-526b-8026-b59279a7e060 |  | textbox | List Attendees:
button | e091273a-d4b8-5080-bf13-985e291dfac3 |  | button | Acceptance | Yes,No,N/A
label | 8cbc68c6-937d-52ba-99a4-36cb9d70a2f9 |  | note | If 'no' please see below If 'yes' please proceed to Conformance Check
label | 39c24a2e-6181-598d-89b5-7e85ebabfe9c |  | note | Key - H
label | 441e742f-19dc-5f26-b13b-bb0253a4db09 |  | note | MDR/VIVA Key - W
label | c9e4d077-121e-5383-b93c-65cd02b4cb90 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 74ba581f-2fc9-5ce5-b627-f90f5236bd6e |  | tickbox | Proof roll checklist [235929-MG1668-CV- 003-SUBC-000053]
checkpoint-status |  |  | checkpoint | 3.7 - Identification of soft wet or unstable material
label | 95e5b108-fac5-5515-b8c0-cc9048cdb6c9 |  | note | Acceptance criteria - Has any soft or wet unsuitable material been found?
button | e010e420-4c20-55bc-98eb-15eb30ae9f9c |  | button | Acceptance | Yes,No,N/A
label | febfea7e-0b56-5b46-8dc1-237eac1d2d42 |  | note | Key - W
label | 80d09676-4e64-50f1-87bf-572b396ef562 |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 3.8 - Treatment of unsuitable material
label | 7623fbb6-0b92-5c0e-acd8-4fa1c88f85a5 |  | note | Ref docs - 235929-000- CV-SP-00002 Sec 12.1, Symal Proof Roll Procedure Doc
label | 0526dd2b-c120-5c17-857b-56d93c49baa5 |  | note | Acceptance criteria - Have any issues been determined?
text | 44dcaf17-29d8-5dcb-b903-396ebbd75e82 |  | textbox | (length) |  |  | m
text | f2c2b076-ad13-5148-9185-a729d9f65fd5 |  | textbox | (width) |  |  | m
button | 498a0a65-ffd3-5383-9400-4d9a02b89f6f |  | button | Acceptance | Yes,No,N/A
label | 6a2b81fc-9995-5f0f-bde7-357d0f7e278d |  | note | Key - W
label | 8ce4edd9-e6a3-5cf4-bac8-f7eb4d94ab9b |  | note | MDR/VIVA Key - W
label | c1711777-6c0f-538d-94d4-5734d8e221ef |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Proof Roll Checklist, Dockets / Photos
checkpoint-group |  |  | section | 4.0 Conformance check
checkpoint-status |  |  | checkpoint | 4.1 - Subgrade level and shape
label | 4a32164d-617a-5d45-b7d9-c8c2d2c62728 |  | note | Ref docs - 235929 IFC Drawings
label | 1ec92379-64a0-51e5-8d42-44d7d51ad26b |  | note | Acceptance criteria - Has the prepared subgrade been surveyed in accordance with and verifying specified requirements?
label | 9d26e3ab-8309-5a70-8eae-6226750a50af |  | note | ○ Final grade +- 60mm
button | 57c34ad4-27ed-57c5-9994-5f4ed7d17c25 |  | button | Acceptance | Yes,No,N/A
label | 78001b3d-1342-56e5-a5f7-0ddd17672814 |  | note | Key - H
label | 19578b77-12aa-50e7-a3a6-6215b317b037 |  | note | MDR/VIVA Key - W
label | 60c3c6fe-2e3a-588b-9791-af591495ee2e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
boolean | 86e2d997-539e-568a-a7d5-4b04bc121298 |  | tickbox | As built report
text | 5f382c3b-f132-5b5c-875d-59a7be186117 |  | textbox | IFC drawing number:
text | ad5daabb-5230-587b-bce5-a329176f6c59 |  | textbox | Rev:
checklist-sectioned |  |  | checklist | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev 3 | itp |  |  |  | Yes | INF-HSEQ CC0398-ITP-031 Blinding, Pile Caps and Slab Footings Rev 3 | fb9861af-a689-4541-93a0-241e1cc8be4a
checkpoint-group |  |  | section | 1.0 General
checkpoint-status |  |  | checkpoint | 1.1 - Material Submission / Approval
label | 38dc39c1-97aa-5987-bc61-8cc1a17d59b7 |  | note | Ref docs - AS 3600 235929-000- CV-SP-00007
label | 66bc53e2-f270-563e-a4b5-d9d15ed3de85 |  | note | Acceptance criteria - Has the mix design to be approved prior to placement. Material properties meet project specification, AS 3600, AS 1379?
label | 2051261c-d26c-51f1-a53b-15cc5181a8cd |  | note | ○ Do Structural Elements meet: Minimum Concrete strength 40 MPa or as specified in Drawings?
label | 5f725601-87d4-5f25-98f8-ff0c4a102d4e |  | note | ○ Do Non-Structural Elements meet: Minimum Concrete strength 15 MPa or as specified in Drawings?
label | 0b478f3b-221b-593b-bd2a-27904927049d |  | note | ○ Has Steel Reinforcement schedule provided to MDR for review and approved?
label | fd49ac14-fc4c-577d-b810-d73735edd6c8 |  | note | ○ Do admixtures shall conform with AS 1478.1 and are permitted if used in accordance with manufacturers instructions?
label | bfd4a202-eac0-583a-8d60-53ff6f4a61f1 |  | note | ○ Mixtures containing calcium chloride shall not be used.
button | 1e83a2a2-1a47-58b0-9171-77d1d5b38a78 |  | button | Acceptance | Yes,No,N/A
label | de1c3c54-5e6f-59fd-9d9f-cc7d4a4f11f6 |  | note | Key - H
label | dc65c313-7a5a-5d5d-a677-e787b15d0c60 |  | note | MDR/VIVA Key - H
label | 556114eb-a1b4-5385-b989-cb03ac46bf52 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Mix Design Number, Bar Bending Schedules, Material compliance certificates
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 1.2 - Determine lot size
label | 5ae5a78b-cf2a-597c-bce9-680c9cdad51c |  | note | Acceptance criteria -
text | 9cc93c84-89f3-523e-af5a-3b1a4e2623ca |  | textbox | Lot Size = Each pour section per day (location or m2) or each structural (Pilecap)
label | dfe7de41-a4ef-5ac9-b818-c1a6c13751da |  | note | Key - S
label | c76448c8-724e-5395-b5f5-34fc6089ff77 |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 1.3 - Permits
label | 9bff6d0e-771e-52a8-946a-8d127d399758 |  | note | Acceptance criteria - The following are relevant, in place and signed onto:
label | 5af0f85a-9817-5358-b330-02e31e30ebc7 |  | note | – Penetration permit
label | da668d64-52b7-55d5-b6ed-31b53edc1a2d |  | note | – Hot works permit
label | f304070e-4b95-5b82-a3d3-695a812a5b09 |  | note | – Temporary work permit
label | 79378160-af0d-5fa8-97d6-79591e53e5bc |  | note | – Working at heights permit
button | 1b6ccd4a-1282-5b7c-b04d-9e07d17fb828 |  | button | Acceptance | Yes,No,N/A
label | 138c99c4-157f-5bbc-9974-29302a05cf6b |  | note | Key - H
label | 51da0678-2edf-5890-9cd5-b33a628dca49 |  | note | MDR/VIVA Key - S
checkpoint-group |  |  | section | 2.0 Blinding/Lean Concrete
checkpoint-status |  |  | checkpoint | 2.1 - Set out
label | 86fe4bc4-62ff-5c40-9bb9-3a7cd82075f1 |  | note | Ref docs - IFC drawings
label | 089626ac-9bbd-548e-bd18-dacf51ff92f9 |  | note | Acceptance criteria - Extents, grades and levels correct to relevant drawings. All services have been marked out.
button | 33a08e2f-ba2f-5484-a2b9-57125200af6a |  | button | Acceptance | Yes,No,N/A
label | f591230a-d954-5fcf-a8ca-acc37573e700 |  | note | Key - W
label | a4ef8778-38d4-53a9-b6bb-1d5f4a174358 |  | note | MDR/VIVA Key - W
checkpoint-status |  |  | checkpoint | 2.2 - Pre-Pour Inspection
label | ec7ee693-13c8-5626-ab42-5d7cca6da121 |  | note | Ref docs - Bulk Earthworks ITP 02
text | d6ed777d-3d29-5f36-8e20-774571a70ff7 |  | textbox | Underlying lot number: ---------------------------
label | 508b44c2-a4d5-5b6a-8064-f431605ab32e |  | note | Acceptance criteria - Has a pre-pour inspection been completed with the client, and they have verified in writing that the pour is able to commence?
label | 01eabe0a-10f8-5400-9041-d074788419d5 |  | note | ○ The foundation base excavation shall be tested, surface compacted and approved prior to placement of the blinding.
label | ae86cf42-f983-5714-ab6c-42571514a449 |  | note | ○ The foundation location, depth and dimensions shall also be checked and confirmed prior. to placing the blinding.
label | 4de94789-0a5f-514d-b31d-d228bee0d2aa |  | note | ○ Approval shall be provided, in writing, by McDermott to the foundation. subcontractor before commencing with concrete placement.
label | 766f8803-c430-5e51-9098-f4c55463bf94 |  | note | ○ Has this been completed?
button | be854e56-748b-562b-b097-10edb85de43e |  | button | Acceptance | Yes,No,N/A
label | 85c6c7fb-2f8a-53f4-b9f3-8d5eac4d1f55 |  | note | Key - H
label | e6e9c8c3-c1d8-54f1-88e0-e11486688fa5 |  | note | MDR/VIVA Key - H
label | ca558a49-2270-58c0-a08d-98204cced2cc |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Pre-Pour Checklist, 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 2.3 - Lean Mix Concrete
label | c0181690-db59-5f12-936c-d0cb9382f4ec |  | note | Ref docs - Section 5.1.2 of document 235929-000- CV-SP-00007
label | b999404c-0268-5609-b37f-fe95f278faf5 |  | note | Acceptance criteria - Approved Concrete Mix Design.
button | d4c31910-d804-590a-8b32-76c475a8e69a |  | button | Acceptance | Yes,No,N/A
label | 6983f950-b771-5c06-850e-ab5b59e303b2 |  | note | Key - W
label | 0c5e9dcb-64e5-5698-8cf9-c92c8380d069 |  | note | MDR/VIVA Key - W
label | 15a44087-ddb2-5c30-a1fc-a12f8ba0a5ef |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Dockets
checkpoint-status |  |  | checkpoint | 2.4 - Placement of Lean Mix
label | 49209e33-c527-599b-bd12-ae606910c89e |  | note | Ref docs - 235929-000-CV-SP-00007
label | a84414c6-b35c-56cf-b14c-8fc6cd13cf02 |  | note | Acceptance criteria - Has the blinding been poured to the correct level? The following are acceptable:
label | 5a62b3de-cf3f-5125-bd5e-4329bb47d03b |  | note | – Minimum Thickness = 50mm
button | 6e9a8561-a3de-5bbf-a3cd-386009a4c82c |  | button | Acceptance | Yes,No,N/A
label | 0a030111-d672-5aef-a44c-b2489fda43a8 |  | note | Key - W
label | 7387a6ed-a301-5b0b-b17e-e8e79b0d6977 |  | note | MDR/VIVA Key - W
label | d5da4906-4e10-5691-b7c4-785fe3ed91e4 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - As-built Survey
checkpoint-group |  |  | section | 3.0 Formwork
checkpoint-status |  |  | checkpoint | 3.1 - Temporary works requirements
label | c7819eff-ac8d-5ff9-b597-0f2b6f3a4a78 |  | note | Ref docs - SYM-INF-Temporary Work Procedure IFU 05122
label | fb975dca-1c9e-50e7-9e2d-f87b208c3eeb |  | note | Acceptance criteria - Formwork above 1.0m to be designed by temporary works engineer.
label | 2ab242e7-9df3-5ef7-8398-aa12988d9771 |  | note | ○ Has design to be undertaken by external consultant complying with AS1170 and AS3610 plus any project specification requirements?
button | 4478758b-9afd-5146-93d3-af9f63a08daf |  | button | Acceptance | Yes,No,N/A
label | f8449bb5-6135-5252-a322-90a42793f594 |  | note | Key - H
label | 1f9c2ac4-53bd-5031-986d-94e9fcfd3364 |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 3.2 - Pile Penetration
label | ca94c097-afa7-5f79-a50e-916650438797 |  | note | Ref docs - Civil Drawings IFC
label | 20309ffe-f6ee-590f-9186-18ba5bd6f161 |  | note | Acceptance criteria - Pile C.O.L to penetrate 50mm above blinding of pile cap (+/- 25mm).
label | 7b063ac0-ac9b-5948-9e3a-1146ce759369 |  | note | ○ Has the pile been determined to be free of cracking and concrete damage following cropping?
button | 9f1bb396-e983-53ed-ba99-e6d9d34cd1a8 |  | button | Acceptance | Yes,No,N/A
label | 344e6758-6c88-5409-8f2f-0a58e050cf22 |  | note | Key - H
label | 9de46810-e107-5e8a-96c8-6c10f3f048d1 |  | note | MDR/VIVA Key - H
label | 854479c7-f6e2-581e-8033-e770c58f9fef |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 3.3 - Formwork Setout and positioning correct
label | 5535dc21-45a0-5166-aeaa-70a54f48f3ca |  | note | Ref docs - Civil drawings 235929-000- CV-SP-00008; Section 6
label | e7480757-5b6f-5994-b7b2-b90610675b29 |  | note | Acceptance criteria - Is formwork checked for potential loose sections, ensuring no movement upon placement of concrete?
label | 5b47baf0-737f-596f-9bbf-ebb400095fe0 |  | note | ○ Is formwork in line with survey markings?
label | 7f7dd498-3c4f-5eff-9bc5-ce271fcbfc67 |  | note | ○ Have chamfers (if required) been attached to formwork in level manner?
button | 7d1dcfdb-096d-5461-ab3a-78ebee5e310f |  | button | Acceptance | Yes,No,N/A
label | 7ad068b9-91fc-590d-b608-0150ab8ff736 |  | note | Key - W
label | 1b82924b-a9bb-5542-aacf-0703c64a07b0 |  | note | MDR/VIVA Key - W
checkpoint-status |  |  | checkpoint | 3.4 - Concrete jointing
label | 4f59ced6-d6b0-5831-837d-bf1581fcd594 |  | note | Ref docs - Civil drawings
label | 91eede06-c374-5b5f-92ff-d89a7db6e3f2 |  | note | Acceptance criteria - Have construction joints to be installed as detailed on Drawings and notes using correct materials?
button | 5721c9c0-a3fc-546a-97d9-092302ebc07b |  | button | Acceptance | Yes,No,N/A
label | 0228c326-27c4-510e-b07a-cb7faf01793e |  | note | Key - W
label | 4c1d22f1-532a-514d-9c9b-f26cbffbb870 |  | note | MDR/VIVA Key - S
checkpoint-group |  |  | section | 4.0 Reinforcement
checkpoint-status |  |  | checkpoint | 4.1 - Steel reinforcement supply
label | f42931b2-66a1-51f1-be50-2c7e599cc49e |  | note | Acceptance criteria - Have steel tags checked against supply schedule prior to installation?
label | 61b24da6-4ac4-5952-8d6b-4337b1843aec |  | note | ○ Does the manufacturer hold a valid ACRS certificate?
label | fd813473-0387-5126-a63b-b569baf3b18c |  | note | ○ Is reinforcement is free from rust and other contaminates that may affect bonding?
button | e59386e9-e209-5aaa-82f8-cdd0697773db |  | button | Acceptance | Yes,No,N/A
label | 890a24d8-f366-56c7-b083-3bffc08bdef2 |  | note | Key - S
label | 8221f792-3caa-5c2e-ba97-26cff7f5ab2f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Delivery Dockets / certificates / product tags, Incoming material checklist Photo’s
checkpoint-status |  |  | checkpoint | 4.2 - Steel reinforcement installation
label | d22409ec-ccf9-5370-b6eb-4dbbf8715b67 |  | note | Ref docs - 235929-000- CV-SP-00009, AS3600 17.5.3, 235929-000- CV-01-92002- 010002
label | 6810c17f-d835-59a0-ac94-7a3df2f24a31 |  | note | Acceptance criteria - Is steel installed as per the latest IFC drawings?
label | 70f1ae2d-0b63-5ef3-8fa0-1d2c9a22913e |  | note | ○ Does steel reinforcement conform with Steel Reinforcement Specification?
label | 866f16bd-0658-51b0-95d6-2bc197050c44 |  | note | – – – – – – – – – – – – – –
label | 4fdf6b1d-4ff2-5ef9-9362-2baa7e9ab501 |  | note | 17.5.3 Tolerance on position of reinforcement and tendons
label | 216d941c-878a-5ede-ab23-3d86b51297ec |  | note | The deviation from the specified position of reinforcement and tendons shall not exceed the following:
label | bf01ae81-1011-5a6a-81c4-8f7e5eb74919 |  | note | (a) For positions controlled by cover –
label | e7b5e44b-7575-5e12-a0c2-ecaff87cd733 |  | note | (i) in beams, slabs, columns and walls: -5, +10 mm;
label | f8f39c39-2cfc-51fd-ba00-ce6cfa6e2b3f |  | note | (ii) in slabs-on-ground: -10, +20 mm; and
label | ea7f388f-2b47-5ff4-8246-2e841888ff04 |  | note | (iii) in footings cast in the ground: -10, +40 mm,
label | a4f8bc42-4867-53e0-b2a1-65ce6b07823a |  | note | where a positive value indicates the amount the cover increases and a negative value indicates the amount the cover decreases.
label | 823636fa-9bb5-59e4-b47f-57b5832f0b1c |  | note | (b) For positions not controlled by cover, namely –
label | b9133cb8-cb80-5600-aaaf-d6ee1eb8d8d1 |  | note | (i) the location of tendons on a profile: 5 mm;
label | 99065f29-b07c-594f-841c-6df3a506c4d7 |  | note | (ii) the position of the ends of reinforcement: 50 mm; and
label | af268ade-110f-5716-a4cf-67cdaebfb06a |  | note | (iii) the spacing of bars in walls and slabs and of fitments in beams and columns: 10% of the specified spacing or 15 mm, whichever is greater.
label | ee259f74-8863-5c36-899c-9be71202c541 |  | note | – – – – – – – – – – – – – –
label | 16a1861c-5b6b-5fc6-846f-36200d7dcc3b |  | note | ○ Has minimum cover to inside face of wall must be maintained? All reinforcement shall be in accordance with AS 3600 & Civil drawings.
label | d2fe726d-b515-5987-9f1d-bbd12508d9b8 |  | note | – – – – – – – – – – – – – –
label | d63c2bfc-fe63-5578-a6d5-82ffca82744a |  | note | 8.1 CONCRETE COVER SHALL BE IN ACCORDANCE WITH AUSTRALIAN STANDARD AS 3600 OR THE VALUES STATED BELOW, WHICHEVER IS GREATER.
label | 0f40a8cf-669f-53ed-9c92-6f5ebb5f02ac |  | note | ○ PAVING (TOP) = 30 mm
label | 6d8f4b08-39eb-5b25-8d96-a62bdab591f1 |  | note | ○ PAVING (BOTTOM - AGAINST GROUND) = 50 mm
label | 16e94149-4024-5b9f-9d6f-42ae460a5559 |  | note | ○ FOUNDATIONS CAST AGAINST FORMWORK (INCL. EXPOSED WEATHER FACE) = 45 mm
label | 021a922d-e5d0-513f-890d-c06debe22372 |  | note | ○ FOUNDATIONS CAST AGAINST GROUND = 65 mm
label | 0973c0aa-da2f-5900-88f6-b3260841c5fc |  | note | ○ EXPOSED TO WASH DOWN WATER AND/OR PROCESS SPILLAGE = 50 mm
label | 81964aa0-8a8f-543e-8519-793fafead59f |  | note | ○ CAST ON LEAN CONCRETE = 45 mm
label | c7557033-23b8-54df-98eb-9909d90dc9ca |  | note | ○ CFA PILES = 70 mm
label | 9926baa2-c277-5d16-8aa2-294dd6120c87 |  | note | – – – – – – – – – – – – – –
button | 7e9e464f-63c6-50ef-a40b-8ee9989570f8 |  | button | Acceptance | Yes,No,N/A
label | 9f00da5c-02b5-57c6-9ee4-45d014933309 |  | note | Key - H
label | 5d6b38f5-845a-5e80-993e-560195f284be |  | note | MDR/VIVA Key - S
label | 05102a51-0c35-550a-ad38-1a1984d66084 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - IFC Drawing Number and Revision
checkpoint-group |  |  | section | 5.0 Structural Concrete Pour
checkpoint-status |  |  | checkpoint | 5.1 - Pre-pour Inspection
label | 239ffe9e-5ec3-5fd1-b0c4-f20c7e67ae4b |  | note | Ref docs - 235929-000-CV-SP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
label | 4db2740b-4bb6-5ccc-b27e-5b092ab54960 |  | note | Acceptance criteria - Has a pre-pour inspection checklist completed prior to placement?
button | 0b4afb99-2b27-5759-b940-2528358e76b5 |  | button | Acceptance | Yes,No,N/A
label | 9236e013-4ce8-5ec0-bf67-f3a5d594cb12 |  | note | Key - H
label | b137a84d-23cd-5150-ada7-fac772779c01 |  | note | MDR/VIVA Key - H
label | 52f81244-cb49-539d-80e2-05c4178e5004 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.1 Pre-Concrete Placement Checklist
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 5.2 - Placement
label | cf45ad69-6304-520e-ac92-0418c788afea |  | note | Ref docs - 235929-000- CV-SP-00007 Appendix 7.3 Concrete Truck Record
label | b20d327c-4997-5b05-b905-9173ff44a912 |  | note | Acceptance criteria - Concrete shall not be placed when temperature is less the 5°C or greater than 36°C. Between 32°C and 36°C admixtures and placing requirements must be met.
label | 3b518dbe-f4ef-51f9-a0de-f4b0f17e3944 |  | note | ○ Concrete shall be transported, handled and placed to prevent segregation, loss or leakage of materials.
label | 90b508b7-9702-5ee3-921a-475378d98e79 |  | note | ○ Concrete shall not be dropped from a height greater than 2m.
label | 5f46a6c2-e296-59d7-83f1-6aece02703d6 |  | note | ○ Concrete shall be discharge within 90 minutes of dispatch from plant.
label | 2deae49a-8fe0-535d-9ff4-94c49e292fcc |  | note | ○ For continuous pours, the maximum time lag between truck loads shall not exceed 25 minutes.
label | a8eeefbb-ca7c-5b1d-9a41-e4a56283a0b2 |  | note | ○ Concrete shall be thoroughly vibrated to ensure no honey combing, voids or surface defects occurs and compaction is achieve throughout structure.
label | 77a59b85-24df-5680-8886-66f8739d49d4 |  | note | ○ Water shall not be added to achieve slump greater than that specified. Slump test to be completed after water is added.
button | 895d47a5-a1aa-549c-a38c-11b1e0dd2ae1 |  | button | Acceptance | Yes,No,N/A
label | 2f23a380-2723-599a-8be2-b9d622724aab |  | note | Key - H
label | 74c06dfc-9064-5b62-9ade-07340b55e3cf |  | note | MDR/VIVA Key - W
label | 0d5bea98-5a15-51b4-a762-f1c9019ae34c |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour Record/Dockets
checkpoint-status |  |  | checkpoint | 5.3 - Slump Test
label | df23455f-3b5a-5d55-8fac-fa1d22e46fe8 |  | note | Ref docs - Section 5.1.1 235929-000- CV-SP-00007
label | 32e1fcef-a061-5f7c-ba59-e3482e2575f3 |  | note | Acceptance criteria - Slump must be within tolerance of designed slump.
label | c2171f33-7ce8-5763-adaf-bb6787dbadbf |  | note | ○ Testing shall be +- 15% of stated.
label | 86df0126-48a2-5e18-bd77-5ff70ac53d96 |  | note | ○ Approved mix design slump
button | d1ef89bb-380e-5796-91f7-2829c0908bde |  | button | Acceptance | Yes,No,N/A
label | ecd5aa8f-f4ed-54d6-a786-af29109ff584 |  | note | Key - S
label | 16baa9ec-1bc4-597c-b27e-8406c7aa512f |  | note | MDR/VIVA Key - S
label | f6a24409-a0b3-536c-afca-48d362553b0f |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test docket
checkpoint-status |  |  | checkpoint | 5.4 - Strength Testing
label | 6a712eec-24b0-515d-b216-0914620452ee |  | note | Ref docs - 235929-000- CV-SP-00007 Section 6.8
label | 436c519e-acfa-54a4-9e8c-583a2586890a |  | note | Acceptance criteria - Samples to be taken from chute. 5 cylinders collected per sample – 1x 7day, 3x 28day, 1x reserve.
label | 36fa5d97-aa53-5a90-b994-98f5f4f0ebc9 |  | note | ○ 1 test for the first 20m3
label | 5d6827c1-535d-50ae-b753-418f1a284471 |  | note | ○ 1 test per 40n3 thereafter
label | 35fcfc0c-c309-5d8d-9de0-4c58c778f5bf |  | note | ○ Frequency reduce to 1 test per 80m3 for pours over 400m3
label | 322fdf96-ea09-5a44-ad31-dbc9ae3f6d98 |  | note | Acceptance
label | a0426478-4d97-538c-b10c-52d69069e918 |  | note | – – – – – – – – – – – – – –
label | 1d705805-ea00-5501-94af-40d2904998cb |  | note | No. of samples ¦¦ Volume of concrete (m3)
label | eeedf888-d6b9-54ea-a141-1f1d40027f74 |  | note | – – – – – – – – – – – – – –
label | bbc71923-925e-575e-98d7-466e7be68a57 |  | note | 1 ¦¦ <20
label | 5a9c0c7a-b950-5538-a8d8-739efd701cfe |  | note | 2 ¦¦ 20-60
label | e971d102-313c-5225-a980-fd95f29b565d |  | note | 3 ¦¦ 60-100
label | 80c633b5-0611-5e1b-861a-88805ff61a31 |  | note | 4 ¦¦ 100-140
label | e2ab1c0c-441c-5b5d-9c66-11b4d40eb400 |  | note | – – – – – – – – – – – – – –
label | 9983feff-0c46-5f99-948b-86aed595806f |  | note | Key - H
label | 45500009-804d-54b6-8fed-29d19bac0829 |  | note | MDR/VIVA Key - S
label | 180eefb4-5dcc-5324-a1ed-2aaee9d8ddcc |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Test report
checkpoint-status |  |  | checkpoint | 5.6 - Curing of Concrete
label | f7c0712b-8955-55e8-ab27-f69d4626a3a7 |  | note | Ref docs - 235929-000-CV-SP-00007 Section 6.5
label | c1edee11-ee08-5473-b83b-4a2a6ed25110 |  | note | Acceptance criteria - As per the approved Curing Methodology.
label | adf2a0c3-8e3f-5603-81f6-b2380f89ae5a |  | note | – Applied once bleed water has gone
label | 65f5950e-d5e8-54bd-8253-75674123c1e6 |  | note | – Continuous uniform film achieved
label | cb076cc0-2c21-551d-bb2e-620e61c15228 |  | note | – Rate of 5m2/L
label | b5547988-aa51-55c8-a251-12d415d7da7d |  | note | ○ Has curing been conducted as per approved curing methodology?
button | 817fae1c-00a7-52d5-a06c-fbc361bf5901 |  | button | Acceptance | Yes,No,N/A
label | 17874744-6164-5a97-933e-416f164d96fc |  | note | Key - H
label | 1e74c937-5f23-5ec4-bba8-f6195146f428 |  | note | MDR/VIVA Key - W
label | 92fa07e0-a3fe-5057-a34f-dd18e3de53c6 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Approved Curing Technical Data Sheet
checkpoint-status |  |  | checkpoint | 5.7 - Concrete Finishing
label | ca172474-abe9-5707-9354-92222823cb7e |  | note | Ref docs - 235929-000-CV-SP-00007 Section 6.4
label | 0e6e3ad2-49b5-5869-92fb-3e51d525d504 |  | note | Acceptance criteria - Finish concrete per schedule below:
label | a0814925-0f71-561b-b587-d7a05fccbb1e |  | note | ○ Interior walls or columns exposed: smooth form/rubbed finish.
label | c5f50b3a-6d8c-5caf-9989-bb2fea7549bf |  | note | ○ Exterior walls or columns exposed: smooth form/rubbed finish.
label | 5ecdd4ef-02b2-56c3-bb96-20a75b791a03 |  | note | ○ Walls below grade: rough form finish.
label | d6ea72f1-fd74-5653-ad3c-401c3053c4f9 |  | note | ○ Exterior slabs for spill containment: float finish.
label | a6b1b127-b96e-5e22-9317-4a01d53b7d2c |  | note | ○ Other exterior slabs (i.e. foot traffic): broom finish.
label | bc06f7d0-e86b-5d4f-a708-03e036c88fd7 |  | note | ○ Interior slabs: steel trowel.
label | a11f21c5-2d68-555f-8348-706701894c3a |  | note | ○ Interior slabs to accept additional finish: steel trowel.
label | 9dea0913-2eda-5e7d-b7bc-d4c125d26d0b |  | note | ○ Surfaces to be grouted: rough [6 mm amplitude] but even finish with laitance removed to provide good bond between grout and concrete.
button | a30e398c-0496-5a92-b198-9caff7926968 |  | button | Acceptance | Yes,No,N/A
label | 860f64e1-1579-5c3c-ad59-70ce5fcc6bdd |  | note | Key - S
label | 1c75f4e8-aabf-5861-9841-72c7b9f3affc |  | note | MDR/VIVA Key - S
label | 315fb1fd-846f-5914-a953-3709828694a0 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - 235929-000-CVSP-00007 Appendix 7.3 Concrete Truck Pour
checkpoint-status |  |  | checkpoint | 5.8 - Formwork Stripping
label | fa3a5756-6946-57eb-acac-9d5d87d55622 |  | note | Ref docs - 235929-000-CV-SP-00007, AS1510, AS1509, Section 6.6 of 235929-000-CV SP-00008 CONC FORMWORK
label | 8b21296e-c06f-5993-954b-ae76c7df9417 |  | note | Acceptance criteria - Has Remove formwork progressively so no unbalanced loads are applied to the structure, or concrete is damaged?
label | 0c2c6fda-7612-55fb-aefd-5e0c545ef761 |  | note | ○ Has the formwork been removed in the same sequence as concrete placement to achieve similar concrete surface coloration?
label | 50ba77fb-2509-5919-89c0-9c478a004902 |  | note | ○ In accordance with AS3600 Table 4.4 and Section 17.1.5, removal of forms before 7 days would require a curing membrane conforming to AS3799 to be applied immediately or any other approved acceptable method of water retention in the concrete.
label | 621e2dc8-4940-5541-bdf8-c42a4b914fca |  | note | ○ Has this been completed?
button | 501e0beb-5a27-5550-b675-c737dea147cd |  | button | Acceptance | Yes,No,N/A
label | 396cd9db-d4ed-5070-8c8c-3651e219380c |  | note | Key - S
label | a95a6b67-8daf-5635-8665-fea3aa2b89dd |  | note | MDR/VIVA Key - S
checkpoint-status |  |  | checkpoint | 5.9 - Post Pour inspection
label | 83b22758-b60c-5795-93f8-c10d1940174c |  | note | Acceptance criteria - All abovementioned works have been completed in-line with the drawings and specification and backfilling around structure can be completed (if applicable)
button | 481205fd-06dc-5e83-86f2-969975dc853b |  | button | Acceptance | Yes,No,N/A
label | 1700a992-191f-5f1d-82cb-31f02e3c63b6 |  | note | Key - H
label | ec247bc9-a2be-5b86-9e16-1a94cc9299f9 |  | note | MDR/VIVA Key - H
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-group |  |  | section | 6.0 Completion
checkpoint-status |  |  | checkpoint | 6.1 - As Built
label | a4a248be-348c-596f-bb94-db2e17b0b3ee |  | note | Acceptance criteria - As built to be submitted after pour, showing set out, RLs, grades, extents, bolts, grout tubes, starter bars, etc.
button | dd426662-ba58-5d08-a428-ffd5f9a65067 |  | button | Acceptance | Yes,No,N/A
label | 31c043f2-f95a-5193-af01-8d294bcbac7a |  | note | Key - S
label | 2eae9447-6a3d-5a16-9da6-e962fa10673d |  | note | MDR/VIVA Key - H
label | f461e7b7-35df-5ee5-b3f2-3cd1c91fea8e |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Survey Conformance report
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.2 - Concrete Test Results
label | b0567501-b655-5047-805f-92a97030f726 |  | note | Ref docs - 235929-000-CV-SP-00007 AS3600, AS1379, AS3610 IFC drawings
label | 4c830c25-5a30-5cde-8b1c-c4ad69c131fd |  | note | Acceptance criteria - Submission of 28 days results. Results meet requirements of 40MPa.
button | 882fd5d6-c066-5d45-ac9e-f6265108dcbe |  | button | Acceptance | Yes,No,N/A
label | 9378086f-efbb-56df-a8d4-c7f36335e80d |  | note | Key - H
label | 62736c2b-c383-51eb-814a-f744b74d40ff |  | note | MDR/VIVA Key - S
label | da0c4da8-e8c2-5f85-8aaa-0ab3912af901 |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - NATA endorsed test report
checkpoint-status |  |  | checkpoint | 6.3 - Concrete cracking approval
label | ee34ac15-e616-59bb-8540-c270d0479483 |  | note | Acceptance criteria - Contractor is to submit a concrete crack repair methodology to MDR prior to commencing any crack repair. Has this been approved?
label | ef164b3f-5bce-5145-a896-fd14f3aa7aa9 |  | note | – – – – – – – – – – – – – –
label | c19c26dc-0b16-532a-bdcc-050cae2b75d3 |  | note | Maximum Allowable Crack Widths in New Concrete
label | 843c554a-8132-52c5-9c68-020dd3a3602f |  | note | – – – – – – – – – – – – – –
label | 34360a93-ec16-558c-8d16-8eaae13492ef |  | note | Service Exposure Condition ¦¦ Crack Width, μm
label | a11b7ea0-7c7b-5a1f-afef-85f410f63e8c |  | note | – – – – – – – – – – – – – –
label | 7c9647fa-d9e2-5392-b4b3-156699739c90 |  | note | Interior ¦¦ 300
label | 3105f302-a6da-57b6-aee1-73160c8d4993 |  | note | Exterior air (or soil) ¦¦ 200
label | 320853ad-9ad1-5686-87f5-fd0b0b860ad3 |  | note | Water-retaining structures ¦¦ 100
label | f5b4a7d2-f20c-59ea-b522-91085f645b10 |  | note | – – – – – – – – – – – – – –
button | 75e83a5f-9507-5d54-aefc-f438730e4bd0 |  | button | Acceptance | Yes,No,N/A
label | 318f2ad8-d665-5344-8acb-3bf3225ac2b9 |  | note | Key - H
label | b16419de-1901-5fd9-bfea-cc56b3ed6245 |  | note | MDR/VIVA Key - H
label | 6d3a76c9-6037-5d0a-be16-9752f81fb2ae |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Concrete Repair Method Document Approval
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT
checkpoint-status |  |  | checkpoint | 6.4 - Concrete cracking repair
label | 4690863e-91d7-573c-928b-0dc622373387 |  | note | Acceptance criteria - Has concrete crack repair been undertaken as per the approved method?
button | d5217aab-b234-5307-ba82-f79ac01566e9 |  | button | Acceptance | Yes,No,N/A
label | 0a981ae8-f477-5408-a8fb-c610b4e47dfc |  | note | Key - H
label | b6f635be-858e-52e8-b614-4c5c61f0214a |  | note | MDR/VIVA Key - H
label | cb75cf7c-87e6-551c-a1d3-29fc188af5aa |  | note | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Photo’s
holdpoint |  |  | signoff | AUTHORITY HOLDPOINT