## Sheet1
ConQA Team Notes: | [10 empty] | Comments/Queries:
Document Title: |  | ITP-113-CIV-CPD-Inspection & Test Plan - Conduit & Pits - Rail (Supply and Install)
ITP Description: |  | Conduit & Pits - Jemena HV relocation
Discipline (e.g. CIV/STR/RAIL: |  | CIV
Revision Number: |  | 1
Revision Date: |  | 2023-12-08
ITP created by: |  | Lachlan Morris/Pat Sabaruddin
ITP approved for use by: |  | Pradeep Talasila
Special Notes to ConQA Team : |  | This ITP is to be used in Calder Park Dr only.
Inspection & Test Plan - Conduit & Pits - Rail (Supply and Install)
[9 empty] | Revision: | 1
[9 empty] | Date: | 08/12/223
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | IFC Drawings | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | VESI D&C Standard | VESI_URD_003 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Plastic Industry Pipe Association - Industry Guidelines | PIPA POP 003 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Australian Standards | AS 2032 AS 2053 AS2648.1 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries - Materials
2.1 | Conduits | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003; cl4.4.2, cl5.8.2 AS2053 | HV & Comms: Conduit sizes as per IFC and VESI 4.4.2 CONDUITS USED WITHIN THE VESI NETWORKS SHALL BE HEAVY DUTY SOLID WALL, ELECTRICAL CONDUIT TO AS2053. HV & COMMS CONDUITS TO HAVE A max BENDING RADIUS AS PER VESI_URD_003 - 5.8.2 Inspect materials upon delivery and attached delivery dockets. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.2 | Pits and Pit Lids | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Pits: Pits to be used and installed as per IFC drawings and manafacturer requirements Inspect materials upon delivery and attached delivery dockets. | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs Attach delivery dockets
2.3 | Warning/Marker Tape | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 AS/NZ 2648.1 VESI_URD_003 -5.5.2 | Warning/Marker Tape: Above HV: Orange 150 or 300mm width marker tape compliant with AS/NZS 2648.1 shall be used Inspect materials upon delivery | Visual Document Review | Each Material Type, Each Delivery | IP | SE/PE | Attach Material Conformnace Certs
3 | Prelimnaries - Procedures & Documentation
3.1 | Services | VESI_URD_003 4.4.2, 5.10 | Clearances are requried between individual electrical assets and between assets of other authorities. | Visual | Prior to commencement of works | IP | SE/Site Supervisor | This ITP
4 | Pre-Construction Activities
4.1 | Survey Set-out | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Survey to set out trench alignment and pits, and establish construction control (alignment and level). Survey to mark out existing services. | Measure Visual | Each element | IP | Surveyor SE/Site Supervisor | This ITP
4.2 | IFC Drawings | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Check the revision of the IFC drawings are current as per the drawing register (on Teambinder) | Document Review | Prior to commencement of works and at regualr intervals | IP | SE/Site Supervisor | This ITP
5 | Construction Activities
5.1 | Trench Excavation | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 | Trench profile and depth as per IFC drawings. Depth of trench is to be sufficient to allow for the minimum cover as per IFC from the top of conduits. Cl5.3.2 Within the VESI networks, cabbles shall be buried up to a maximum depth of 1400mm (max trench depth of 1500mm). The bottom of the cable trench shall be level across its width and free from any protrusions and rubble that could cause damage to the conduits. | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.2 | Placement of Bedding/Embedment and Backfill of conduits | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 - 5.7 VESI_URD_003 -5.4.2.2 | Bedding/Embedment material placed as per VESI_URD_003 - 5.7 Trench arrangement details. For non-paved areas existing Spoil is to be used as backfill. The Soil shall be compacted to ensure ground subsidence will be negligible. For paved areas all trenches will be backfilled with wet mix of Class 3, 20mm CL3 crushed rock to be compacted in 150mm layers under road surfaces. Each layer has | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.3 | Conduit Placement & Configuration | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 | Conduits are configured in accordance with IFC drawings and meet cable separation requirements. VESI 5.10.1.3 Where shown on the approved plan or by prior written approval conduits may be stacked in vertical alignment. VESI 5.8.1 Conduits are to be provided with suitable non-perishable, watertight, endcaps or plugs. For any | Measure, Visual | Each lot | IP | SE/Site Supervisor | This ITP
5.4 | Joints | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 -5.8 AS2032. | All conduit joints shall be made by utilising the spigot and socket ends. Conduits are to be joined using solvent cement and comply with AS2032. Socket ends to be placed firmly into the spigots prior to backfill. | Visual | Each Joint in each trench | IP | SE/Site Supervisor | This ITP
5.5 | Conduit Inspection | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 | Inspection of conduits undertaken by VEDN accredited contractor | Visual | Each lot | HP* | SE/PE | This ITP
5.6 | Marker Tape | VESI_URD_003 -5.5.2.2 | Marker tape shall be installed no closer than 150mm to the cover slab or conduit and no closer to the final surface level than 250mm. Marker tape should be located no deeper than 600mm from FSL. Tape to be one continuous length. | Visual | Each lot | HP* | SE/PE | This ITP
5.7 | Pit Installation | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003; cl5.9 | Comms and electrical pits to be installed as per TC-2203 Pit chamber floor to be 100mm lower than the underside of the lowest conduit. Entry conduits installed 75mm into pit. Bedding: 50mm crushed rock bedding backfill: Crushed rock is to be compacted in 150 layers arround the pit to bring the surface back to existing levels. | Viual, Measure | Each Pit | IP | SE/Site Supervisor | This ITP
6 | Post-construction / Post-installation Activities
6.1 | As-built Survey | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Survey report to include but not limited to: - Cable pit locations (Corners) - Pit dimensions & pit lid type - Changes of direction - Spare Conduits - Conduits labelled as per trench profile - every 10m - Other significant points of the cable route Attached Survey Report | Document Review | Each Lot | IP | SE/PE | This ITP
6.2 | Handover | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Jemena Audit form complete | Document Review | Each Lot | HP* | PE, Jemena | This ITP
6.3 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed. | Document Review | Once, prior to closure of this lot / element / Work area | HP* | SE/PE/SPE | This ITP
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /