## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-114-CIV-CPD-Inspection & Test Plan - Horizontal Directional Drilling
ITP Description: |  | Jemena Conduit Bore
Discipline (e.g. CIV/STR/RAIL: |  | CIV
Revision Number: |  | 1
Revision Date: |  | 2023-12-12
ITP created by: |  | Lachlan Morris/Pat Sabaruddin
ITP approved for use by: |  | Pradeep Talasila
Special Notes to ConQA Team : |  | This ITP is to be used in Calder Park Dr only.
Inspection & Test Plan - Horizontal Directional Drilling
[9 empty] | Revision: | 1
[9 empty] | Date: | 2023-12-12
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | IFC Drawings | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | VESI D&C Standard | VESI_URD_003 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.3 | Plastic Industry Pipe Association - Industry Guidelines | PIPA POP 003 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.4 | Australian Standards | AS 2033 AS4142 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminary Works/ Materials
2.1 | Electrical Conduits | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 | Conduit Grade PE100, SDR 13.6 Reference:TeamBinder Material Approval Number: | Document Review | Prior to commencement | HP | PE/SE | Teambinder approval number
2.2 | Grout | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | N/A | Document Review | Prior to commencement | HP
3 | Preliminary Works/ Procedures
3.1 | Check that current revision drawings are being used | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Drawing revison must be confirmed with the design manager | Document review | Prior to commencement | HP* | SE/PE/SPE | Design drawings.
3.2 | Auditor accreditation | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 | Auditors are to be VESI accredited | Document review | Prior to commencement | HP* | PE/SE | Teambinder approval number
3.3 | PE Welders Qualifications | AS 2033 PIPA-POP-003 | PE welders are to be qualified and regularly certified by a suitable RTO to PMBWELD301E Reference:Teambinder Hold point release number: | Document review | Prior to commencement | HP | SE/PE | Teambinder approval number
4 | Pre-construction / Pre-installation Activities
4.1 | Survey Set-out | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003; cl5.10.13 | Set out line and level of drilling works. Survey to mark out existing services. Must maintain a min. clearance as per VESI D&C 5.10.13. | Measure Visual | Each element | IP | Surveyor SE/PE/SPE | This ITP
4.2 | Draw ropes | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 AS4142 | All conduits must have minimum of one 6mm polypropylene draw rope to AS4142. | Document review/ Visual | Prior to commencement | IP | PE/SE | Material compliance certificate
5 | Construction / Installation Activities
5.1 | Conduit welding | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 PIPA-POP-003 | Joints are to be butt welded. Weld map to be supplied and identify unique joint numbers. Butt Welding records to be supplied. | Document review | All Joints | IP | SE/Site Supervisor/Survey | Sign ITP Butt Welding Records
5.2 | Drill rig setout | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Location as per current Drill shot plans | Measure Visual | Prior to commencement | IP | SE | This ITP
5.3 | Installation of Pipeline (Trenchless method) | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 VESI_URD_003 | Drill to be installed as per the survey setout. Bore logs to be supplied. When multiple conduits are installed into one bore hole care shall be taken to ensurethe conduits do not rotate during installation. Accurate detailing of conduit positions must be undertaken. | Document review Visual inspection | During pilot bore and conduit installation | WP | SE/Site Supervisor | Bore logs
5.4 | Plug pulling | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Mandrel with 90% of the pipe diameter to be pulled thrugh each conduit to ensure the conduit hasent been compressed. | Record and Review | All Pipe | HP* | SE/SPE | Sign ITP Visual of pipe pull pictures. Subcontractor Test Record
5.5 | Draw rope | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | All draw ropes must be continious between shafts and have 2m slack in the shaft. | Visual | All Pipe | IP | SE | Sign ITP.
5.6 | Auditing | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Auditing to be completed on conduit ends prior to backfilling of entry and exit shafts. | Record and Review | Alll Pipe | HP* | SE | Sign ITP Auditing Report
5.7 | Reinstatement | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Entry pits, exit pits and trenches to be backfilled with Type A or crushed rock. Backfill material shall be compacted to the same density as adjacent material or as specified. | Visual | Each shaft | IP | SE/Site Supervisor | Sign ITP
5.8 | Subcontractor ITP | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Acceptance and closeout of subcontractor ITP | Document review | Each element | IP | SE/SPE | Sign ITP Completed
6 | Post-construction / Post-installation Activities
6.1 | As-built Survey | JEMEE-DW-UG-10061100/01 JEMEE-DW-UG-10061100/02 JEMEE-DW-UG-10061100/03 | Survey as built report to be compiled. Borelog obtained from subcontractor Autocad and PDF reports are to be supplied to: | Document Review | Each element | IP | Surveyor SE/PE/SPE | Survey As Report
6.2 | Red-line / As-constructed IFC Drawings | MRPA Quality Management Plan | All RFIs, NCRs and changes to the IFC drawings are captured on a controlled drawing set marked "Red-line", "As-built" or similar. | Document Review | Once, after construction of the design package | WP | SE/PE/SPE | This ITP
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /
Note on L36: RATHNAYAKE, Thilan: Correct - that’s the process we will be follwing. We will not be installing a tracer wire. In water pipes there are no tracer wires. Entry pits and exit pits location are not a quality related item so i dont thnk it need to be in the ITP. But I believe we have a dispensation for it. drawings are reviewd by victrack as well before it got to IFC.
Note on L38: RATHNAYAKE, Thilan: Yes this will be done as a PTW process(Permit to Work)
Note on L41: RATHNAYAKE, Thilan: We will be doing this under occupations and also have a permit to disturb track. Also track will be monitored whole time of drilling.