## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-113-CIV-CPD- Jemena Conduit & Pits (Supply & Install) Rev1 | itp |  |  |  |  | ITP-113-CIV-CPD- Jemena Conduit & Pits (Supply & Install) Rev1
section | 1. Referenced Documentation
checkpoint-no-status | 1. Referenced Documentation
label | Document Title: ITP-113-CIV-CPD-Inspection & Test Plan - Conduit & Pits - Rail (Supply and Install)
label | ITP Description: Conduit & Pits - Jemena HV relocation
label | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | Discipline (e.g. CIV/STR/RAIL): CIV
label | Revision Number: 1
label | Revision Date: 8/12/2023
label | ITP created by: Lachlan Morris/Pat Sabaruddin
label | ITP approved for use by: Pradeep Talasila
checkpoint | 1.1 - IFC Drawings
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03
checkpoint | 1.2 - VESI D&C Standard
label | Reference - VESI_URD_003
checkpoint | 1.3 - Plastic Industry Pipe Association - Industry Guidelines
label | Reference - PIPA POP 003
checkpoint | 1.4 - Australian Standards
label | Reference - AS 2032, AS 2053, AS2648.1
section | 2. Preliminaries - Materials
checkpoint | 2.1 - Conduits
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003; cl4.4.2, cl5.8.2 AS2053
label | Acceptance Criteria - HV & Comms: Conduit sizes as per IFC and VESI 4.4.2 CONDUITS USED WITHIN THE VESI NETWORKS SHALL BE HEAVY DUTY SOLID WALL, ELECTRICAL CONDUIT TO AS2053.
label | ○ HV & COMMS CONDUITS TO HAVE A max BENDING RADIUS AS PER VESI_URD_003 - 5.8.2
label | ○ Inspect materials upon delivery and attached delivery dockets.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
date | Date Completed:
checkpoint | 2.2 - Pits and Pit Lids
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03
label | Acceptance Criteria - Pits:
label | ○ Pits to be used and installed as per IFC drawings and manafacturer requirements
label | ○ Inspect materials upon delivery and attached delivery dockets.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
date | Date Completed:
checkpoint | 2.3 - Warning/Marker Tape
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, AS/NZ 2648.1, VESI_URD_003 -5.5.2
label | Acceptance Criteria - Warning/Marker Tape:
label | Above HV:
label | ○ Orange 150 or 300mm width marker tape compliant with AS/NZS 2648.1 shall be used
label | ○ Inspect materials upon delivery
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs
date | Date Completed:
section | 3. Prelimnaries - Procedures & Documentation
checkpoint | 3.1 - Services
label | Reference - VESI_URD_003 4.4.2, 5.10
label | Acceptance Criteria - Clearances are requried between individual electrical assets and between assets of other authorities.
label | Method - Visual
label | Frequency - Prior to commencement of works
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
section | 4. Pre-Construction Activities
checkpoint | 4.1 - Survey Set-out
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03
label | Acceptance Criteria - Survey to set out trench alignment and pits, and establish construction control (alignment and level). Survey to mark out existing services.
label | Method - Measure, Visual
label | Frequency - Each element
label | Category - IP
label | Responsibility - Surveyor, SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.2 - IFC Drawings
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03
label | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
label | Method - Document Review
label | Frequency - Prior to commencement of works and at regualr intervals
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
section | 5. Construction Activities
checkpoint | 5.1 - Trench Excavation
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003
label | Acceptance Criteria - Trench profile and depth as per IFC drawings.
label | ○ Depth of trench is to be sufficient to allow for the minimum cover as per IFC from the top of conduits.
label | ○ Cl5.3.2 Within the VESI networks, cabbles shall be buried up to a maximum depth of 1400mm (max trench depth of 1500mm).
label | ○ The bottom of the cable trench shall be level across its width and free from any protrusions and rubble that could cause damage to the conduits.
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.2 - Placement of Bedding/Embedment and Backfill of conduits
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003 - 5.7, VESI_URD_003 -5.4.2.2
label | Acceptance Criteria - Measure, Visual
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.3 - Conduit Placement & Configuration
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003
label | Acceptance Criteria - Conduits are configured in accordance with IFC drawings and meet cable separation requirements.
label | ○ VESI 5.10.1.3 Where shown on the approved plan or by prior written approval conduits may be stacked in vertical alignment.
label | ○ VESI 5.8.1 Conduits are to be provided with suitable non-perishable, watertight, endcaps or plugs. For any
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.4 - Joints
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003 -5.8, AS2032.
label | Acceptance Criteria - All conduit joints shall be made by utilising the spigot and socket ends.
label | ○ Conduits are to be joined using solvent cement and comply with AS2032.
label | ○ Socket ends to be placed firmly into the spigots prior to backfill.
label | Method - Visual
label | Frequency - Each Joint in each trench
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.5 - Conduit Inspection
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003
label | Acceptance Criteria - Inspection of conduits undertaken by VEDN accredited contractor
label | Method - Visual
label | Frequency - Each lot
label | Category - HP*
label | Responsibility - SE/PE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.6 - Marker Tape
label | Reference - VESI_URD_003 -5.5.2.2
label | Acceptance Criteria - Marker tape shall be installed no closer than 150mm to the cover slab or conduit and no closer to the final surface level than 250mm.
label | ○ Marker tape should be located no deeper than 600mm from FSL.
label | ○ Tape to be one continuous length.
label | Method - Visual
label | Frequency - Each lot
label | Category - HP*
label | Responsibility - SE/PE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.7 - Pit Installation
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03, VESI_URD_003; cl5.9
label | Acceptance Criteria - Comms and electrical pits to be installed as per TC-2203
label | ○ Pit chamber floor to be 100mm lower than the underside of the lowest conduit. Entry conduits installed 75mm into pit.
label | Bedding: 50mm crushed rock bedding
label | Backfill: Crushed rock is to be compacted in 150 layers arround the pit to bring the surface back to existing levels.
label | Method - Visual, Measure
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
section | 6. Post-construction / Post-installation Activities
checkpoint | 6.1 - As-built Survey
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03
label | Acceptance Criteria - Survey report to include but not limited to:
label | – Cable pit locations (Corners)
label | – Pit dimensions & pit lid type
label | – Changes of direction
label | – Spare Conduits
label | – Conduits labelled as per trench profile
label | – every 10m
label | – Other significant points of the cable route
label | ○ Attached Survey Report
label | Method - Document Review
label | Frequency - Each Lot
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 6.2 - Handover
label | Reference - JEMEE-DW-UG-10061100/01, JEMEE-DW-UG-10061100/02, JEMEE-DW-UG-10061100/03
label | Acceptance Criteria - Jemena Audit form complete
label | Method - Document Review
label | Frequency - Each Lot
label | Category - HP*
label | Responsibility - PE, Jemena
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 6.3 - Non-conformance Report (NCR) Closure
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | Method - Document Review
label | Frequency - Once, prior to closure of this lot / element / Work area
label | Category - HP*
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | Name:
text | Position:
date | Date Completed:
holdpoint | Sign ITP