## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ-ITP-002 - Bulk Earthworks REV D | itp |  |  |  |  | INF-HSEQ-ITP-002 - Bulk Earthworks REV D
section | 1.0 Preliminaries
checkpoint | 1.1 - Determine lot size
label | Acceptance criteria - What is the lot size?
textbox | Acceptance |  |  | m2
label | Key - S
label | MDR/VIVA Key - S
checkpoint | 1.2 - Survey set-out
label | Ref docs - 235929 IFC Drawings
label | Acceptance criteria - Has the work area been set out for line and level?
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA Key - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | IFC drawing number:
textbox | Rev:
checkpoint | 1.3 - Excavation material classification
label | Ref docs - 235929-000- CV-SP-00002
label | Acceptance criteria - Has the material being excavated been inspected with category agreed upon by Superintendent and/or Superintendents Environmental Representative?
label | Tick category below:
bool | Common Fill (CF1)
bool | Sand Fill (S1)
bool | Structural Fill (SF1)
bool | Topsoil (TS1)
bool | Reuse of Site Won material
bool | Rock
bool | Contaminated Material
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - W
checkpoint | 1.4 - Material Submission / Approval
label | Ref docs - 235929-000- CV-SP-00002 Sec 11.1 Aggregate report
label | Acceptance criteria - Has any imported material (to be used as permanent fill) been approved by MDR for usage on site.
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material mix design
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Bulk earthworks – cut
checkpoint | 2.1 - Subgrade preparation
label | Acceptance criteria - Has the area been excavated to top of earthworks layer.
label | ○ Note: Existing surface material is approximately 200-300mm of crushed rock.
label | ○ Is the surface evenly graded and free-draining.
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA Key - S
checkpoint | 2.2 - Material Export / Stockpiling
label | Ref docs - SMP 20359156-211-R-Rev
label | Acceptance criteria - Adherence to Soil Management Plan.
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA Key - S
section | 3.0 Bulk earthworks - fill
checkpoint | 3.1 - Preparation of surface
label | Acceptance criteria - Has surface been cleared of all loose material visible on surface.
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA Key - S
checkpoint | 3.2 - Compaction Trial for Blended Material
label | Ref docs - 235929-PE- WI-000009 - Backfill Specification
label | Acceptance criteria -
button | ○ Is the material to be used for backfill blended material. | Yes,No,N/A
label | If No, go to item 3.3.
button | ○ Has the compaction trial been undertaken? | Yes,No,N/A
button | ○ Did the compaction trial achieve the appropriate design backfill requirements of 70kPa? | Yes,No,N/A
button | ○ Does MDR approve usage of site blended material for backfill purposes? | Yes,No,N/A
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
textbox | MDR approval:
textbox | (correspondence reference number)
checkpoint | 3.3 - Fill Placement
label | Ref docs - 235929-000-CV-SP-00002 Sec 12.2, 235929 IFC Drawings
label | Acceptance criteria - Has fill been placed in maximum 200mm compacted layer thickness?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
checkpoint | 3.4 - Moisture
label | Acceptance criteria - Has the material maintained at +/- 3% modified moisture content, with additional water being added if required during compaction?
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 3.5 - Compaction
label | Ref docs - 235929-000- CV-SP-00002 Sec 13 & Sec 14.2
label | Acceptance criteria - Has the layer been adequately compacted achieving a mean value of minimum 98% MDD?
label | ○ Density test to be completed on first backfill to verify procedure. Procedure assumed to be equal henceforth (Inspector may request additional test upon insufficient density or compaction).
label | Acceptance -
bool | Small Foundations
label | (1 test per foundation)
bool | Large Foundation
label | (larger than 10m2) minimum 3 tests per lift
bool | Fill Areas minimum 2 tests per 185m2 but not less than 3 tests per area
label | Key - H
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Test reports
checkpoint | 3.6 - Fill layer – test rolling
label | Ref docs - 235929-000- CV-SP-00002 Sec 12
label | Acceptance criteria - Does the layer withstand test rolling without visible deformation or springing?
textbox | List Attendees:
button | Acceptance | Yes,No,N/A
label | If 'no' please see below If 'yes' please proceed to Conformance Check
label | Key - H
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Proof roll checklist [235929-MG1668-CV- 003-SUBC-000053]
checkpoint | 3.7 - Identification of soft wet or unstable material
label | Acceptance criteria - Has any soft or wet unsuitable material been found?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - S
checkpoint | 3.8 - Treatment of unsuitable material
label | Ref docs - 235929-000- CV-SP-00002 Sec 12.1, Symal Proof Roll Procedure Doc
label | Acceptance criteria - Have any issues been determined?
textbox | (length) |  |  | m
textbox | (width) |  |  | m
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Proof Roll Checklist, Dockets / Photos
section | 4.0 Conformance check
checkpoint | 4.1 - Subgrade level and shape
label | Ref docs - 235929 IFC Drawings
label | Acceptance criteria - Has the prepared subgrade been surveyed in accordance with and verifying specified requirements?
label | ○ Final grade +- 60mm
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA Key - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As built report
textbox | IFC drawing number:
textbox | Rev: